## Disclaimer
DISCLAIMER
Essential Energy is registered as a Distribution Network Service Provider. This Distribution Annual Planning Report 2023 has been prepared and published by Essential Energy under clause 5.12.2 and 5.13.2 of the National Electricity Rules to notify Registered Participants and Interested Parties of the results of the distribution network annual planning review and should only be used for those purposes.
This document does not purport to contain all of the information that a prospective investor, participant or potential participant in the National Electricity Market, or any other person or interested parties may require. In preparing this document it is not possible, nor is it intended, for Essential Energy to have regard to the investment objectives, financial situation and particular needs of each person who reads or uses this document.
In all cases, anyone proposing to rely on or use the information in this document should independently verify and check the accuracy, completeness, reliability and suitability of that information for their own purposes.
Accordingly, Essential Energy makes no representations or warranty as to the accuracy, reliability, completeness or suitability for particular purposes of the information in this document. Persons reading or utilising this document acknowledge that Essential Energy and their employees, agents and consultants shall have no liability (including liability to any person by reason of negligence or negligent misstatement) for any statements, opinions, information or matter (expressed or implied) arising out of, contained in or derived from, or for any omissions from, the information in this document, except in so far as liability under any New South Wales and Commonwealth statute cannot be excluded.
Contact
For all enquiries regarding the Distribution Annual Planning Report 2023 and for making written submissions contact:
Essential Energy DM Coordinator PO Box 5730 Port Macquarie NSW 2444 Email: dmcoordinator@essentialenergy.com.au

## ZSSummer
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 23/24 | 24/25 | 25/26 | 26/27 | 27/28
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 33 | 0.99988 | 13.7867 | 13.7769 | 13.7631 | 13.7777 | 13.7964 | 13.0061 | 2
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 33 | 0.99959 | 15.3688 | 15.5126 | 15.6823 | 15.7974 | 15.9 | 12.2954 | 2.5
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 44 | 0.99998 | 11.4499 | 11.502 | 11.5559 | 11.6161 | 11.6887 | 0 | 2.5
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 16.5 | 0.99995 | 11.0155 | 11.053 | 11.0769 | 11.1461 | 11.1624 | 13.5074 | 2
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.99431 | 19.3155 | 19.3969 | 19.4829 | 19.5518 | 19.6739 | 18.9371 | 4.5
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 220 | 0.98869 | 94.2201 | 94.2015 | 94.4232 | 94.2922 | 94.3412 | 0 | 2.5
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.99922 | 6.3937 | 6.5564 | 6.741 | 6.9096 | 7.0821 | 8.204 | 3
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 27.5 | 0.98698 | 16.2958 | 16.3662 | 16.4735 | 16.5702 | 16.6784 | 3.9968 | 3
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99986 | 14.2038 | 14.253 | 14.3126 | 14.3843 | 14.4727 | 12.5318 | 2
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 22 | 0.99325 | 11.3005 | 11.4768 | 11.675 | 11.8733 | 12.0688 | 12.2065 | 1.5
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 33 | 0.99604 | 26.0455 | 25.9799 | 26.0302 | 25.8976 | 26.0452 | 22.5388 | 2
Lismore | Ballina 132kV | 132/66 | 75/112 |  |  | 0 | 0.96392 | 22.6059 | 22.5988 | 22.6587 | 22.7167 | 22.6508 | 0 | 2
Lismore | Dunoon | 132/11 | 10 | 10 |  | 11 | 0.98773 | 6.3468 | 6.3683 | 6.4099 | 6.4444 | 6.4883 | 6.2776 | 3.5
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.99983 | 19.2458 | 19.5563 | 19.8514 | 20.128 | 20.4665 | 14.42 | 2.5
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 11 | 0.97923 | 8.4854 | 8.6164 | 8.7797 | 8.9384 | 9.0329 | 5.7633 | 2
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 17.6 | 0.99994 | 5.595 | 5.743 | 5.92 | 6.0772 | 6.2163 | 6.2778 | 4.5
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 264 | 0.99999 | 77.0002 | 77.2227 | 77.4753 | 77.9377 | 78.4515 | 0 | 1
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 25.3 | 0.99514 | 16.5503 | 16.815 | 17.1156 | 17.363 | 17.629 | 12.7913 | 1.5
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 52.8 | 0.99225 | 7.768 | 7.7724 | 7.7908 | 7.7781 | 7.758 | 0 | 0.5
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 33 | 0.99462 | 18.8576 | 18.9937 | 19.1543 | 19.3449 | 19.5167 | 12.2673 | 2
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 11 | 0.99995 | 7.2532 | 7.3582 | 7.4626 | 7.5725 | 7.681 | 9.1451 | 3.5
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | 0.99957 | 10.8474 | 11.0043 | 11.1887 | 11.3314 | 11.5239 | 10.1454 | 4
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 11 | 0.99998 | 7.9202 | 7.9374 | 7.9776 | 8.0071 | 8.047 | 5.9561 | 2
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 2.75 | 0.89775 | 0.9025 | 0.90708 | 0.91352 | 0.92111 | 0.92578 | 0.7542 | 4
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0.98392 | 28.9159 | 28.98 | 29.1046 | 29.1738 | 29.2633 | 0 | 4
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 33 | 0.98824 | 24.2817 | 24.3746 | 24.3511 | 24.3646 | 24.3523 | 14.647 | 6
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 3.85 | 0.98888 | 3.5735 | 3.5931 | 3.6213 | 3.6492 | 3.6763 | 0 | 3
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.99999 | 1.3363 | 1.3472 | 1.3589 | 1.3672 | 1.3772 | 0.6948 | 3.5
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 5.5 | 0.99733 | 0.68713 | 0.68787 | 0.68915 | 0.69375 | 0.69381 | 0.48025 | 1.5
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.99185 | 0.8401 | 0.84117 | 0.84418 | 0.84258 | 0.84453 | 0.5622 | 5
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 27.5 | 0.99987 | 16.7871 | 16.813 | 16.8283 | 16.8594 | 16.868 | 9.4489 | 3
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 26.95 | 0.97445 | 17.4775 | 17.4478 | 17.3959 | 17.3776 | 17.3457 | 10.5735 | 1.5
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | 0.94037 | 2.2259 | 2.2387 | 2.2546 | 2.2663 | 2.2812 | 2.0852 | 1
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.79042 | 9.5928 | 9.5684 | 9.5989 | 9.6341 | 9.5644 | 8.9575 | 8.5
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0.98821 | 0.34618 | 0.34489 | 0.34397 | 0.34373 | 0.34307 | 0 | 4
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.66 | 0.96079 | 0.22587 | 0.22353 | 0.22295 | 0.22132 | 0.22001 | 0.2795 | 1.5
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.55 | 0.98892 | 0.34569 | 0.34482 | 0.34385 | 0.34329 | 0.34268 | 0.2306 | 4
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | 0.9976 | 0.90189 | 0.94531 | 0.96288 | 1.0035 | 1.039 | 0.99187 | 2.5
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 25.3 | 0.99966 | 11.047 | 11.1224 | 11.2459 | 11.3549 | 11.4118 | 8.7522 | 3.5
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 33 | 0.99939 | 9.8515 | 9.8579 | 9.9596 | 10.0134 | 10.0445 | 7.1941 | 1
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 33 | 0.99919 | 8.2808 | 8.2945 | 8.3122 | 8.3251 | 8.3511 | 0 | 1
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 50.6 | 0.99809 | 22.9381 | 22.8914 | 26.5215 | 26.4874 | 26.4935 | 13.0245 | 1
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99027 | 21.7656 | 21.8814 | 21.9982 | 22.0289 | 22.1545 | 8.6443 | 1
Coffs Harbour | Dorrigo | 66/11, 132/11 | 7.5/10 | 10 |  | 11 | 0.99073 | 2.4261 | 2.4064 | 2.3872 | 2.3856 | 2.3714 | 1.9091 | 7
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 17.6 | 1 | 5.5769 | 5.6857 | 5.8102 | 5.9392 | 6.0182 | 6.1738 | 3
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 6.875 | 0.9543 | 2.9954 | 3.0051 | 3.0095 | 3.0172 | 3.0195 | 2.4421 | 4
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 26.95 | 0.89633 | 9.2884 | 9.302 | 9.3091 | 9.3352 | 9.308 | 6.1675 | 2
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.97673 | 0.38441 | 0.38704 | 0.38853 | 0.39097 | 0.39411 | 0.3738 | 2
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 33 | 0.99767 | 10.0013 | 10.1553 | 10.2855 | 10.4368 | 10.5895 | 10.7102 | 3
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 33 | 0.99893 | 8.9687 | 8.9873 | 8.9978 | 9.003 | 9.0341 | 8.0251 | 2.5
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 25.3 | 0.99521 | 7.259 | 7.3409 | 7.3922 | 7.4802 | 7.564 | 6.1774 | 4.5
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 33 | 0.98809 | 9.3812 | 9.3714 | 9.3692 | 9.3768 | 9.373 | 8.6323 | 4.5
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.4 | 0.99415 | 1.5535 | 1.549 | 1.5461 | 1.5455 | 1.5454 | 1.3291 | 9
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.99592 | 1.5177 | 1.5162 | 1.516 | 1.5155 | 1.5226 | 1.2006 | 2
Kempsey | North St | 33/11 | 10 | 16 |  | 11 | 0.99182 | 11.464 | 11.568 | 11.6486 | 11.7387 | 11.8063 | 6.1199 | 4
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 16.5 | 0.97584 | 8.0872 | 8.1425 | 8.2017 | 8.2224 | 8.287 | 5.0632 | 1.5
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 5.5 | 0.98412 | 4.2932 | 4.3588 | 4.4202 | 4.5063 | 4.5727 | 2.1242 | 1
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 13.75 | 0.99895 | 6.2886 | 6.3389 | 6.391 | 6.4436 | 6.4903 | 5.0239 | 4
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 33 | 1 | 20.2535 | 20.6408 | 20.9903 | 21.3951 | 21.7854 | 10.8993 | 3
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.98635 | 1.3684 | 1.3663 | 1.3617 | 1.3609 | 1.3593 | 1.0349 | 2
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 33 | 0.99986 | 19.6338 | 19.8642 | 20.0134 | 20.2798 | 23.9659 | 18.5356 | 2.5
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 3.85 | 0.99835 | 2.5526 | 2.6135 | 2.6825 | 2.7489 | 2.82 | 2.0199 | 2
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 8.8 | 0.99185 | 5.1597 | 5.2456 | 5.3316 | 5.4302 | 5.4943 | 5.9601 | 1
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 22 | 0.98745 | 14.3643 | 14.3815 | 14.342 | 14.3295 | 14.3538 | 5.0149 | 3.5
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 16.5 | 0.99188 | 11.7602 | 11.783 | 11.7776 | 14.4493 | 14.5307 | 9.3872 | 1
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.4 | 0.99929 | 1.8218 | 1.8412 | 1.8557 | 1.8708 | 1.896 | 1.5279 | 1.5
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0.99594 | 10.7475 | 10.6999 | 10.6588 | 10.6568 | 10.6426 | 0 | 2.5
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | 0.9521 | 0.84059 | 0.83815 | 0.83833 | 0.83514 | 0.83582 | 0.7455 | 3
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.4 | 0.99987 | 3.5012 | 3.534 | 3.5567 | 3.5982 | 3.6414 | 2.8619 | 1
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 22 | 0.99986 | 7.7296 | 7.7229 | 7.7313 | 7.7326 | 7.742 | 6.8964 | 1
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 7.7 | 0.99082 | 5.8844 | 6.0329 | 6.1651 | 6.3242 | 6.446 | 5.4396 | 2
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 5.5 | 0.98098 | 3.8727 | 3.8988 | 3.9256 | 3.9595 | 3.9798 | 1.3564 | 3
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.99156 | 2.7189 | 2.7472 | 2.7815 | 2.8124 | 2.8584 | 2.0884 | 4.5
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.99871 | 14.4903 | 14.5158 | 14.61 | 14.6784 | 14.7575 | 9.2662 | 2.5
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.9983 | 7.1135 | 7.1241 | 7.1529 | 7.1514 | 7.1834 | 6.7641 | 2.5
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 6.875 | 0.99972 | 3.1608 | 3.2133 | 3.2568 | 3.3133 | 3.363 | 3.481 | 2
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 27.5 | 0.99932 | 9.2834 | 9.1572 | 9.0516 | 8.9077 | 8.7976 | 6.3045 | 4
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 17.6 | 0.99938 | 5.736 | 5.8152 | 5.9169 | 6.0803 | 6.1752 | 3.4698 | 3.5
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 22 | 0.99055 | 18.2529 | 18.1107 | 17.9465 | 17.9088 | 17.8782 | 7.4333 | 4
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 11 | 0.97567 | 11.368 | 11.472 | 11.5386 | 11.6335 | 11.7427 | 5.5829 | 1.5
Stroud | Booral | 33/11 | 3 | 2.5 |  | 2.75 | 0.96076 | 1.5937 | 1.5967 | 1.601 | 1.6047 | 1.5935 | 1.0648 | 2
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.95532 | 3.9231 | 3.967 | 3.9991 | 4.0427 | 4.0878 | 2.1467 | 1.5
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.99017 | 8.5518 | 8.6363 | 8.7133 | 8.8034 | 8.895 | 4.0945 | 1
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.99621 | 8.636 | 8.6394 | 8.6537 | 8.6763 | 8.7077 | 4.7219 | 1
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.96109 | 2.4289 | 2.4285 | 2.4249 | 2.4195 | 2.4174 | 1.3169 | 3.5
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.98631 | 3.6322 | 3.6556 | 3.6679 | 3.7056 | 3.7206 | 2.1099 | 2
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.99944 | 4.0034 | 4.0034 | 4.0005 | 3.9909 | 3.9999 | 2.6233 | 3
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 66 | 0.99556 | 35.1964 | 35.387 | 35.597 | 35.8483 | 36.0596 | 0.0046 | 1.5
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 5.5 | 0.98602 | 2.8222 | 2.8323 | 2.8483 | 2.8468 | 2.8647 | 1.6438 | 1.5
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0.99781 | 8.5528 | 8.6331 | 8.643 | 8.7179 | 8.7254 | 0 | 3.5
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.99973 | 9.2413 | 9.2895 | 9.3253 | 9.3637 | 9.3658 | 5.3491 | 2.5
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply | [5 empty] | 0.99408 | 4.2246 | 4.2435 | 4.2813 | 4.2926 | 4.3201 | 2.0992 | 3
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 2.75 | 0.99995 | 1.666 | 1.6769 | 1.6945 | 1.7122 | 1.7311 | 1.4551 | 2
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 13.75 | 0.99681 | 9.3864 | 9.5352 | 9.6871 | 9.8301 | 9.9385 | 6.7566 | 2
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.95882 | 0.54259 | 0.54426 | 0.54725 | 0.55998 | 0.56326 | 0.1922 | 3
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 13.75 | 0.99468 | 7.7837 | 7.8163 | 7.8604 | 7.896 | 7.9362 | 4.6702 | 3
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.99984 | 7.0355 | 7.0413 | 7.0653 | 7.1256 | 7.1668 | 4.6055 | 4
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 3.85 | 0.95273 | 0.39344 | 0.39648 | 0.39964 | 0.40266 | 0.40564 | 0.1464 | 2
Armidale | Uralla | 66/11 | 8 | 5 |  | 5.5 | 0.95585 | 3.0078 | 3.0118 | 3.0145 | 3.0195 | 3.0313 | 2.6505 | 4
Armidale | Walcha South 66/22kV | 66/22 | 8 | 3 |  | 3.3 | 0.74574 | 1.6662 | 1.6969 | 1.7226 | 1.7502 | 1.7816 | 0.7496 | 4
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.3 | 0.99754 | 1.3538 | 1.3581 | 1.3545 | 1.3566 | 1.3463 | 0.83565 | 4
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.9546 | 0.69209 | 0.69162 | 0.68852 | 0.69083 | 0.6886 | 0.9686 | 3
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | 0.70538 | 0.14788 | 0.14724 | 0.147 | 0.14783 | 0.14768 | 0.1286 | 1.5
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 22 | 0.99737 | 6.0923 | 6.0941 | 6.0917 | 6.0947 | 6.0981 | 5.706 | 7
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 5.5 | 0.99963 | 3.7743 | 3.8509 | 3.9169 | 4.0142 | 4.0876 | 2.6854 | 5
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0.99943 | 0.0038418 | 0.0040717 | 0.004127 | 0.0042382 | 0.0044299 | 0.0126 | 0
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.94717 | 0.7135 | 0.71654 | 0.7188 | 0.72282 | 0.724 | 0.6892 | 4
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.3 | 0.98714 | 2.4754 | 2.4869 | 2.5046 | 2.5218 | 2.5496 | 1.671 | 4
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 33 | 0.99842 | 20.0019 | 20.0459 | 19.935 | 19.9746 | 19.9595 | 11.9755 | 2.5
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | 0.58595 | 1.2883 | 1.3173 | 1.3454 | 1.3733 | 1.4044 | 0.6509 | 3
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.65 | 0.95349 | 0.86053 | 0.86319 | 0.86429 | 0.86338 | 0.86442 | 0 | 3
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 5.5 | 0.95174 | 3.4299 | 3.4275 | 3.4301 | 3.4251 | 3.4266 | 1.2147 | 1
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 5.5 | 0.95151 | 1.8377 | 1.8376 | 1.8394 | 1.8387 | 1.8379 | 0.2811 | 2.5
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | 0.87398 | 0.18339 | 0.18509 | 0.18634 | 0.18832 | 0.18887 | 0.1188 | 1
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.4 | 0.99796 | 3.0168 | 3.032 | 3.0433 | 3.0639 | 3.0754 | 2.0892 | 3.5
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.95227 | 2.1851 | 2.1907 | 2.1991 | 2.2003 | 2.2096 | 0.8643 | 5
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 16.5 | 0.99807 | 14.6841 | 14.7301 | 14.8209 | 14.8335 | 14.9129 | 5.3587 | 5
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.99617 | 5.2681 | 5.2969 | 5.3344 | 5.367 | 5.4164 | 2.3685 | 6
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.98929 | 2.6565 | 2.623 | 2.6415 | 2.6342 | 2.6934 | 0.4279 | 9
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 2.75 | 0.95039 | 1.1403 | 1.143 | 1.1473 | 1.1461 | 1.1491 | 0.5026 | 6
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 33 | 0.99698 | 21.1257 | 21.5391 | 21.8957 | 22.6843 | 31.7055 | 12.2256 | 6
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.954 | 2.6351 | 2.6397 | 2.6465 | 2.6505 | 2.6614 | 1.0272 | 9
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.95514 | 4.1832 | 4.1798 | 4.2013 | 4.2098 | 4.2108 | 0.2327 | 0.5
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | 0.91142 | 2.7498 | 2.7839 | 2.8203 | 2.8525 | 2.9033 | 0.0456 | 19
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.97491 | 2.813 | 2.8515 | 2.8878 | 2.9202 | 2.9629 | 1.1385 | 2
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 5.5 | 0.99647 | 2.1222 | 2.1143 | 2.1153 | 2.108 | 2.1043 | 0.6226 | 2
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 5.5 | 0.99999 | 3.1357 | 3.1586 | 3.1714 | 3.1911 | 3.2152 | 2.2111 | 9
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0.85758 | 1.5118 | 1.5294 | 1.5469 | 1.5668 | 1.5871 | 0.59358 | 2.5
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.99444 | 15.2995 | 15.3108 | 15.2726 | 15.2749 | 15.2755 | 7.9882 | 2
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 11 | 0.98335 | 5.2209 | 5.2558 | 5.288 | 5.3298 | 5.3442 | 2.5107 | 4
Narrabri | Wee Waa | 66/22 | 10 | 16 |  | 11 | 0.94585 | 7.3735 | 7.3895 | 7.3948 | 7.4005 | 7.3878 | 2.6556 | 8
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.15 | 0.99656 | 3.2622 | 3.2547 | 3.251 | 3.258 | 3.2737 | 1.3567 | 6
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.99125 | 22.7353 | 22.7815 | 22.7943 | 22.8737 | 22.9598 | 9.4065 | 3.5
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0.97615 | 0.28048 | 0.27915 | 0.27645 | 0.2804 | 0.27927 | 0.027 | 3
Tamworth | Attunga | 66/11 | 5 | 8 |  | 5.5 | 0.95376 | 3.438 | 3.4378 | 3.4378 | 3.4411 | 3.4305 | 1.2213 | 4
Tamworth | Barraba | 66/11 | 5 | 5 |  | 5.5 | 0.99771 | 2.278 | 2.2758 | 2.2642 | 2.2697 | 2.272 | 1.5665 | 2
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.1 | 0.99691 | 0.69303 | 0.70046 | 0.70422 | 0.70646 | 0.71259 | 0.4782 | 2
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.2 | 0.96276 | 0.96544 | 0.96387 | 0.96306 | 0.96219 | 0.96022 | 0.0795 | 1
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.65 | 0.93857 | 1.2361 | 1.2545 | 1.268 | 1.2795 | 1.2895 | 0.3286 | 6
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.9536 | 1.29 | 1.28 | 1.2754 | 1.2697 | 1.2648 | 0.4739 | 4
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 33 | 1 | 11.639 | 11.6411 | 11.6464 | 11.6504 | 11.66 | 2.6697 | 4.5
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.99059 | 6.0081 | 6.0555 | 6.1053 | 6.1515 | 6.1908 | 3.5458 | 1.5
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.89672 | 5.0743 | 5.0839 | 5.1043 | 5.1158 | 5.118 | 2.0197 | 3
Tamworth | Murrurundi | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.99659 | 2.7679 | 2.7659 | 2.772 | 2.7785 | 2.783 | 1.3808 | 3
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 2.75 | 0.96607 | 1.4937 | 1.4703 | 1.4542 | 1.429 | 1.4148 | 0.91465 | 3
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 33 | 0.99641 | 19.025 | 19.3266 | 19.5122 | 19.7878 | 19.9521 | 8.9196 | 1.5
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.99896 | 6.4738 | 6.4638 | 6.4718 | 6.466 | 6.5016 | 2.5589 | 2
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 11 | 0.98859 | 5.0556 | 5.0582 | 5.07 | 5.0812 | 5.0819 | 0 | 4.5
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.97475 | 0.63273 | 0.63956 | 0.64478 | 0.65244 | 0.65946 | 0.1576 | 6
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 50.6 | 0.99111 | 31.0326 | 30.9196 | 30.953 | 30.9921 | 30.9406 | 8.8689 | 2.5
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99244 | 23.42 | 23.3608 | 23.3436 | 23.3312 | 23.2908 | 10.7096 | 3.5
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.944 | 0.71244 | 0.70375 | 0.6976 | 0.68862 | 0.67918 | 0.1016 | 4.5
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 6.875 | 0.94882 | 2.5888 | 2.5957 | 2.6033 | 2.6063 | 2.6119 | 1.0287 | 2
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 14.3 | 0.99984 | 8.1269 | 8.1524 | 8.143 | 8.1391 | 8.1345 | 5.447 | 3
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 11 | 0.99642 | 5.0418 | 5.0235 | 5.0085 | 5.0009 | 4.9764 | 3.3866 | 6
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | 0.99997 | 2.9148 | 2.9222 | 2.9201 | 2.9261 | 2.9465 | 1.7292 | 2
Beryl | Mudgee | 66/22, 132/22 | 18/30 | 30 |  | 33 | 0.99631 | 22.7853 | 22.777 | 22.8399 | 22.793 | 22.7888 | 13.7005 | 4.5
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 2.75 | 0.95414 | 2.4105 | 2.4102 | 2.4125 | 2.416 | 2.4253 | 1.3496 | 2
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 2.75 | 0.95364 | 1.3495 | 1.3653 | 1.3771 | 1.3977 | 1.4142 | 0.52139 | 4
Wellington | Wellington 11kV | 132/11, 66/11 | 10 | 15 |  | 11 | 0.98489 | 8.9336 | 8.9658 | 8.9588 | 8.9736 | 9.0167 | 4.303 | 5
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 11 | 0.99724 | 5.9406 | 5.9866 | 6.0305 | 6.0743 | 6.1178 | 3.0315 | 4
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 99 | 0.98237 | 57.8413 | 57.787 | 57.6966 | 57.7841 | 57.7811 | 0 | 5
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 33 | 0.96656 | 20.3985 | 20.3699 | 20.2121 | 20.1156 | 20.0048 | 4.9032 | 2
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 33 | 0.99651 | 17.9969 | 18.1692 | 18.3749 | 18.5854 | 18.7759 | 11.4656 | 1.5
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 25.3 | 0.9857 | 15.0969 | 15.2477 | 15.4315 | 15.5594 | 15.6935 | 9.1961 | 3.5
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 33 | 0.99319 | 18.8178 | 18.8893 | 18.9202 | 19.0069 | 19.0462 | 12.8055 | 2.5
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | 0.98039 | 1.5016 | 1.4981 | 1.5108 | 1.5142 | 1.5169 | 0.84383 | 4
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 13.2 | 0.99193 | 6.9087 | 6.9352 | 6.9726 | 6.9988 | 7.0345 | 3.8779 | 2
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.95297 | 1.6408 | 1.6479 | 1.6534 | 1.6595 | 1.6641 | 0.9057 | 1.5
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 26.4 | 0.99849 | 12.1785 | 12.2349 | 12.2555 | 12.2134 | 12.2117 | 6.6888 | 3
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 11 | 0.91841 | 6.7097 | 6.7181 | 6.7154 | 6.7545 | 6.7639 | 2.9493 | 2
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 27.5 | 0.96518 | 7.6319 | 7.637 | 7.6359 | 7.6463 | 7.646 | 1.7417 | 13
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.99942 | 5.299 | 5.3529 | 5.4122 | 5.4702 | 5.5304 | 2.2559 | 9
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.80531 | 3.0799 | 3.143 | 3.1988 | 3.2621 | 3.3227 | 0.6548 | 2
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.1 | 0.99532 | 0.11386 | 0.11431 | 0.11519 | 0.11497 | 0.11513 | 0.0426 | 1
Nyngan | Cobar CSA | 132/11 | 15/18 | 30/45 |  | 19.8 | 0.99151 | 21.8363 | 22.107 | 22.4819 | 22.8201 | 23.2637 | 0 | 7
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 16.5 | 0.916 | 2.125 | 2.1335 | 2.1417 | 2.1663 | 2.2038 | 0 | 1
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 22 | 0.94088 | 15.6132 | 15.6811 | 15.7541 | 15.9004 | 15.9536 | 0 | 129
Nyngan | Cobar Town | 66/22 | 8/11 | 10/13 |  | 12.1 | 0.9565 | 6.2469 | 6.203 | 6.1474 | 6.1 | 6.0389 | 3.8283 | 5
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0.91615 | 3.1302 | 3.1493 | 3.1846 | 3.191 | 3.2208 | 0 | 23
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 33 | 0.99894 | 30.543 | 30.5728 | 30.6147 | 30.618 | 30.6282 | 0 | 14
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 11 | 0.99808 | 7.5041 | 7.5005 | 7.4585 | 7.4173 | 7.3923 | 2.2354 | 2.5
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply | [5 empty] | 0.99328 | 39.3779 | 40.7843 | 42.2206 | 42.2131 | 42.0724 | 18.7411 | 4
Broken Hill | Wilcannia 33kV | [5 empty] | 0.87545 | 0.63398 | 0.65138 | 0.66905 | 0.68667 | 0.70375 | 0.2973 | 4.5
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 5.5 | 0.99992 | 0.88053 | 0.88286 | 0.88736 | 0.89479 | 0.9025 | 0.8644 | 2.5
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.65 | 0.88191 | 1.3183 | 1.3411 | 1.3639 | 1.3872 | 1.4026 | 0.6556 | 9
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.65 | 0.99969 | 0.61856 | 0.62117 | 0.61882 | 0.62375 | 0.63043 | 0.204 | 161
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 16.5 | 0.91833 | 6.8504 | 8.1543 | 9.5691 | 9.6238 | 9.7349 | 0 | 5.5
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | 0.97778 | 0.62273 | 0.6318 | 0.63511 | 0.63478 | 0.64718 | 0.1145 | 3
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.4 | 0.97202 | 2.1246 | 2.1332 | 2.1373 | 2.1275 | 2.1312 | 0.1932 | 5
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 3.85 | 0.97163 | 0.91964 | 0.9309 | 0.94588 | 0.95833 | 0.97184 | 0.5009 | 3.5
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 11 | 1 | 10.168 | 10.289 | 10.3529 | 10.4671 | 10.6243 | 8.3632 | 6
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 33 | 0.9521 | 14.016 | 13.9565 | 13.9341 | 13.9193 | 13.8851 | 5.9488 | 4
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 33 | 0.99264 | 17.3615 | 17.7812 | 18.1446 | 18.611 | 19.1052 | 9.5786 | 4
Orange | Orange West | 66/11 | 30 | 30 |  | 33 | 0.99985 | 12.6007 | 12.5621 | 12.4915 | 12.446 | 12.3399 | 8.7468 | 4
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 2.75 | 0.94683 | 2.3299 | 2.3506 | 2.3926 | 2.4415 | 2.4537 | 1.1495 | 1.5
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 26.4 | 0.96723 | 9.8439 | 9.8484 | 9.8739 | 9.8719 | 9.8693 | 1.7197 | 10
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.4 | 0.99935 | 3.4996 | 3.4799 | 3.5001 | 3.4961 | 3.5065 | 2.0182 | 2
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 22 | 0.98675 | 10.0344 | 10.0891 | 10.1684 | 10.2364 | 10.3064 | 3.8296 | 2
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 2.75 | 0.99564 | 2.1664 | 2.1645 | 2.1631 | 2.1693 | 2.1679 | 1.4182 | 1.5
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 33 | 0.99999 | 18.7976 | 18.8039 | 18.7633 | 18.8111 | 18.8172 | 9.6868 | 2.5
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 66 | 0.99569 | 19.2119 | 19.1111 | 19.1415 | 19.1633 | 19.2396 | 8.0582 | 2.5
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 22 | 0.99982 | 18.3325 | 18.4551 | 18.4983 | 18.676 | 18.6702 | 10.7693 | 2
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0.82741 | 0.44904 | 0.44973 | 0.44809 | 0.44886 | 0.44949 | 0 | 1.5
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 49.5 | 0.90981 | 31.1387 | 32.1113 | 33.0095 | 33.9593 | 34.9375 | 0 | 28
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 16.5 | 0.99966 | 4.991 | 5.0872 | 5.1934 | 5.3026 | 5.4482 | 2.8956 | 3.5
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 33 | 0.99225 | 18.3471 | 18.4797 | 18.6272 | 18.7726 | 18.853 | 9.9435 | 2
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 11 | 0.99815 | 1.6681 | 1.6676 | 1.6657 | 1.6648 | 1.6654 | 1.2628 | 1.5
Parkes | Trundle | 66/22 | 8 | 5 |  | 5.5 | 0.99303 | 3.6325 | 3.678 | 3.6538 | 3.6678 | 3.7101 | 1.92 | 7
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 11 | 0.9999 | 7.046 | 7.0274 | 7.0341 | 7.0226 | 7.0274 | 3.7778 | 6
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 33 | 0.99239 | 13.935 | 13.9903 | 14.0284 | 14.0525 | 14.1059 | 6.8347 | 7
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 7.7 | 0.99942 | 3.6735 | 3.6856 | 3.6947 | 3.7137 | 3.725 | 2.5896 | 5.5
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 5.5 | 0.95551 | 5.8119 | 5.7996 | 5.8327 | 5.8125 | 5.8264 | 1.0442 | 3.5
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.4 | 0.97856 | 2.1 | 2.0946 | 2.0904 | 2.0814 | 2.0734 | 0.4008 | 3
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.99983 | 19.8535 | 19.898 | 19.9688 | 20.0772 | 20.1018 | 10.228 | 2
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.3 | 0.98953 | 1.1874 | 1.1805 | 1.1763 | 1.1725 | 1.1718 | 0.9812 | 2
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 44 | 0.99729 | 21.6493 | 21.891 | 22.1074 | 22.337 | 22.5997 | 0 | 5
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.99637 | 6.0425 | 6.0361 | 6.0273 | 6.0188 | 6.0134 | 4.538 | 5.5
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 13.75 | 0.99757 | 6.7169 | 6.7616 | 6.8439 | 6.8741 | 6.9449 | 5.3181 | 3
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 13.75 | 0.99937 | 5.931 | 5.9563 | 5.9871 | 5.9964 | 6.0254 | 4.4811 | 3.5
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | 0.9977 | 1.9907 | 1.9863 | 1.971 | 1.9545 | 1.9483 | 1.9698 | 6
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 5.5 | 0.99788 | 0.96745 | 0.98961 | 1.0082 | 1.0269 | 1.045 | 0.5827 | 2.5
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 5.5 | 0.78692 | 0.08946 | 0.08849 | 0.089144 | 0.090012 | 0.089285 | 0 | 28
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 22 | 0.99377 | 10.2789 | 10.2785 | 10.278 | 10.2634 | 10.2584 | 5.4267 | 1.5
Cooma | Eucumbene | 66/11 | 0.6 |  |  | 0 | 0.95735 | 0.13866 | 0.13886 | 0.13867 | 0.13887 | 0.13865 | 0.0556 | 4
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 33 | 0.9913 | 4.5412 | 4.5375 | 4.5404 | 4.5352 | 4.5345 | 2.8324 | 3
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0.95445 | 0.36233 | 0.37481 | 0.38623 | 0.39728 | 0.4108 | 0.1494 | 1
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 11 | 0.99905 | 2.222 | 2.2769 | 2.3339 | 2.3944 | 2.4498 | 1.885 | 2
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 0.87388 | 0.13431 | 0.13459 | 0.13361 | 0.13522 | 0.13269 | 0 | 1
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.98677 | 0.50147 | 0.49777 | 0.49703 | 0.51548 | 0.51415 | 0 | 1
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 0.99999 | 0.47437 | 0.48683 | 0.50058 | 0.51353 | 0.52496 | 0.1388 | 3
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 0.99931 | 0.49163 | 0.49795 | 0.48728 | 0.49134 | 0.49081 | 0 | 19.5
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 11 | 0.95464 | 1.2348 | 1.2528 | 1.2852 | 1.3064 | 1.3216 | 0.0698 | 13
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0.6038 | 0.030974 | 0.031083 | 0.031187 | 0.032658 | 0.032721 | 0 | 1
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0.99719 | 2.9611 | 3.0101 | 2.9843 | 3.1277 | 3.069 | 0 | 2
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.98881 | 2.1643 | 2.1846 | 2.2058 | 2.225 | 2.2444 | 0.0302 | 3
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.99949 | 31.883 | 31.9438 | 31.967 | 31.9983 | 32.029 | 0 | 3
Bega | Bermagui | 33/11 | 5 | 5 |  | 5.5 | 0.99762 | 2.6237 | 2.6225 | 2.6253 | 2.6257 | 2.629 | 2.2342 | 2.5
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0.9724 | 0.71357 | 0.71524 | 0.71647 | 0.71665 | 0.718 | 0.4297 | 2
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 2.75 | 0.99933 | 1.1969 | 1.1986 | 1.1997 | 1.1989 | 1.2043 | 1.5723 | 4.5
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.99899 | 4.0353 | 4.0383 | 4.0326 | 4.0306 | 4.0261 | 2.4547 | 2
Bega | Edrom | 66/11 | 5 | 5 |  | 5.5 | 0.90055 | 2.3356 | 2.3416 | 2.3523 | 2.3527 | 2.3645 | 0 | 4.5
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0.99849 | 4.306 | 4.3045 | 4.316 | 4.324 | 4.3434 | 0 | 6.5
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.99105 | 13.7579 | 13.7994 | 13.8249 | 13.8305 | 13.8977 | 7.2377 | 3.5
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 17.6 | 0.99967 | 11.5785 | 11.5524 | 11.5362 | 11.5254 | 11.5073 | 9.0965 | 2.5
Bega | Quira | 66/11 | 5 |  |  | 0 | 0.98869 | 1.2095 | 1.2015 | 1.2004 | 1.2021 | 1.1933 | 0.84258 | 4
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 14.3 | 0.99823 | 4.2645 | 4.2688 | 4.2794 | 4.2808 | 4.2907 | 1.2676 | 7.5
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | 0.99773 | 4.846 | 4.8575 | 4.8685 | 4.8712 | 4.9019 | 0 | 3
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.96772 | 0.69599 | 0.70676 | 0.71683 | 0.72719 | 0.73792 | 0.364 | 8.5
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 2.75 | 0.99709 | 1.3686 | 1.3633 | 1.3717 | 1.3632 | 1.3668 | 1.1938 | 1
Tumut | Batlow | 66/11 | 5 | 5 |  | 5.5 | 0.98731 | 1.602 | 1.5954 | 1.5848 | 1.5842 | 1.583 | 1.0949 | 5
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 8.8 | 0.99639 | 5.9408 | 5.9289 | 5.9393 | 5.9528 | 5.9571 | 2.9837 | 3
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.1 | 0.99982 | 1.0612 | 1.0555 | 1.0512 | 1.0514 | 1.0505 | 0.4682 | 4
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.99999 | 0.096777 | 0.096371 | 0.095673 | 0.095508 | 0.094843 | 0.0692 | 1
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | 0.90824 | 0.53227 | 0.5563 | 0.58133 | 0.60416 | 0.62807 | 0.3241 | 1
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 8.8 | 0.99849 | 7.6416 | 7.6468 | 7.6567 | 7.6723 | 7.6887 | 2.6564 | 3
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 33 | 0.96437 | 13.0185 | 12.8395 | 12.7253 | 12.707 | 12.6699 | 5.6464 | 1
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 1 | 7.8492 | 7.8481 | 7.9498 | 7.9868 | 8.0307 | 6.723 | 3.5
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 5.5 | 0.99951 | 6.2196 | 6.5548 | 6.8951 | 7.2497 | 7.611 | 2.4958 | 9
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 11 | 0.98256 | 0.76249 | 0.7642 | 0.76378 | 0.75655 | 0.75606 | 0 | 1
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 33 | 0.99869 | 8.0895 | 8.3332 | 8.5764 | 8.8236 | 9.0722 | 8.2182 | 3
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 33 | 0.99556 | 12.9012 | 12.8812 | 12.4011 | 12.3893 | 12.3966 | 6.3858 | 3
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 33 | 0.99968 | 21.612 | 21.796 | 16.7191 | 16.9678 | 17.2633 | 13.1815 | 3
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 8.8 | 0.99444 | 3.6729 | 3.7033 | 3.7132 | 3.7325 | 3.7446 | 3.5049 | 3
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 2.75 | 0.96474 | 2.3301 | 2.3537 | 2.3781 | 2.3857 | 2.4004 | 1.8459 | 2.5
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 20.9 | 0.99568 | 12.5545 | 12.6368 | 12.6821 | 12.8251 | 12.9776 | 5.6599 | 3.5
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0.99998 | 3.7885 | 3.7846 | 3.7939 | 3.7924 | 3.8106 | 3.386 | 3
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 33 | 0.99994 | 8.3584 | 8.3773 | 8.3631 | 8.3512 | 8.4054 | 2.9038 | 4.5
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.9919 | 32.0186 | 32.3132 | 32.6433 | 33.0736 | 33.3897 | 0 | 1
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 16.5 | 0.99964 | 7.786 | 7.6807 | 7.7161 | 7.7778 | 7.687 | 0 | 1.5
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 16.5 | 0.99256 | 6.2708 | 6.3187 | 6.3656 | 6.4119 | 6.472 | 2.2553 | 3
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.95655 | 7.5538 | 7.548 | 7.5584 | 7.5814 | 7.5855 | 0 | 4
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 15.4 | 0.99956 | 7.8109 | 7.8176 | 7.8783 | 7.8728 | 7.9009 | 1.189 | 14.5
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | 0.9513 | 1.6979 | 1.7058 | 1.7164 | 1.7213 | 1.7313 | 1.2267 | 1
Cowra | Canowindra | 66/11 | 5 | 8 |  | 5.5 | 0.98735 | 5.8474 | 5.8627 | 5.8793 | 5.8888 | 5.8857 | 3.2063 | 5
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 33 | 0.99751 | 19.2055 | 19.2373 | 19.2566 | 19.2993 | 19.4235 | 9.2977 | 3.5
Cowra | Grenfell | 66/11 | 8 | 5 |  | 5.5 | 0.95272 | 4.4159 | 4.4198 | 4.4181 | 4.4084 | 4.4095 | 3.3739 | 2.5
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.9627 | 0.8666 | 0.86419 | 0.86098 | 0.85814 | 0.85294 | 0.5819 | 2
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 5.5 | 0.98266 | 3.4604 | 3.4796 | 3.498 | 3.5126 | 3.5241 | 2.5076 | 1.5
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 20.9 | 0.99995 | 9.3033 | 9.3388 | 9.3023 | 9.3045 | 9.3084 | 5.8833 | 3
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.15 | 0.9558 | 1.6593 | 1.6651 | 3.4799 | 3.4911 | 3.5026 | 0.3501 | 5
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 11 | 0.98589 | 4.4217 | 4.4057 | 4.3746 | 4.3641 | 4.35 | 3.095 | 4.5
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 33 | 0.99793 | 15.9013 | 15.9559 | 15.9101 | 15.9242 | 15.947 | 8.0122 | 3
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 2.75 | 0.99882 | 1.1066 | 1.116 | 1.1231 | 1.1241 | 1.1314 | 0.9836 | 2
Yass | Marilba | 66/11 | 3 | 1 |  | 1.1 | 1 | 1.4017 | 1.4008 | 1.4152 | 1.4217 | 1.431 | 0.92545 | 2.5
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | 0.99549 | 6.0308 | 6.1336 | 6.2549 | 6.3782 | 6.4574 | 6.1681 | 3
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 14.3 | 0.96978 | 12.0908 | 12.1698 | 12.1896 | 12.2703 | 12.3571 | 6.7919 | 3
Temora | Anona | 66/22 | 3 |  |  | 0 | 0.97872 | 1.3057 | 1.3216 | 1.34 | 1.3561 | 1.3732 | 0.81 | 3.5
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 2.75 | 0.98388 | 0.77769 | 0.77929 | 0.78008 | 0.77963 | 0.78212 | 0.4511 | 3
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.3 | 0.99878 | 0.99541 | 1.0053 | 1.0098 | 1.0196 | 1.0251 | 0.6039 | 4
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | 0.99375 | 0.19266 | 0.1946 | 0.19726 | 0.20035 | 0.20503 | 0.1564 | 2.5
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.99918 | 18.794 | 18.9046 | 21.6336 | 21.6397 | 21.7684 | 0 | 4
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 11 | 0.99797 | 7.1433 | 7.1233 | 7.1035 | 7.1006 | 7.1193 | 4.7146 | 5
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 11 | 0.9725 | 8.0217 | 8.0404 | 10.7641 | 10.7891 | 10.8134 | 4.2703 | 2
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.3 | 0.99939 | 0.70905 | 0.7074 | 0.70554 | 0.70404 | 0.70183 | 0.25365 | 8
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 33 | 0.99322 | 11.0772 | 11.0778 | 11.0681 | 14.5608 | 20.4668 | 0.27455 | 35.5
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/10 | 6.75/10 |  | 11 | 0.99779 | 8.5065 | 8.6527 | 8.7966 | 8.943 | 9.1064 | 3.5028 | 2.5
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.4 | 0.98476 | 1.7218 | 1.7242 | 1.716 | 1.7168 | 1.7117 | 0 | 3
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 8.8 | 0.99301 | 4.6198 | 4.6226 | 4.6223 | 4.6364 | 4.6229 | 3.0297 | 7
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.3 | 0.95791 | 1.2305 | 1.2303 | 1.2239 | 1.2283 | 1.2328 | 0.5303 | 4
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 15.4 | 0.98805 | 4.9477 | 4.9096 | 4.9122 | 4.8966 | 4.8925 | 1.8593 | 2
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | 0.98504 | 0.47995 | 0.47135 | 0.46029 | 0.45282 | 0.44331 | 0.1817 | 3
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 16.5 | 0.9973 | 6.6759 | 6.6761 | 6.6925 | 6.7113 | 6.7178 | 3.2049 | 8
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | 0.99935 | 11.535 | 11.5839 | 11.588 | 11.6196 | 11.6766 | 0 | 2
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.99443 | 0.46632 | 0.46385 | 0.46166 | 0.46023 | 0.46266 | 0.3704 | 2
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.2 | 0.99906 | 1.6303 | 1.6328 | 1.6462 | 1.6596 | 1.6781 | 0 | 4.5
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 7.59 | 0.9765 | 3.6645 | 3.6582 | 3.65 | 3.6548 | 3.6531 | 0.4615 | 6
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.1 | 0.90655 | 1.0447 | 1.0416 | 1.0397 | 1.0351 | 1.0368 | 0.6279 | 4
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 33 | 0.98811 | 18.154 | 18.1625 | 18.1153 | 18.0889 | 18.0195 | 8.025 | 6
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.99687 | 11.8751 | 11.949 | 12.0497 | 12.1143 | 12.1962 | 7.3278 | 3
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0.99517 | 0.1613 | 0.16215 | 0.16298 | 0.16224 | 0.16205 | 0 | 5
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 33 | 0.99979 | 14.3069 | 14.3766 | 14.3336 | 14.3178 | 14.3287 | 3.6557 | 10
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 5.5 | 0.99348 | 2.3613 | 2.3722 | 2.3857 | 2.3999 | 2.4276 | 1.6428 | 5
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 27.5 | 0.99226 | 17.2985 | 17.5401 | 17.7853 | 18.0867 | 18.2599 | 9.1291 | 4
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 5.5 | 0.99083 | 3.2809 | 3.2846 | 3.287 | 3.2935 | 3.3089 | 2.0535 | 5
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 22 | 0.98242 | 11.2127 | 11.2206 | 11.1422 | 11.1046 | 11.1176 | 1.7558 | 4
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 17.6 | 0.99899 | 5.5485 | 5.5579 | 5.5719 | 5.5961 | 5.6013 | 2.7325 | 3
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 7.7 | 0.98532 | 3.7916 | 3.7978 | 3.7954 | 3.8018 | 3.8079 | 2.9537 | 3.5
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 7.7 | 0.99956 | 3.4449 | 3.4511 | 3.4502 | 3.4541 | 3.4526 | 2.3464 | 4
Morven | Morven | 132/66 | 30 |  |  | 0 | 0.9975 | 7.337 | 7.4226 | 7.5308 | 7.6323 | 7.7601 | 0 | 4
Albury | Corowa | 132/22 | 30 | 27/30 |  | 33 | 0.99328 | 14.5955 | 14.5006 | 14.5309 | 14.5162 | 14.5538 | 7.9009 | 2
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 48.4 | 0.99738 | 37.1854 | 37.0883 | 36.9484 | 36.7497 | 36.6153 | 11.8796 | 3.5
Albury | Mulwala | 132/22 | 30 | 30 |  | 33 | 0.9892 | 13.0156 | 13.0413 | 13.0505 | 13.0478 | 13.0843 | 5.2066 | 5.5
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 77 | 0.99361 | 50.7668 | 51.9723 | 53.2006 | 54.3579 | 55.5076 | 33.5575 | 3
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 33 | 0.99982 | 12.1151 | 12.1152 | 12.1581 | 12.1652 | 12.1708 | 8.0445 | 3
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.98859 | 3.012 | 3.0199 | 3.0268 | 3.0343 | 3.0403 | 1.8037 | 7
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 11 | 0.99854 | 5.1704 | 5.2038 | 5.2364 | 5.2976 | 5.3485 | 2.8911 | 2
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 33 | 0.99824 | 19.1245 | 19.0983 | 19.1599 | 19.1075 | 19.131 | 9.5823 | 6
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 5.5 | 0.99479 | 4.568 | 4.6108 | 4.6616 | 4.7142 | 4.7624 | 2.0477 | 3
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 33 | 0.99787 | 14.8495 | 15.0184 | 15.2376 | 15.4644 | 15.641 | 6.3241 | 3
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 5.5 | 0.99946 | 1.5747 | 1.5758 | 1.5788 | 1.5673 | 1.5701 | 0.9199 | 5
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0.86586 | 0.61546 | 0.61211 | 0.60953 | 0.60677 | 0.60246 | 0 | 3.5
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 27.5 | 0.94966 | 12.2918 | 12.3147 | 12.3109 | 12.3529 | 12.3716 | 0.6451 | 3.5
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 8.25 | 0.96169 | 1.7095 | 1.6943 | 1.6782 | 1.6642 | 1.6592 | 0.6977 | 3
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 13.75 | 0.87805 | 3.4266 | 3.4265 | 3.4226 | 3.4157 | 3.4252 | 1.0742 | 3
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 2.75 | 0.88961 | 0.91545 | 0.89372 | 0.8817 | 0.86252 | 0.84691 | 0.1024 | 5
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.76912 | 2.2577 | 2.2449 | 2.228 | 2.2163 | 2.2073 | 0.5057 | 11.5
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.65 | 0.91508 | 0.74788 | 0.73816 | 0.72731 | 0.71686 | 0.70746 | 0.1909 | 4.5
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 33 | 0.99096 | 8.8581 | 8.8796 | 8.8583 | 8.8527 | 8.8591 | 0.993 | 12
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 11 | 0.99255 | 4.7723 | 4.8033 | 4.8316 | 4.8706 | 4.9104 | 2.6437 | 4
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 17.6 | 0.99981 | 11.5286 | 11.5999 | 11.7543 | 11.8307 | 11.992 | 3.0082 | 5
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.1 | 0.9776 | 0.94984 | 0.94652 | 0.9437 | 0.93886 | 0.93669 | 0.256 | 2.5
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 13.75 | 0.954 | 11.1151 | 11.342 | 11.6036 | 11.8768 | 12.1008 | 4.8158 | 4
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 55 | 0.99555 | 23.5002 | 23.5686 | 23.4953 | 23.572 | 23.4998 | 8.2317 | 2
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 27.5 | 0.98624 | 13.9598 | 14.0279 | 14.0652 | 14.1022 | 14.1731 | 1.8229 | 9
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | 0.97628 | 1.9017 | 1.9117 | 1.9229 | 1.9291 | 1.9366 | 0.5927 | 4
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.99912 | 13.6219 | 13.6775 | 13.7406 | 13.7874 | 13.819 | 5.614 | 3
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 2.75 | 0.90323 | 1.0276 | 1.0072 | 1.0019 | 0.98822 | 0.97964 | 0.4552 | 5.5
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0.89507 | 0.46453 | 0.46458 | 0.46593 | 0.46803 | 0.46628 | 0 | 3
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.9423 | 1.8889 | 1.8887 | 1.911 | 1.8936 | 1.8997 | 0.297 | 2
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 10.45 | 0.99994 | 6.7066 | 6.7121 | 6.7155 | 6.7242 | 6.7269 | 1.6291 | 4
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.94866 | 0.42433 | 0.4304 | 0.43702 | 0.44427 | 0.45123 | 0.1534 | 3.5
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.97237 | 18.7223 | 18.6606 | 18.6584 | 18.6349 | 18.5952 | 6.8846 | 5
Yanco | Murrami | 33/11 | 5 | 5 |  | 5.5 | 0.836 | 1.4314 | 1.4314 | 1.4367 | 1.4415 | 1.4393 | 0.3937 | 16
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.96632 | 10.1933 | 10.2666 | 10.2822 | 10.3522 | 10.4214 | 4.1105 | 3
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.97297 | 4.0116 | 3.9924 | 3.9559 | 3.9614 | 3.9384 | 0.8144 | 7
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.97265 | 2.5245 | 2.5253 | 2.534 | 2.5395 | 2.5474 | 1.3394 | 4
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.98314 | 10.3252 | 10.3178 | 10.3147 | 10.3095 | 10.3164 | 0.5928 | 3.5
Buronga | Powercor Robinvale 22kV Euston Distribution Supply | [5 empty] | 0.97758 | 6.1995 | 6.256 | 6.3154 | 6.3696 | 6.4326 | 1.7272 | 10
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply | [5 empty] | 1 | 3.8241 | 3.8354 | 3.8441 | 3.8491 | 3.866 | 1.0693 | 2.5
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 33 | 0.97924 | 14.1329 | 14.1226 | 14.0998 | 14.0616 | 14.0497 | 4.4294 | 2
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 33 | 0.9819 | 7.6196 | 7.4174 | 7.2287 | 7.044 | 6.8867 | 3.3488 | 3
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.99996 | 2.6683 | 2.6738 | 2.6791 | 2.6828 | 2.6813 | 0.48 | 4.5
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0.93212 | 6.6996 | 6.7132 | 6.7084 | 6.7296 | 6.7791 | 0 | 49
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0.99738 | 0.28813 | 0.27507 | 0.26853 | 0.27199 | 0.26424 | 0 | 30

## ZSWinter
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 2024 | 2025 | 2026 | 2027 | 2028
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 36 | 0.99568 | 13.1198 | 13.29 | 13.4779 | 13.6617 | 13.8395 | 13.0061 | 5
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 36 | 0.99946 | 14.4224 | 14.5155 | 14.6264 | 14.7135 | 14.8018 | 12.2954 | 4
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 48 | 0.99902 | 11.7182 | 11.8372 | 11.9194 | 12.0605 | 12.2158 | 0 | 3.5
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 18 | 0.99875 | 11.7559 | 11.9847 | 12.213 | 12.434 | 12.6777 | 13.5074 | 3.5
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99966 | 19.9449 | 20.0183 | 20.1298 | 20.2272 | 20.3744 | 18.9371 | 5.5
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 240 | 0.99995 | 85.2686 | 86.2534 | 87.1839 | 88.3113 | 89.476 | 0 | 3
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 36 | 0.99489 | 7.047 | 7.1823 | 7.3066 | 7.4722 | 7.624 | 8.204 | 3
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 30 | 0.99999 | 11.6842 | 11.718 | 11.7518 | 11.7912 | 11.8135 | 3.9968 | 6
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 36 | 0.99986 | 12.53 | 12.5643 | 12.6212 | 12.6706 | 12.7529 | 12.5318 | 5
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 24 | 0.99899 | 11.4662 | 11.4233 | 11.3705 | 11.3298 | 11.2828 | 12.2065 | 2
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 36 | 0.99706 | 28.2085 | 28.2256 | 28.2952 | 28.1982 | 28.2838 | 22.5388 | 3
Lismore | Ballina 132kV | 132/66 | 75/112 |  |  | 0 | 0.9986 | 20.0696 | 20.1095 | 20.1252 | 20.132 | 20.1206 | 0 | 3
Lismore | Dunoon | 132/11 | 10 | 10 |  | 12 | 0.9956 | 6.7168 | 6.706 | 6.7124 | 6.7213 | 6.7119 | 6.2776 | 4
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 54 | 0.99943 | 17.4927 | 17.5718 | 17.6135 | 17.6799 | 17.777 | 14.42 | 5
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 12 | 0.99612 | 7.0657 | 7.1234 | 7.1752 | 7.235 | 7.2946 | 5.7633 | 3
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 19.2 | 0.99973 | 7.2278 | 7.2946 | 7.3757 | 7.4406 | 7.5019 | 6.2778 | 2
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 288 | 0.99569 | 69.9389 | 69.8073 | 69.6997 | 69.5364 | 69.6541 | 0 | 2
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 27.6 | 0.99983 | 13.6418 | 13.8481 | 14.0799 | 14.2853 | 14.5304 | 12.7913 | 2.5
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 57.6 | 0.9999 | 8.5667 | 8.5894 | 8.5654 | 8.5307 | 8.5592 | 0 | 3
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 36 | 0.99706 | 16.1675 | 16.4131 | 16.7294 | 16.9346 | 17.2463 | 12.2673 | 3
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 12 | 0.99913 | 9.1528 | 9.3086 | 9.4288 | 9.5688 | 9.7243 | 9.1451 | 4
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | 0.99921 | 12.9662 | 13.1012 | 13.2669 | 13.407 | 13.5719 | 10.1454 | 3
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 12 | 0.99967 | 7.0194 | 7.0754 | 7.1268 | 7.196 | 7.2611 | 5.9561 | 3
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 3 | 0.89727 | 0.77598 | 0.77302 | 0.77191 | 0.76947 | 0.76718 | 0.7542 | 8
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0.99774 | 23.4949 | 23.8391 | 24.1438 | 24.4642 | 24.8328 | 0 | 2.5
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 36 | 0.99744 | 19.8993 | 20.0629 | 20.2171 | 20.361 | 20.5329 | 14.647 | 3.5
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 4.2 | 0.99996 | 3.0924 | 3.1428 | 3.1995 | 3.2542 | 3.312 | 0 | 7.5
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 3 | 0.99945 | 1.2494 | 1.2606 | 1.2703 | 1.2831 | 1.2965 | 0.6948 | 4
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 6 | 0.99991 | 0.61242 | 0.6292 | 0.66884 | 0.69487 | 0.72471 | 0.48025 | 1.5
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 3 | 0.99876 | 0.95324 | 0.97027 | 0.98939 | 1.009 | 1.028 | 0.5622 | 7
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 30 | 0.99314 | 13.0885 | 13.13 | 13.1663 | 13.2002 | 13.2423 | 9.4489 | 4
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 29.4 | 0.99955 | 13.0305 | 13.0718 | 13.1089 | 13.141 | 13.2008 | 10.5735 | 3
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | 0.97347 | 2.5383 | 2.584 | 2.633 | 2.6789 | 2.7267 | 2.0852 | 1
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.69851 | 9.0838 | 9.0488 | 9.0774 | 9.1002 | 9.0645 | 8.9575 | 7.5
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0.9975 | 0.33171 | 0.33244 | 0.33237 | 0.33216 | 0.33227 | 0 | 5.5
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.72 | 0.95936 | 0.2799 | 0.28157 | 0.27915 | 0.28127 | 0.2854 | 0.2795 | 3
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.6 | 0.99757 | 0.33161 | 0.3316 | 0.33166 | 0.33217 | 0.33217 | 0.2306 | 5.5
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | 0.99971 | 1.1346 | 1.1627 | 1.187 | 1.2111 | 1.2384 | 0.99187 | 8
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 27.6 | 0.99372 | 10.4892 | 10.5299 | 10.5045 | 10.4915 | 10.462 | 8.7522 | 6
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 36 | 0.99781 | 10.4002 | 10.5334 | 10.6552 | 10.8242 | 10.972 | 7.1941 | 3.5
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 36 | 0.99048 | 8.8899 | 8.935 | 9.0011 | 9.0523 | 9.1222 | 0 | 3
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 55.2 | 0.99988 | 21.8617 | 22.056 | 25.8281 | 26.0415 | 26.2052 | 13.0245 | 4.5
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 36 | 0.99999 | 17.2676 | 17.4199 | 17.5865 | 17.7422 | 17.9006 | 8.6443 | 6
Coffs Harbour | Dorrigo | 66/11, 132/11 | 7.5/10 | 10 |  | 12 | 0.9993 | 2.6758 | 2.676 | 2.6748 | 2.6803 | 2.6792 | 1.9091 | 4.5
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.99936 | 5.8425 | 6.0067 | 6.1834 | 6.3575 | 6.5326 | 6.1738 | 3
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 7.5 | 0.95334 | 2.8069 | 2.8855 | 2.9558 | 3.0403 | 3.1241 | 2.4421 | 7
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 29.4 | 0.91279 | 10.3324 | 10.4193 | 10.5089 | 10.6091 | 10.7367 | 6.1675 | 7
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.97852 | 0.48253 | 0.49181 | 0.5019 | 0.51208 | 0.52243 | 0.3738 | 3.5
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 36 | 0.99393 | 12.538 | 12.8139 | 13.1081 | 13.3658 | 13.6562 | 10.7102 | 3.5
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 36 | 0.99956 | 9.6358 | 9.7096 | 9.7801 | 9.8465 | 9.9367 | 8.0251 | 5.5
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 27.6 | 0.9968 | 8.6352 | 8.6873 | 8.7444 | 8.8123 | 8.8632 | 6.1774 | 4
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 36 | 0.99892 | 11.1356 | 11.1154 | 11.1334 | 11.1477 | 11.1328 | 8.6323 | 3
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.8 | 0.99537 | 1.9542 | 1.9517 | 1.959 | 1.9623 | 1.9598 | 1.3291 | 1.5
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.6 | 0.99787 | 1.2346 | 1.2696 | 1.3038 | 1.3355 | 1.3724 | 1.2006 | 8.5
Kempsey | North St | 33/11 | 10 | 16 |  | 12 | 0.99782 | 10.3714 | 10.4832 | 10.5979 | 10.7301 | 10.8434 | 6.1199 | 7
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 18 | 0.99958 | 7.8266 | 7.8517 | 7.852 | 7.8468 | 7.8832 | 5.0632 | 9
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 6 | 0.99695 | 3.9923 | 4.0732 | 4.164 | 4.2443 | 4.3323 | 2.1242 | 4.5
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 15 | 0.99584 | 7.3952 | 7.538 | 7.6775 | 7.7984 | 7.9668 | 5.0239 | 1.5
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 36 | 0.99671 | 18.1147 | 18.2018 | 18.3012 | 18.465 | 18.5546 | 10.8993 | 3.5
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.6 | 0.99133 | 1.3406 | 1.345 | 1.3513 | 1.359 | 1.37 | 1.0349 | 2
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 36 | 0.99883 | 22.5807 | 23.0195 | 23.4388 | 23.8837 | 27.7519 | 18.5356 | 2.5
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 4.2 | 0.99964 | 2.1208 | 2.1951 | 2.2681 | 2.3445 | 2.4238 | 2.0199 | 2
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 9.6 | 0.99741 | 6.5633 | 6.8396 | 7.0986 | 7.3774 | 7.6522 | 5.9601 | 2
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 24 | 0.99012 | 16.1861 | 16.1891 | 16.1966 | 16.1944 | 16.2006 | 5.0149 | 3.5
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 18 | 1 | 11.4907 | 11.848 | 12.2164 | 15.2853 | 15.6592 | 9.3872 | 2
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.8 | 0.99817 | 1.7229 | 1.7792 | 1.8314 | 1.8905 | 1.9458 | 1.5279 | 5
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0.99882 | 12.15 | 12.4732 | 12.8211 | 13.1918 | 13.5434 | 0 | 2
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | 0.96279 | 1.0026 | 1.0008 | 0.99815 | 0.99521 | 0.99137 | 0.7455 | 5
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.8 | 0.99812 | 3.8158 | 3.88 | 3.9353 | 4.0074 | 4.0682 | 2.8619 | 1.5
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 24 | 0.99936 | 8.5346 | 8.6191 | 8.6613 | 8.7771 | 8.8036 | 6.8964 | 2
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 8.4 | 0.99882 | 6.8999 | 7.0203 | 7.1794 | 7.3253 | 7.4633 | 5.4396 | 2
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 6 | 0.99702 | 3.9845 | 3.9829 | 3.9824 | 3.9819 | 3.9837 | 1.3564 | 1.5
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 0.99949 | 2.5189 | 2.5791 | 2.6233 | 2.6846 | 2.7437 | 2.0884 | 3
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99898 | 16.3492 | 16.5372 | 16.7184 | 16.9048 | 17.0734 | 9.2662 | 2.5
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 19.2 | 0.99671 | 8.291 | 8.3124 | 8.3216 | 8.3423 | 8.3473 | 6.7641 | 4
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 7.5 | 0.9998 | 3.5769 | 3.6849 | 3.788 | 3.9048 | 4.0011 | 3.481 | 3
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 30 | 0.98961 | 11.3131 | 11.3943 | 11.4803 | 11.5753 | 11.6374 | 6.3045 | 12
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 19.2 | 0.99992 | 7.1914 | 7.2186 | 7.2462 | 7.2597 | 7.3221 | 3.4698 | 4.5
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 24 | 0.9978 | 15.0841 | 15.0529 | 15.0945 | 15.0627 | 15.0761 | 7.4333 | 7
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 12 | 0.99574 | 8.4679 | 8.6284 | 8.7839 | 8.9636 | 9.1463 | 5.5829 | 8
Stroud | Booral | 33/11 | 3 | 2.5 |  | 3 | 0.95321 | 1.152 | 1.1488 | 1.1522 | 1.1506 | 1.1505 | 1.0648 | 6
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 0.98901 | 3.1816 | 3.2491 | 3.3155 | 3.3831 | 3.4485 | 2.1467 | 9
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99971 | 6.0988 | 6.1097 | 6.1346 | 6.1646 | 6.1994 | 4.0945 | 5.5
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99525 | 7.3597 | 7.3693 | 7.38 | 7.4012 | 7.4102 | 4.7219 | 8
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 0.99655 | 1.7003 | 1.7239 | 1.7477 | 1.7757 | 1.801 | 1.3169 | 5
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 9.6 | 0.99996 | 2.3738 | 2.4048 | 2.441 | 2.4731 | 2.5088 | 2.1099 | 9
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 9.6 | 0.99999 | 4.7228 | 4.7766 | 4.8207 | 4.8718 | 4.9439 | 2.6233 | 2.5
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 72 | 0.99647 | 38.145 | 38.5655 | 39.147 | 39.6831 | 40.1863 | 0.0046 | 5
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 6 | 0.99989 | 2.1849 | 2.1814 | 2.1767 | 2.1683 | 2.1732 | 1.6438 | 4
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0.9991 | 8.4038 | 8.4986 | 8.5838 | 8.6984 | 8.7981 | 0 | 4
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99959 | 7.7353 | 7.7581 | 7.7859 | 7.8331 | 7.8664 | 5.3491 | 5
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply | [5 empty] | 0.99852 | 5.647 | 5.703 | 5.7614 | 5.8072 | 5.8741 | 2.0992 | 11
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 3 | 0.99983 | 2.1848 | 2.2163 | 2.2556 | 2.2951 | 2.3326 | 1.4551 | 6
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 15 | 0.99936 | 13.5687 | 13.7078 | 13.9163 | 14.0748 | 14.2399 | 6.7566 | 4
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.98111 | 0.44325 | 0.4673 | 0.49358 | 0.50834 | 0.5211 | 0.1922 | 5.5
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 15 | 0.99358 | 12.0127 | 12.2889 | 12.5655 | 12.8117 | 13.1225 | 4.6702 | 5
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 19.2 | 0.99999 | 10.0884 | 10.1021 | 10.1291 | 10.1347 | 10.162 | 4.6055 | 4
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 4.2 | 0.94647 | 0.45315 | 0.45357 | 0.4544 | 0.45574 | 0.45739 | 0.1464 | 7
Armidale | Uralla | 66/11 | 8 | 5 |  | 6 | 0.95685 | 3.8297 | 3.8426 | 3.8561 | 3.8838 | 3.8962 | 2.6505 | 6
Armidale | Walcha South 66/22kV | 66/22 | 8 | 3 |  | 3.6 | 0.74027 | 2.3369 | 2.356 | 2.3722 | 2.3957 | 2.4161 | 0.7496 | 5.5
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.6 | 0.99973 | 1.6793 | 1.7091 | 1.7457 | 1.7797 | 1.8122 | 0.83565 | 12
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.95189 | 0.96137 | 0.97442 | 0.98974 | 1.002 | 1.0159 | 0.9686 | 2
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | 0.78501 | 0.16105 | 0.16168 | 0.16138 | 0.16179 | 0.16218 | 0.1286 | 2
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 24 | 0.99956 | 8.9263 | 8.9864 | 9.0424 | 9.1092 | 9.1873 | 5.706 | 4
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 6 | 0.99959 | 4.53 | 4.584 | 4.6423 | 4.688 | 4.7436 | 2.6854 | 9
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0.99988 | 0.0012496 | 0.0012033 | 0.0011768 | 0.0011442 | 0.001242 | 0.0126 | 0
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.95241 | 0.5995 | 0.60576 | 0.61053 | 0.61525 | 0.62082 | 0.6892 | 7
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.6 | 0.97463 | 2.2378 | 2.2836 | 2.3361 | 2.3858 | 2.4442 | 1.671 | 3.5
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 36 | 1 | 20.9271 | 21.0577 | 21.2006 | 21.3089 | 21.3904 | 11.9755 | 4
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | 0.66286 | 1.3463 | 1.3566 | 1.3653 | 1.3753 | 1.384 | 0.6509 | 5
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.8 | 0.9524 | 0.941 | 0.94139 | 0.94461 | 0.94366 | 0.9444 | 0 | 1.5
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 6 | 0.95243 | 2.4081 | 2.4273 | 2.4479 | 2.4776 | 2.4966 | 1.2147 | 2
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 6 | 0.95092 | 1.8132 | 1.8584 | 1.9006 | 1.9481 | 1.9903 | 0.2811 | 1.5
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | 0.88986 | 0.21172 | 0.21347 | 0.2153 | 0.2173 | 0.21899 | 0.1188 | 2
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.8 | 0.97166 | 2.8746 | 2.9135 | 2.9624 | 3.0015 | 3.0524 | 2.0892 | 4.5
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.95096 | 1.784 | 1.785 | 1.7879 | 1.7911 | 1.7923 | 0.8643 | 5
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 18 | 0.99855 | 17.4578 | 17.4957 | 17.4934 | 17.4651 | 17.5198 | 5.3587 | 3
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.98677 | 5.2869 | 5.4262 | 5.5697 | 5.7085 | 5.8532 | 2.3685 | 15
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.99429 | 3.8199 | 3.8795 | 3.8479 | 3.8289 | 3.858 | 0.4279 | 15
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 3 | 0.99435 | 0.91462 | 0.92873 | 0.9445 | 0.95648 | 0.97034 | 0.5026 | 4
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 36 | 0.99876 | 22.5967 | 22.7826 | 23.3752 | 32.2518 | 35.6416 | 12.2256 | 14
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.95217 | 5.7115 | 5.6979 | 5.7078 | 5.7098 | 5.7041 | 1.0272 | 15.5
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.956 | 6.3955 | 6.4067 | 6.3701 | 6.3878 | 6.3897 | 0.2327 | 8
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | 0.92977 | 2.97 | 3.0088 | 3.0251 | 3.0342 | 3.0752 | 0.0456 | 35
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.92228 | 2.4101 | 2.4347 | 2.4548 | 2.479 | 2.4973 | 1.1385 | 3
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 6 | 0.99529 | 1.6484 | 1.6452 | 1.6474 | 1.6484 | 1.6525 | 0.6226 | 4
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 6 | 0.99594 | 3.1278 | 3.1514 | 3.1826 | 3.2077 | 3.2324 | 2.2111 | 4
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0.99638 | 2.553 | 2.5618 | 2.5602 | 2.5599 | 2.5568 | 0.59358 | 27.5
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 36 | 0.994 | 17.4484 | 17.4258 | 17.3788 | 17.3794 | 17.329 | 7.9882 | 7
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 12 | 0.95527 | 5.1596 | 5.3079 | 5.4173 | 5.5521 | 5.6772 | 2.5107 | 2.5
Narrabri | Wee Waa | 66/22 | 10 | 16 |  | 12 | 0.97622 | 10.1658 | 10.2788 | 10.4376 | 10.5955 | 10.707 | 2.6556 | 10.5
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.8 | 0.99539 | 4.8655 | 4.938 | 5.0149 | 5.0835 | 5.1724 | 1.3567 | 8
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 36 | 0.98392 | 21.2574 | 21.6706 | 22.0356 | 22.3325 | 22.7331 | 9.4065 | 4
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0.98816 | 0.19126 | 0.19534 | 0.20003 | 0.20406 | 0.20887 | 0.027 | 2
Tamworth | Attunga | 66/11 | 5 | 8 |  | 6 | 0.95088 | 2.3535 | 2.3569 | 2.359 | 2.3627 | 2.3635 | 1.2213 | 7
Tamworth | Barraba | 66/11 | 5 | 5 |  | 6 | 0.99992 | 2.2964 | 2.3096 | 2.3254 | 2.3364 | 2.3503 | 1.5665 | 9
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.2 | 0.99874 | 0.73352 | 0.73657 | 0.7397 | 0.74292 | 0.74648 | 0.4782 | 6
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.4 | 0.95024 | 0.67697 | 0.67839 | 0.68011 | 0.68431 | 0.68719 | 0.0795 | 2
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.8 | 0.9774 | 0.97469 | 0.97556 | 0.97575 | 0.97624 | 0.97601 | 0.3286 | 5
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.95236 | 1.0761 | 1.0894 | 1.1011 | 1.1153 | 1.1284 | 0.4739 | 6
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 36 | 0.99582 | 10.5321 | 10.6781 | 10.8537 | 11.0132 | 11.1906 | 2.6697 | 15.5
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.99718 | 5.6426 | 5.7394 | 5.8211 | 5.942 | 6.0462 | 3.5458 | 5
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 7.5 | 0.90314 | 3.8148 | 3.8453 | 3.8737 | 3.9064 | 3.9306 | 2.0197 | 4
Tamworth | Murrurundi | 33/11 | 5/8 | 5/8 |  | 9.6 | 0.99988 | 2.544 | 2.5872 | 2.6363 | 2.6839 | 2.7324 | 1.3808 | 6.5
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 3 | 0.95671 | 1.6628 | 1.6895 | 1.7117 | 1.7377 | 1.7608 | 0.91465 | 2
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 36 | 0.9933 | 18.7121 | 19.0735 | 19.4602 | 19.8181 | 20.198 | 8.9196 | 6
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 15.96 | 0.99964 | 5.9585 | 6.0983 | 6.2387 | 6.3775 | 6.5391 | 2.5589 | 4
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 12 | 0.99982 | 4.3806 | 4.4633 | 4.5481 | 4.6239 | 4.7076 | 0 | 5
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.98414 | 0.64641 | 0.64771 | 0.6493 | 0.64763 | 0.64992 | 0.1576 | 5
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 55.2 | 0.9994 | 26.9817 | 26.976 | 27.0707 | 27.135 | 27.2383 | 8.8689 | 4
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 36 | 0.99824 | 23.2736 | 23.4142 | 23.5679 | 23.7315 | 23.9527 | 10.7096 | 3.5
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.97488 | 0.50238 | 0.50222 | 0.49839 | 0.49841 | 0.49504 | 0.1016 | 1.5
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 7.5 | 0.94687 | 2.3357 | 2.3342 | 2.3309 | 2.3284 | 2.3281 | 1.0287 | 4.5
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 15.6 | 0.99274 | 8.5466 | 8.6329 | 8.7124 | 8.7902 | 8.8757 | 5.447 | 5
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 12 | 0.98734 | 5.435 | 5.523 | 5.5998 | 5.6693 | 5.7582 | 3.3866 | 8
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | 0.99966 | 3.4559 | 3.4657 | 3.4613 | 3.4687 | 3.4697 | 1.7292 | 7
Beryl | Mudgee | 66/22, 132/22 | 18/30 | 30 |  | 36 | 0.99843 | 24.2435 | 24.6626 | 25.0998 | 25.5339 | 25.9969 | 13.7005 | 11
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 3 | 0.95454 | 3.0031 | 3.0889 | 3.1804 | 3.2731 | 3.3431 | 1.3496 | 1
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 3 | 0.9537 | 1.1217 | 1.1223 | 1.123 | 1.121 | 1.1224 | 0.52139 | 12.5
Wellington | Wellington 11kV | 132/11, 66/11 | 10 | 15 |  | 12 | 0.99702 | 9.054 | 9.1252 | 9.2291 | 9.3355 | 9.4172 | 4.303 | 4.5
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 12 | 0.97847 | 5.3522 | 5.3849 | 5.418 | 5.4465 | 5.4896 | 3.0315 | 10.5
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 108 | 0.99742 | 53.1354 | 53.6961 | 54.0883 | 54.5758 | 54.9448 | 0 | 7.5
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 36 | 0.97516 | 17.9516 | 17.8693 | 17.836 | 17.7956 | 17.7441 | 4.9032 | 9
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 36 | 0.99999 | 17.3259 | 17.4318 | 17.6045 | 17.6929 | 17.7584 | 11.4656 | 3
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 27.6 | 0.99844 | 14.0333 | 14.1119 | 14.1846 | 14.2727 | 14.363 | 9.1961 | 6
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 36 | 0.99983 | 17.455 | 17.4766 | 17.5072 | 17.5487 | 17.5303 | 12.8055 | 6
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | 0.99799 | 1.2272 | 1.2286 | 1.2255 | 1.2312 | 1.2316 | 0.84383 | 6.5
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 14.4 | 0.99901 | 6.324 | 6.3596 | 6.4006 | 6.4546 | 6.4897 | 3.8779 | 7.5
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.952 | 1.5384 | 1.5298 | 1.5244 | 1.5198 | 1.5148 | 0.9057 | 6
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 28.8 | 0.99999 | 12.5598 | 12.6813 | 12.7867 | 12.917 | 13.1106 | 6.6888 | 6.5
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 12 | 0.99661 | 8.381 | 8.3372 | 8.375 | 8.3513 | 8.3538 | 2.9493 | 8
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 30 | 0.96982 | 6.9309 | 6.925 | 6.9334 | 6.9448 | 6.9542 | 1.7417 | 19
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 12 | 0.99766 | 6.2004 | 6.2336 | 6.2449 | 6.2689 | 6.3308 | 2.2559 | 4
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.60579 | 2.8209 | 2.8189 | 2.823 | 2.8235 | 2.8234 | 0.6548 | 1.5
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.2 | 0.97541 | 0.080177 | 0.080322 | 0.080816 | 0.081066 | 0.081217 | 0.0426 | 1
Nyngan | Cobar CSA | 132/11 | 15/18 | 30/45 |  | 21.6 | 0.98968 | 17.8694 | 17.9593 | 18.0026 | 18.0619 | 18.1327 | 0 | 6.5
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 18 | 0.89463 | 2.0129 | 1.9202 | 1.9198 | 1.8973 | 1.855 | 0 | 14
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 24 | 0.95125 | 11.1187 | 11.2622 | 11.3603 | 11.4584 | 11.5695 | 0 | 142
Nyngan | Cobar Town | 66/22 | 8/11 | 10/13 |  | 13.2 | 0.95229 | 5.8611 | 5.8638 | 5.8719 | 5.8637 | 5.8689 | 3.8283 | 6
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0.91419 | 3.1818 | 3.2408 | 3.299 | 3.3594 | 3.4152 | 0 | 8
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 36 | 0.99989 | 29.1876 | 29.2794 | 29.402 | 29.5572 | 29.6234 | 0 | 10
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 12 | 0.99477 | 6.9659 | 7.1026 | 7.2612 | 7.4168 | 7.5849 | 2.2354 | 7
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply | [5 empty] | 0.99997 | 36.6413 | 38.1102 | 39.6098 | 39.6382 | 39.6895 | 18.7411 | 15
Broken Hill | Wilcannia 33kV | [5 empty] | 0.80151 | 0.57184 | 0.58045 | 0.58783 | 0.59608 | 0.60425 | 0.2973 | 8.5
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 6 | 0.99605 | 0.71034 | 0.71203 | 0.71417 | 0.7172 | 0.71756 | 0.8644 | 6
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.8 | 0.77239 | 1.1888 | 1.2384 | 1.288 | 1.3395 | 1.3906 | 0.6556 | 12.5
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.8 | 0.95041 | 0.48398 | 0.47723 | 0.46769 | 0.46405 | 0.46271 | 0.204 | 28
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 18 | 0.83013 | 6.3164 | 7.5581 | 8.8547 | 8.9015 | 8.9564 | 0 | 15
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | 0.94978 | 0.66176 | 0.66667 | 0.67018 | 0.67747 | 0.68161 | 0.1145 | 1
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.8 | 0.95574 | 1.869 | 1.9354 | 1.991 | 2.0418 | 2.0918 | 0.1932 | 10
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 4.2 | 0.99273 | 0.93863 | 0.95651 | 0.97393 | 0.9908 | 1.0068 | 0.5009 | 4
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 12 | 0.99965 | 12.0644 | 12.219 | 12.3471 | 12.5234 | 12.6332 | 8.3632 | 5.5
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 36 | 0.93922 | 16.1422 | 16.1342 | 16.1229 | 16.1272 | 16.0704 | 5.9488 | 8
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 36 | 0.99595 | 23.2854 | 23.5234 | 23.7736 | 24.0319 | 24.2851 | 9.5786 | 10
Orange | Orange West | 66/11 | 30 | 30 |  | 36 | 0.99992 | 14.653 | 14.7508 | 14.8541 | 14.9862 | 15.105 | 8.7468 | 8
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 3 | 0.95193 | 1.8268 | 1.8697 | 1.923 | 1.9759 | 2.0205 | 1.1495 | 3
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 28.8 | 0.97772 | 9.5567 | 9.5513 | 9.5361 | 9.5239 | 9.5183 | 1.7197 | 19
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.8 | 0.99783 | 3.5626 | 3.5821 | 3.6051 | 3.6273 | 3.6483 | 2.0182 | 3
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 24 | 0.99086 | 12.6113 | 12.7173 | 12.851 | 12.9302 | 13.0218 | 3.8296 | 5.5
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 3 | 0.99895 | 2.4918 | 2.5051 | 2.5191 | 2.5298 | 2.5422 | 1.4182 | 4
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 36 | 0.99961 | 21.1234 | 21.2195 | 21.3259 | 21.4143 | 21.518 | 9.6868 | 8
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 72 | 0.99495 | 25.1333 | 25.0718 | 25.0958 | 25.084 | 25.0618 | 8.0582 | 4
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 24 | 0.99844 | 20.4497 | 20.6761 | 20.9827 | 21.1878 | 21.4838 | 10.7693 | 4
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0.84917 | 0.51779 | 0.51877 | 0.51888 | 0.52089 | 0.52183 | 0 | 1.5
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 54 | 0.90593 | 34.1302 | 34.7676 | 35.4611 | 36.1434 | 36.8582 | 0 | 32.5
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 18 | 0.99995 | 5.8841 | 5.8867 | 5.9133 | 5.917 | 5.9363 | 2.8956 | 10
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 36 | 0.99861 | 17.0784 | 17.3317 | 17.5678 | 17.791 | 18.0194 | 9.9435 | 3
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 12 | 0.99997 | 1.4788 | 1.4782 | 1.4794 | 1.4807 | 1.482 | 1.2628 | 3.5
Parkes | Trundle | 66/22 | 8 | 5 |  | 6 | 0.99386 | 3.167 | 3.2051 | 3.129 | 3.1897 | 3.2266 | 1.92 | 7
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 12 | 0.99582 | 6.9882 | 7.0672 | 7.1356 | 7.1979 | 7.2751 | 3.7778 | 4
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 36 | 0.99594 | 11.5347 | 11.5539 | 11.5762 | 11.5927 | 11.6075 | 6.8347 | 6
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 8.4 | 0.98845 | 3.4062 | 3.4083 | 3.4178 | 3.4223 | 3.4291 | 2.5896 | 2
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 6 | 0.94304 | 4.1812 | 4.2121 | 4.2017 | 4.2315 | 4.2352 | 1.0442 | 4
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.8 | 0.99873 | 1.5073 | 1.5005 | 1.495 | 1.4934 | 1.5038 | 0.4008 | 1.5
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 54 | 0.99953 | 20.6073 | 20.7526 | 20.891 | 21.0308 | 21.1292 | 10.228 | 8.5
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.6 | 0.99945 | 1.4369 | 1.4436 | 1.4521 | 1.4584 | 1.4663 | 0.9812 | 4.5
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 48 | 0.99758 | 35.3049 | 35.5495 | 35.8121 | 36.1729 | 36.4755 | 0 | 1.5
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.99984 | 7.6481 | 7.7587 | 7.8534 | 7.958 | 8.0712 | 4.538 | 5
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 15 | 0.99432 | 9.0095 | 9.0662 | 9.188 | 9.2579 | 9.3523 | 5.3181 | 5.5
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 15 | 0.99991 | 8.2972 | 8.3546 | 8.4297 | 8.5054 | 8.5701 | 4.4811 | 5
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | 0.99923 | 2.6986 | 2.7549 | 2.8042 | 2.8508 | 2.9028 | 1.9698 | 4
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 6 | 0.9945 | 1.372 | 1.3684 | 1.3712 | 1.3669 | 1.369 | 0.5827 | 5
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 6 | 0.97071 | 0.2685 | 0.26853 | 0.26603 | 0.26728 | 0.27515 | 0 | 25
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 24 | 0.9986 | 13.7364 | 13.9394 | 14.1121 | 14.3173 | 14.5039 | 5.4267 | 9.5
Cooma | Eucumbene | 66/11 | 0.6 |  |  | 0 | 0.96169 | 0.23562 | 0.24027 | 0.24437 | 0.24825 | 0.25269 | 0.0556 | 3
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 36 | 0.99965 | 12.1455 | 12.2791 | 12.4519 | 12.5608 | 12.7176 | 2.8324 | 7
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0.99832 | 0.73039 | 0.72741 | 0.72716 | 0.72727 | 0.72575 | 0.1494 | 2
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 12 | 0.99708 | 5.0013 | 5.1149 | 5.2204 | 5.3213 | 5.4367 | 1.885 | 5.5
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 1 | 0.18362 | 0.18478 | 0.18505 | 0.18395 | 0.18511 | 0 | 1
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.87312 | 5.3383 | 5.3219 | 5.3218 | 5.3119 | 5.3071 | 0 | 14
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 1 | 1.1858 | 1.2289 | 1.2687 | 1.3041 | 1.3449 | 0.1388 | 4
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 0.99641 | 0.94874 | 0.94997 | 0.94959 | 0.94713 | 0.94936 | 0 | 3
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 12 | 0.95848 | 9.157 | 9.2047 | 9.2587 | 9.3145 | 9.3836 | 0.0698 | 3.5
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0.89268 | 0.028337 | 0.028218 | 0.028152 | 0.028486 | 0.02849 | 0 | 5
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0.99921 | 8.1786 | 8.2743 | 8.2535 | 8.1958 | 8.305 | 0 | 6
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.9632 | 13.63 | 13.6299 | 13.622 | 13.594 | 13.5969 | 0.0302 | 14
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.99988 | 43.9756 | 45.1558 | 46.1799 | 47.2548 | 48.3261 | 0 | 8.5
Bega | Bermagui | 33/11 | 5 | 5 |  | 6 | 0.99973 | 3.3766 | 3.4419 | 3.491 | 3.5466 | 3.6039 | 2.2342 | 7
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0.97631 | 0.74652 | 0.76453 | 0.78048 | 0.79615 | 0.8111 | 0.4297 | 3
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 3 | 0.99844 | 1.7035 | 1.7332 | 1.7589 | 1.7811 | 1.8175 | 1.5723 | 4
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.99834 | 4.7712 | 4.8473 | 4.9354 | 5.0208 | 5.1097 | 2.4547 | 13
Bega | Edrom | 66/11 | 5 | 5 |  | 6 | 0.91595 | 2.2684 | 2.2661 | 2.2643 | 2.2555 | 2.2516 | 0 | 3.5
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0.99622 | 6.033 | 6.246 | 6.4469 | 6.6661 | 6.8488 | 0 | 6
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 36 | 0.99753 | 16.2385 | 16.4237 | 16.6363 | 16.8453 | 17.0505 | 7.2377 | 8
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 19.2 | 0.99944 | 17.1237 | 17.2121 | 17.3449 | 17.4513 | 17.5674 | 9.0965 | 7.5
Bega | Quira | 66/11 | 5 |  |  | 0 | 0.97618 | 1.5628 | 1.5646 | 1.5637 | 1.5581 | 1.5565 | 0.84258 | 3
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 15.6 | 0.99794 | 4.9979 | 5.0418 | 5.1002 | 5.1457 | 5.2015 | 1.2676 | 12
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | 0.99777 | 5.5711 | 5.6261 | 5.6786 | 5.7256 | 5.7826 | 0 | 3.5
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.97834 | 0.88986 | 0.90864 | 0.9282 | 0.94561 | 0.96511 | 0.364 | 17
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 3 | 0.99986 | 1.3029 | 1.3049 | 1.3057 | 1.309 | 1.3105 | 1.1938 | 8
Tumut | Batlow | 66/11 | 5 | 5 |  | 6 | 0.98759 | 2.1315 | 2.1236 | 2.1187 | 2.1135 | 2.1128 | 1.0949 | 4
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 9.6 | 0.99983 | 5.7291 | 5.7901 | 5.8488 | 5.907 | 5.9637 | 2.9837 | 6
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.2 | 0.99756 | 0.82275 | 0.83347 | 0.84474 | 0.8521 | 0.86885 | 0.4682 | 1.5
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.99595 | 0.099124 | 0.098561 | 0.098237 | 0.097812 | 0.097401 | 0.0692 | 4
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | 0.78011 | 0.60441 | 0.61971 | 0.63635 | 0.65645 | 0.67308 | 0.3241 | 2
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 9.6 | 0.99852 | 8.5177 | 8.5151 | 8.517 | 8.5231 | 8.5104 | 2.6564 | 6
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 36 | 0.99475 | 13.7855 | 13.8603 | 13.8454 | 13.8879 | 13.9034 | 5.6464 | 3
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 12 | 0.99793 | 9.7883 | 9.9261 | 10.0691 | 10.2061 | 10.3499 | 6.723 | 8
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 6 | 0.99994 | 7.7684 | 8.137 | 8.5447 | 8.8558 | 9.2514 | 2.4958 | 8
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 12 | 0.99694 | 0.91403 | 0.90777 | 0.91645 | 0.91899 | 0.91606 | 0 | 2
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 36 | 0.99996 | 12.5084 | 13.0848 | 13.6507 | 14.2092 | 14.8108 | 8.2182 | 4.5
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 36 | 0.99549 | 19.1784 | 18.8406 | 18.8704 | 18.9582 | 19.0276 | 6.3858 | 4
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 36 | 0.99961 | 27.9533 | 22.665 | 22.8226 | 23.01 | 23.1437 | 13.1815 | 5
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 9.6 | 0.99189 | 5.1009 | 5.2599 | 5.4336 | 5.6029 | 5.7531 | 3.5049 | 8
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 3 | 0.96261 | 2.6387 | 2.6598 | 2.6767 | 2.6964 | 2.7117 | 1.8459 | 2.5
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 22.8 | 0.99102 | 15.8314 | 16.0393 | 16.2587 | 16.4919 | 16.6625 | 5.6599 | 12
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 12 | 0.99989 | 4.3458 | 4.3436 | 4.3491 | 4.3323 | 4.3339 | 3.386 | 8
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 36 | 1 | 9.6433 | 9.6779 | 9.7179 | 9.7726 | 9.8321 | 2.9038 | 11
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.9951 | 44.3092 | 44.7195 | 45.0507 | 45.2502 | 45.8007 | 0 | 4
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 18 | 1 | 11.5751 | 11.531 | 11.5212 | 11.6139 | 11.6283 | 0 | 2.5
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 18 | 0.99253 | 6.9466 | 7.1295 | 7.3011 | 7.4759 | 7.6529 | 2.2553 | 9
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.94954 | 7.6014 | 7.6594 | 7.7173 | 7.7849 | 7.8399 | 0 | 4
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 16.8 | 0.99098 | 7.1336 | 7.2108 | 7.2125 | 7.2724 | 7.3185 | 1.189 | 5
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | 0.99759 | 1.5424 | 1.5395 | 1.5444 | 1.5503 | 1.5494 | 1.2267 | 6.5
Cowra | Canowindra | 66/11 | 5 | 8 |  | 6 | 0.99401 | 4.9741 | 5.0181 | 5.0643 | 5.109 | 5.1541 | 3.2063 | 3
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 36 | 0.99187 | 15.7951 | 15.9568 | 16.0903 | 16.242 | 16.3834 | 9.2977 | 8.5
Cowra | Grenfell | 66/11 | 8 | 5 |  | 6 | 0.95383 | 4.6714 | 4.7583 | 4.8091 | 4.87 | 4.9433 | 3.3739 | 6
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.99877 | 0.91609 | 0.91893 | 0.92359 | 0.92585 | 0.93176 | 0.5819 | 3
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 6 | 0.98992 | 3.8746 | 4.021 | 4.1616 | 4.2962 | 4.435 | 2.5076 | 12
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 22.8 | 0.99915 | 8.6314 | 8.7113 | 8.789 | 8.8576 | 8.9222 | 5.8833 | 5.5
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.8 | 0.97846 | 1.4916 | 1.4796 | 3.2672 | 3.2553 | 3.245 | 0.3501 | 6
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 12 | 0.99888 | 4.8422 | 4.8795 | 4.9124 | 4.9589 | 4.993 | 3.095 | 3.5
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 36 | 0.99616 | 17.8521 | 18.0698 | 18.2855 | 18.5427 | 18.7466 | 8.0122 | 6
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 3 | 0.99971 | 1.2804 | 1.3279 | 1.3779 | 1.4287 | 1.4767 | 0.9836 | 3.5
Yass | Marilba | 66/11 | 3 | 1 |  | 1.2 | 0.99975 | 1.5993 | 1.626 | 1.6444 | 1.6679 | 1.6932 | 0.92545 | 6
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | 0.99846 | 7.8369 | 7.9829 | 8.1183 | 8.2719 | 8.4296 | 6.1681 | 9
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 15.6 | 0.98319 | 14.6773 | 14.7973 | 14.9018 | 14.9876 | 15.1033 | 6.7919 | 5
Temora | Anona | 66/22 | 3 |  |  | 0 | 0.94722 | 1.1616 | 1.1651 | 1.1734 | 1.1776 | 1.184 | 0.81 | 8
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 3 | 0.99907 | 0.7021 | 0.70912 | 0.7162 | 0.72212 | 0.72916 | 0.4511 | 1
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.6 | 0.99886 | 0.91938 | 0.93381 | 0.94843 | 0.96288 | 0.97886 | 0.6039 | 4
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | 0.99929 | 0.21219 | 0.21392 | 0.2157 | 0.21772 | 0.22007 | 0.1564 | 2
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.97351 | 16.5951 | 16.7531 | 19.3568 | 19.587 | 19.7188 | 0 | 9
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 12 | 0.99983 | 6.9086 | 6.9896 | 7.0715 | 7.1577 | 7.2463 | 4.7146 | 4.5
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 12 | 0.98397 | 7.4151 | 7.5305 | 10.3407 | 10.4555 | 10.567 | 4.2703 | 8.5
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.6 | 0.99809 | 0.68963 | 0.69378 | 0.69682 | 0.70026 | 0.70392 | 0.25365 | 18
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 36 | 0.99898 | 10.2021 | 10.2101 | 13.7125 | 19.6316 | 35.7348 | 0.27455 | 73
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/10 | 6.75/10 |  | 12 | 0.99941 | 8.3379 | 8.58 | 8.8629 | 9.1168 | 9.4075 | 3.5028 | 2
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.8 | 0.98989 | 1.368 | 1.3603 | 1.3604 | 1.3603 | 1.3615 | 0 | 3
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 9.6 | 0.99996 | 4.2548 | 4.3057 | 4.3407 | 4.3849 | 4.4242 | 3.0297 | 6
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.6 | 0.98898 | 0.87107 | 0.8741 | 0.87071 | 0.87012 | 0.87051 | 0.5303 | 4.5
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 16.8 | 0.98837 | 4.9121 | 4.8993 | 4.8885 | 4.8743 | 4.8919 | 1.8593 | 3.5
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | 0.99919 | 0.45062 | 0.45367 | 0.4526 | 0.45135 | 0.45113 | 0.1817 | 2
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 18 | 0.99926 | 6.7164 | 6.8108 | 6.8953 | 6.9847 | 7.0875 | 3.2049 | 11
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | 0.99988 | 12.0211 | 12.0435 | 12.0758 | 12.1014 | 12.1322 | 0 | 6.5
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.99398 | 0.37796 | 0.37298 | 0.37036 | 0.36499 | 0.36022 | 0.3704 | 4
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.4 | 0.99588 | 1.3498 | 1.3496 | 1.3498 | 1.3497 | 1.3486 | 0 | 3
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 8.28 | 0.99551 | 3.2602 | 3.2748 | 3.294 | 3.3143 | 3.3309 | 0.4615 | 3.5
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.2 | 0.90264 | 1.0138 | 1.0165 | 1.0195 | 1.0211 | 1.0244 | 0.6279 | 2
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 36 | 0.99323 | 17.9911 | 18.1406 | 18.2882 | 18.4051 | 18.5488 | 8.025 | 4
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 15.96 | 0.99998 | 10.9627 | 11.0648 | 11.1873 | 11.2829 | 11.3938 | 7.3278 | 5.5
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0.96943 | 0.14653 | 0.14747 | 0.14803 | 0.14767 | 0.14786 | 0 | 3
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 36 | 0.9999 | 15.3902 | 15.7031 | 15.9735 | 16.2594 | 16.56 | 3.6557 | 3
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 6 | 0.99996 | 2.2921 | 2.2923 | 2.2957 | 2.2919 | 2.2952 | 1.6428 | 4
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 30 | 0.99775 | 15.7671 | 15.8415 | 15.9127 | 15.949 | 15.9993 | 9.1291 | 5
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 6 | 0.95679 | 2.9708 | 2.9771 | 2.9788 | 2.9848 | 2.9869 | 2.0535 | 6.5
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 24 | 0.99166 | 9.7197 | 9.7686 | 9.8235 | 9.8714 | 9.9506 | 1.7558 | 5
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 19.2 | 0.99844 | 4.935 | 5.0055 | 5.0647 | 5.1323 | 5.2027 | 2.7325 | 5
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 8.4 | 0.99501 | 4.439 | 4.465 | 4.495 | 4.515 | 4.5466 | 2.9537 | 1
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 8.4 | 0.99494 | 3.3125 | 3.3143 | 3.3117 | 3.3187 | 3.3239 | 2.3464 | 2
Morven | Morven | 132/66 | 30 |  |  | 0 | 0.99972 | 7.7102 | 7.7723 | 7.8219 | 7.8722 | 7.9223 | 0 | 3
Albury | Corowa | 132/22 | 30 | 27/30 |  | 36 | 0.99973 | 13.0234 | 13.0231 | 13.0736 | 13.0453 | 13.0567 | 7.9009 | 10
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 52.8 | 0.99272 | 34.1411 | 34.5986 | 35.0311 | 35.5142 | 35.9336 | 11.8796 | 5.5
Albury | Mulwala | 132/22 | 30 | 30 |  | 36 | 0.99731 | 10.7033 | 10.7969 | 10.8969 | 10.9883 | 11.1 | 5.2066 | 4.5
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 84 | 0.99681 | 49.1585 | 50.3637 | 51.6081 | 52.8682 | 54.1078 | 33.5575 | 4
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 36 | 0.99924 | 11.3118 | 11.3868 | 11.4526 | 11.5365 | 11.639 | 8.0445 | 2.5
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 12 | 0.99991 | 3.9155 | 3.9373 | 3.9584 | 3.9748 | 4.0084 | 1.8037 | 23.5
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 12 | 0.9941 | 5.5144 | 5.6949 | 5.9032 | 6.1024 | 6.3062 | 2.8911 | 5
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 36 | 0.99991 | 17.753 | 17.7589 | 17.8163 | 17.8534 | 17.859 | 9.5823 | 11
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 6 | 0.99692 | 2.8374 | 2.8383 | 2.8485 | 2.8378 | 2.8351 | 2.0477 | 4.5
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 36 | 0.99387 | 9.4151 | 9.5769 | 9.7403 | 9.903 | 10.08 | 6.3241 | 5.5
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 6 | 0.98023 | 2.6975 | 2.696 | 2.7246 | 2.7379 | 2.7554 | 0.9199 | 21
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0.89526 | 0.54767 | 0.54593 | 0.54324 | 0.54205 | 0.54045 | 0 | 6
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 30 | 0.95445 | 10.1624 | 10.3336 | 10.4617 | 10.6706 | 10.7385 | 0.6451 | 2
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 9 | 0.97385 | 1.6682 | 1.6609 | 1.6565 | 1.6631 | 1.6576 | 0.6977 | 1
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 15 | 0.86436 | 2.735 | 2.7981 | 2.8816 | 2.9522 | 3.0238 | 1.0742 | 5
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 3 | 0.97271 | 0.90336 | 0.90072 | 0.91318 | 0.91282 | 0.92864 | 0.1024 | 5
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.77719 | 1.6848 | 1.6567 | 1.6231 | 1.5999 | 1.573 | 0.5057 | 4
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.8 | 0.94397 | 0.49589 | 0.49715 | 0.49709 | 0.49841 | 0.49861 | 0.1909 | 4.5
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 36 | 0.98431 | 13.7154 | 13.7404 | 13.7831 | 13.8057 | 13.7942 | 0.993 | 18
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 12 | 0.9835 | 7.3448 | 7.4043 | 7.4356 | 7.4838 | 7.5384 | 2.6437 | 8
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 19.2 | 0.99067 | 8.3744 | 8.4493 | 8.5006 | 8.5684 | 8.6405 | 3.0082 | 6
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.2 | 0.97932 | 0.82361 | 0.83833 | 0.85249 | 0.86618 | 0.88206 | 0.256 | 6
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 15 | 0.98768 | 7.6801 | 7.876 | 8.0639 | 8.2533 | 8.4506 | 4.8158 | 2
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 60 | 0.98845 | 20.6461 | 20.6767 | 20.6586 | 20.7207 | 20.6584 | 8.2317 | 4
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 30 | 1 | 12.3794 | 12.4168 | 12.557 | 12.6409 | 12.8065 | 1.8229 | 24
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | 0.98106 | 1.057 | 1.0964 | 1.1348 | 1.1752 | 1.2059 | 0.5927 | 3.5
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99979 | 10.2127 | 10.2613 | 10.3175 | 10.3745 | 10.4425 | 5.614 | 13
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 3 | 0.8806 | 0.85092 | 0.85024 | 0.84856 | 0.84644 | 0.84461 | 0.4552 | 3
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0.94061 | 0.32156 | 0.32074 | 0.32164 | 0.32155 | 0.32126 | 0 | 3
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.95694 | 1.4237 | 1.4534 | 1.5061 | 1.5591 | 1.5897 | 0.297 | 1.5
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 11.4 | 0.99999 | 5.2935 | 5.4132 | 5.4904 | 5.5962 | 5.6984 | 1.6291 | 2.5
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.96733 | 0.3045 | 0.3115 | 0.31641 | 0.31931 | 0.32404 | 0.1534 | 1.5
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 30 | 0.99041 | 16.4669 | 16.4397 | 16.4263 | 16.4117 | 16.4033 | 6.8846 | 7.5
Yanco | Murrami | 33/11 | 5 | 5 |  | 6 | 0.80283 | 1.3593 | 1.3897 | 1.4218 | 1.4466 | 1.4813 | 0.3937 | 6.5
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.97921 | 8.4514 | 8.5869 | 8.6804 | 8.824 | 8.9606 | 4.1105 | 5
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 7.5 | 0.94182 | 2.6121 | 2.6245 | 2.6083 | 2.6044 | 2.5916 | 0.8144 | 3
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.98335 | 2.1213 | 2.1743 | 2.2261 | 2.2805 | 2.3307 | 1.3394 | 5
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.9989 | 9.643 | 9.8009 | 9.9773 | 10.1472 | 10.2963 | 0.5928 | 3
Buronga | Powercor Robinvale 22kV Euston Distribution Supply | [5 empty] | 0.97696 | 3.0767 | 3.0773 | 3.0858 | 3.0804 | 3.0788 | 1.7272 | 4
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply | [5 empty] | 0.97573 | 2.7426 | 2.7534 | 2.7548 | 2.7651 | 2.779 | 1.0693 | 12
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 36 | 0.99726 | 8.5263 | 8.6624 | 8.8329 | 8.9721 | 9.1205 | 4.4294 | 4
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 36 | 0.99546 | 4.3292 | 4.3885 | 4.4455 | 4.5175 | 4.5731 | 3.3488 | 7.5
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.97428 | 1.4581 | 1.4613 | 1.4568 | 1.4485 | 1.445 | 0.48 | 1
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0.92659 | 6.7322 | 6.7669 | 6.7821 | 6.8069 | 6.8149 | 0 | 39
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0.99844 | 0.3337 | 0.33677 | 0.33113 | 0.33747 | 0.33323 | 0 | 0.5

## Lines
Supply Area | Feeder # | Feeder Voltage kV | Feeder Origin | Feeder Destination | Summer | [5 empty] | Winter
[5 empty] | Line Rating | Line Forecast MVA |  |  |  |  | Line Rating | Line Forecast MVA
[5 empty] | MVA | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 | MVA | 2024 | 2025 | 2026 | 2027 | 2028
Casino | 96L | 132 | Transgrid Casino 132kV 96L Tee | Casino ZS | 140 | 26.2005 | 26.3905 | 26.4906 | 26.7048 | 26.8418 | 157 | 23.6415 | 23.8309 | 23.9781 | 24.1816 | 24.3307
Casino | 6501 | 66 | Casino ZS | Rappville Tee | 16 | 0.68713 | 0.68787 | 0.68915 | 0.69375 | 0.69381 | 25 | 0.61242 | 0.6292 | 0.66884 | 0.69487 | 0.72471
Casino | 8401 | 33 | Casino ZS | Mallanganee ZS | 4 | 2.7193 | 2.7295 | 2.7437 | 2.7519 | 2.7618 | 6 | 2.6262 | 2.6476 | 2.672 | 2.6979 | 2.7241
Casino | 8402 | 33 | Mallanganee ZS | Bonalbo ZS | 4 | 1.7192 | 1.7232 | 1.731 | 1.7356 | 1.7404 | 6 | 1.6939 | 1.708 | 1.7263 | 1.7436 | 1.7603
Casino | 8403 | 33 | Bonalbo ZS | Urbenville ZS | 4 | 0.8401 | 0.84117 | 0.84418 | 0.84258 | 0.84453 | 7 | 0.95324 | 0.97027 | 0.98939 | 1.009 | 1.028
Coffs Harbour | 96C/2(D) | 132 | TransGrid 96C Armidale Coffs Harbour Dorrigo Tee | Dorrigo ZS | 122 | 2.4261 | 2.4064 | 2.3872 | 2.3856 | 2.3714 | 137 | 2.6758 | 2.676 | 2.6748 | 2.6803 | 2.6792
Coffs Harbour | 702 | 66 | Boambee South 132/66kV STS | Sawtell ZS | 61 | 9.2884 | 9.302 | 9.3091 | 9.3352 | 9.308 | 68 | 10.3324 | 10.4193 | 10.5089 | 10.6091 | 10.7367
Coffs Harbour | 705 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 15.2942 | 15.3185 | 16.2187 | 16.321 | 16.3635 | 58 | 15.6364 | 15.8517 | 16.9348 | 17.1491 | 17.3711
Coffs Harbour | 706 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 17.4184 | 17.4461 | 18.4713 | 18.5878 | 18.6363 | 58 | 17.8082 | 18.0533 | 19.2868 | 19.531 | 19.7837
Coffs Harbour | 7501 | 66 | Nana Glen ZS | Woolgoolga ZS | 29 | 5.705 | 5.7141 | 6.0498 | 6.088 | 6.1039 | 33 | 5.8326 | 5.9129 | 6.3169 | 6.3969 | 6.4797
Coffs Harbour | 7502 | 66 | Nana Glen ZS | Ulong Tee | 9 | 0.38441 | 0.38704 | 0.38853 | 0.39097 | 0.39411 | 15 | 0.48253 | 0.49181 | 0.5019 | 0.51208 | 0.52243
Coffs Harbour | 7502/1 | 66 | Ulong Tee | Ulong ZS | 9 | 0.38441 | 0.38704 | 0.38853 | 0.39097 | 0.39411 | 15 | 0.48253 | 0.49181 | 0.5019 | 0.51208 | 0.52243
Coffs Harbour | 7503 | 66 | Ulong Tee | Dorrigo ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | 7509 | 66 | Moonee ZS | Woolgoolga ZS | 30 | 9.978 | 10.1553 | 10.2855 | 10.4368 | 10.5895 | 36 | 12.538 | 12.8139 | 13.1081 | 13.3658 | 13.6562
Coffs Harbour | 7510 | 66 | North Coffs ZS | Moonee ZS | 61 | 7.4044 | 7.4161 | 7.8519 | 7.9014 | 7.922 | 68 | 7.57 | 7.6742 | 8.1986 | 8.3024 | 8.4098
Coffs Harbour | 703:NGN | 66 | TransGrid Coffs Harbour 132/66 kV STS | Nana Glen ZS | 62 | 9.3465 | 9.3613 | 9.9114 | 9.974 | 9.9999 | 69 | 9.5556 | 9.6871 | 10.349 | 10.48 | 10.6157
Coffs Harbour | 711:CHN | 66 | TransGrid Coffs Harbour 132/66 kV STS | North Coffs ZS | 62 | 18.8143 | 18.8442 | 19.9515 | 20.0774 | 20.1298 | 69 | 19.2353 | 19.5001 | 20.8325 | 21.0962 | 21.3692
Coffs Harbour | 87C | 66 | North Coffs ZS | South Coffs ZS | 68 | 11.7741 | 11.7928 | 12.4858 | 12.5646 | 12.5973 | 68 | 12.0376 | 12.2033 | 13.0371 | 13.2021 | 13.373
Grafton | 825 | 66 | TransGrid Koolkhan 132/66kV STS | Koolkhan ZS | 62 | 19.6076 | 19.7474 | 19.8904 | 20.1021 | 20.2556 | 69 | 16.0903 | 16.1756 | 16.2618 | 16.3564 | 16.4661
Grafton | 826 | 66 | TransGrid Koolkhan 132/66kV STS | Grafton North ZS | 61 | 15.9985 | 16.1126 | 16.2292 | 16.402 | 16.5273 | 68 | 12.8075 | 12.8754 | 12.944 | 13.0193 | 13.1067
Grafton | 6503 | 66 | Grafton North ZS | South Grafton ZS | 24 | 10.4502 | 10.5247 | 10.6009 | 10.7137 | 10.7956 | 25 | 7.4903 | 7.53 | 7.5701 | 7.6142 | 7.6653
Grafton | 6504 | 66 | Five Mile Sw Stn | South Grafton ZS | 61 | 4.5248 | 4.5571 | 4.5901 | 4.6389 | 4.6744 | 68 | 3.2365 | 3.2537 | 3.271 | 3.2901 | 3.3122
Grafton | 6505 | 66 | Koolkhan SS | Grafton ZS | 52 | 17.3991 | 17.5231 | 17.65 | 17.8378 | 17.9741 | 58 | 13.8247 | 13.898 | 13.972 | 14.0534 | 14.1476
Grafton | 6506 | 66 | Shannon Creek ZS | Nymboida ZS | 14 | 0.26934 | 0.27126 | 0.27322 | 0.27613 | 0.27824 | 21 | 0.36989 | 0.37185 | 0.37383 | 0.37601 | 0.37853
Grafton | 6508 | 66 | Maclean ZS | Yamba ZS | 28 | 11.047 | 11.1224 | 11.2459 | 11.3549 | 11.4118 | 32 | 10.4892 | 10.5299 | 10.5045 | 10.4915 | 10.462
Grafton | 6509 | 66 | Shannon Creek ZS | Five Mile Sw Stn | 14 | 1.2389 | 1.2478 | 1.2568 | 1.2702 | 1.2799 | 21 | 1.0634 | 1.0691 | 1.0748 | 1.081 | 1.0883
Grafton | 6510 | 66 | Grafton North ZS | Five Mile Sw Stn | 28 | 5.656 | 5.6964 | 5.7376 | 5.7987 | 5.843 | 34 | 4.0226 | 4.0439 | 4.0654 | 4.0891 | 4.1165
Grafton | 896:MLN | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 21 | 9.319 | 9.3854 | 9.4534 | 9.554 | 9.627 | 25 | 7.7677 | 7.8089 | 7.8505 | 7.8962 | 7.9492
Grafton | 8G1 | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 68 | 11.9585 | 12.0438 | 12.1309 | 12.2601 | 12.3537 | 68 | 9.8483 | 9.9006 | 9.9533 | 10.0113 | 10.0784
Grafton | 6402 | 33 | Maclean ZS | Yamba Tee | 8 | 0.4848 | 0.48826 | 0.49179 | 0.49703 | 0.50083 | 9 | 0.27742 | 0.27889 | 0.28038 | 0.28201 | 0.2839
Grafton | 6403 | 33 | Yamba Tee | Redcliff ZS | 3 | 0.4848 | 0.48826 | 0.49179 | 0.49703 | 0.50083 | 5 | 0.36989 | 0.37185 | 0.37383 | 0.37601 | 0.37853
Grafton | 6404 | 33 | Yamba Tee | Yamba ZS | 10 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7Y1 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 4.4389 | 4.4806 | 4.4857 | 4.5246 | 4.5285 | 12 | 4.3616 | 4.4108 | 4.455 | 4.5145 | 4.5662
Hawks Nest | 7Y2 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 4.0711 | 4.1094 | 4.1141 | 4.1497 | 4.1533 | 12 | 4.0002 | 4.0453 | 4.0859 | 4.1404 | 4.1879
Hawks Nest | 7V1 | 33 | Ausgrid Salt Ash ZS | Tee with 7Y1 | 7 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Herons Creek | 866:KEW | 66 | Herons Creek 132/66kV STS | Kew ZS | 16 | 12.106 | 12.1373 | 12.1523 | 12.1878 | 12.2581 | 25 | 11.6664 | 11.926 | 12.1838 | 12.4814 | 12.7592
Herons Creek | 871 | 66 | Kew ZS | Laurieton ZS | 36 | 7.7296 | 7.7229 | 7.7313 | 7.7326 | 7.742 | 42 | 8.5346 | 8.6191 | 8.6613 | 8.7771 | 8.8036
Herons Creek | 862/1 | 66 | Kew ZS | Johns River ZS | 16 | 0.84059 | 0.83815 | 0.83833 | 0.83514 | 0.83582 | 25 | 1.0026 | 1.0008 | 0.99815 | 0.99521 | 0.99137
Herons Creek | 862/2 | 66 | TransGrid Taree 132/66/33kV STS | Johns River ZS | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Kempsey | 7R1 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 30 | 7.0214 | 7.1024 | 7.2117 | 7.3255 | 7.4134 | 34 | 7.5639 | 7.6854 | 7.7898 | 7.9159 | 8.0277
Kempsey | 7R2/1 | 33 | TransGrid Kempsey 132/33kV STS | North St Tee | 26 | 8.1269 | 8.2206 | 8.3471 | 8.4789 | 8.5807 | 29 | 8.3732 | 8.5077 | 8.6233 | 8.7629 | 8.8867
Kempsey | 7R2/2 | 33 | North St Tee | Smithtown ZS | 19 | 4.0634 | 4.1103 | 4.1736 | 4.2395 | 4.2903 | 21 | 4.9181 | 4.9971 | 5.065 | 5.147 | 5.2197
Kempsey | 7R2/3 | 33 | North St Tee | North St ZS | 10 | 4.0037 | 4.0499 | 4.1122 | 4.1771 | 4.2272 | 19 | 3.424 | 3.479 | 3.5263 | 3.5833 | 3.634
Kempsey | 7R3 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 26 | 7.0513 | 7.1326 | 7.2424 | 7.3567 | 7.445 | 29 | 7.595 | 7.717 | 7.8219 | 7.9485 | 8.0608
Kempsey | 7R4 | 33 | TransGrid Kempsey 132/33kV STS | Munga ZS | 3 | 1.5177 | 1.5162 | 1.516 | 1.5155 | 1.5226 | 4 | 1.2346 | 1.2696 | 1.3038 | 1.3355 | 1.3724
Kempsey | 7R5 | 33 | TransGrid Kempsey 132/33kV STS | North St ZS | 19 | 6.1549 | 6.2259 | 6.3217 | 6.4215 | 6.4986 | 21 | 6.3499 | 6.452 | 6.5396 | 6.6455 | 6.7393
Kempsey | 7R6/1 | 33 | Prince St ZS | South West Rocks Tee | 15 | 5.1391 | 5.1983 | 5.2783 | 5.3617 | 5.426 | 18 | 5.9453 | 6.0408 | 6.1229 | 6.222 | 6.3099
Kempsey | 7R6/2 | 33 | South West Rocks Tee | South West Rocks ZS | 19 | 2.5994 | 2.6294 | 2.6699 | 2.712 | 2.7446 | 21 | 3.0816 | 3.1311 | 3.1736 | 3.225 | 3.2706
Kempsey | 7R6/3 | 33 | South West Rocks Tee | Smithtown ZS | 19 | 2.4201 | 2.448 | 2.4857 | 2.525 | 2.5553 | 21 | 2.708 | 2.7516 | 2.7889 | 2.8341 | 2.8741
Kempsey | 7R7 | 33 | Prince St ZS | Crescent Head ZS | 5 | 1.5535 | 1.549 | 1.5461 | 1.5455 | 1.5454 | 8 | 1.9542 | 1.9517 | 1.959 | 1.9623 | 1.9598
Kempsey | 7R8 | 33 | Smithtown ZS | South West Rocks ZS | 30 | 3.0775 | 3.113 | 3.1609 | 3.2108 | 3.2493 | 34 | 3.6107 | 3.6688 | 3.7186 | 3.7788 | 3.8322
Lismore | 9U8 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 183 | 52.2746 | 52.6692 | 53.2143 | 53.7869 | 54.2456 | 214 | 48.6426 | 48.9264 | 49.2566 | 49.5552 | 49.9154
Lismore | 9U9 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 48.3757 | 48.7408 | 49.2452 | 49.7752 | 50.1997 | 143 | 44.9944 | 45.257 | 45.5623 | 45.8386 | 46.1718
Lismore | 9W1 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 44.7656 | 45.1034 | 45.5702 | 46.0606 | 46.4534 | 143 | 41.6165 | 41.8593 | 42.1417 | 42.3972 | 42.7054
Lismore | 9G2 | 132 | Ballina ZS | Lennox Head ZS | 124 | 11.5524 | 11.6396 | 11.7601 | 11.8866 | 11.988 | 139 | 9.7285 | 9.7853 | 9.8513 | 9.911 | 9.9831
Lismore | 9G3 | 132 | Lennox Head ZS | Suffolk Park ZS | 124 | 15.4513 | 15.568 | 15.7291 | 15.8983 | 16.0339 | 139 | 14.1874 | 14.2702 | 14.3665 | 14.4536 | 14.5587
Lismore | 9G4 | 132 | Suffolk Park ZS | Ewingsdale ZS | 124 | 21.5164 | 21.6787 | 21.9031 | 22.1388 | 22.3276 | 139 | 20.4029 | 20.5219 | 20.6604 | 20.7857 | 20.9367
Lismore | 9G5 | 132 | Ewingsdale ZS | Mullumbimby ZS | 122 | 37.5453 | 37.8287 | 38.2202 | 38.6315 | 38.9609 | 137 | 38.779 | 39.0052 | 39.2684 | 39.5065 | 39.7937
Lismore | 9U6 | 132 | Lismore 132/66kV STS | Mullumbimby ZS | 107 | 23.6824 | 23.8612 | 24.1081 | 24.3676 | 24.5754 | 123 | 24.8618 | 25.0068 | 25.1756 | 25.3282 | 25.5123
Lismore | 9U7 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 26.7149 | 26.9166 | 27.1951 | 27.4878 | 27.7222 | 123 | 27.6993 | 27.8609 | 28.0489 | 28.2189 | 28.4241
Lismore | 9U7/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 20.5055 | 20.6603 | 20.8741 | 21.0987 | 21.2787 | 123 | 21.8892 | 22.0169 | 22.1654 | 22.2999 | 22.4619
Lismore | 892 | 66 | Lismore 132/66kV STS | Woodburn ZS | 11 | 7.9202 | 7.9374 | 7.9776 | 8.0071 | 8.047 | 19 | 7.0194 | 7.0754 | 7.1268 | 7.196 | 7.2611
Lismore | 893 | 66 | Lismore 132/66kV STS | Casino ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Lismore | 894:LME | 66 | Lismore 132/66kV STS | Kyogle ZS | 11 | 8.4854 | 8.6164 | 8.7797 | 8.9384 | 9.0329 | 19 | 7.0657 | 7.1234 | 7.1752 | 7.235 | 7.2946
Lismore | 0897:LME | 66 | Lismore 132/66kV STS | Alstonville ZS | 62 | 18.3394 | 18.4779 | 18.6691 | 18.87 | 19.0309 | 69 | 18.241 | 18.3474 | 18.4712 | 18.5832 | 18.7183
Lismore | 8502 | 66 | Lismore East ZS | Alstonville ZS | 62 | 9.6751 | 9.7482 | 9.849 | 9.955 | 10.0399 | 69 | 10.1339 | 10.193 | 10.2618 | 10.324 | 10.399
Lismore | 8503 | 66 | Ballina ZS | Alstonville ZS | 62 | 8.5199 | 8.5842 | 8.673 | 8.7664 | 8.8411 | 69 | 8.1071 | 8.1544 | 8.2094 | 8.2592 | 8.3192
Lismore | 8507 | 66 | Alstonville ZS | Ballina ZS | 61 | 9.8195 | 9.8937 | 9.996 | 10.1036 | 10.1898 | 68 | 9.4583 | 9.5135 | 9.5777 | 9.6357 | 9.7058
Lismore | 8510 | 66 | Lismore Sw Stn | East Lismore ZS | 61 | 22.094 | 22.2607 | 22.4911 | 22.7332 | 22.927 | 68 | 21.7541 | 21.881 | 22.0286 | 22.1622 | 22.3233
Lismore | 8511 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 19.3503 | 19.4963 | 19.6981 | 19.9101 | 20.0799 | 69 | 17.9707 | 18.0756 | 18.1976 | 18.3079 | 18.441
Lismore | 8512 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 9.4288 | 9.4968 | 9.5771 | 9.6725 | 9.7584 | 54 | 8.0837 | 8.2066 | 8.3647 | 8.4673 | 8.6231
Lismore | 8513 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 9.4288 | 9.4968 | 9.5771 | 9.6725 | 9.7584 | 54 | 8.0837 | 8.2066 | 8.3647 | 8.4673 | 8.6231
Lismore | 8514 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 3.884 | 3.8862 | 3.8954 | 3.8891 | 3.879 | 68 | 4.2833 | 4.2947 | 4.2827 | 4.2653 | 4.2796
Lismore | 8515 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 3.7734 | 3.7755 | 3.7849 | 3.7785 | 3.7682 | 68 | 4.1831 | 4.1952 | 4.1847 | 4.1683 | 4.1836
Lismore | 8516 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 19.2059 | 19.3508 | 19.5511 | 19.7615 | 19.93 | 69 | 17.8356 | 17.9397 | 18.0607 | 18.1702 | 18.3023
Nambucca Heads | 751 | 66 | TransGrid Nambucca 132/66 kV STS | Nambucca ZS | 15 | 7.259 | 7.3409 | 7.3922 | 7.4802 | 7.564 | 25 | 8.6352 | 8.6873 | 8.7444 | 8.8123 | 8.8632
Port Macquarie | 70Y | 33 | Rocks Ferry ZS | Telegraph Point ZS | 8 | 1.8218 | 1.8412 | 1.8557 | 1.8708 | 1.896 | 12 | 1.7229 | 1.7792 | 1.8314 | 1.8905 | 1.9458
Port Macquarie | 701 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 22 | 10.1405 | 10.1892 | 10.2054 | 10.6545 | 11.2526 | 26 | 10.5763 | 10.6753 | 10.7735 | 11.2577 | 11.854
Port Macquarie | 703:BPM | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 8.4041 | 8.4445 | 8.4579 | 8.8301 | 9.3258 | 29 | 9.054 | 9.1387 | 9.2228 | 9.6373 | 10.1478
Port Macquarie | 707 | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 9.5154 | 9.5611 | 9.5763 | 9.9978 | 10.559 | 29 | 10.1757 | 10.2709 | 10.3654 | 10.8313 | 11.405
Port Macquarie | 708 | 33 | TransGrid Port Macquarie 132/33kV STS | Owen Street ZS | 26 | 11.0434 | 11.0965 | 11.1141 | 11.6032 | 12.2546 | 29 | 13.2204 | 13.3441 | 13.4669 | 14.0721 | 14.8175
Port Macquarie | 710 | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 31 | 12.0157 | 12.0735 | 12.0927 | 12.6249 | 13.3336 | 34 | 15.2235 | 15.3659 | 15.5074 | 16.2043 | 17.0626
Port Macquarie | 711:CPM | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 20 | 11.9463 | 12.0037 | 12.0228 | 12.5519 | 13.2565 | 20 | 15.2235 | 15.3659 | 15.5074 | 16.2043 | 17.0626
Port Macquarie | 712 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 12 | 6.7371 | 6.7696 | 6.7803 | 7.0787 | 7.4761 | 14 | 6.9707 | 7.036 | 7.1007 | 7.4199 | 7.8129
Port Macquarie | 715 | 33 | Clearwater ZS | Owen Street ZS | 31 | 5.0008 | 5.0248 | 5.0328 | 5.2543 | 5.5492 | 34 | 4.1664 | 4.2054 | 4.2441 | 4.4349 | 4.6698
Port Macquarie | 719/1 | 33 | Clearwater ZS | Lake Cathie ZS | 20 | 5.1597 | 5.2456 | 5.3316 | 5.4302 | 5.4943 | 20 | 6.5633 | 6.8396 | 7.0986 | 7.3774 | 7.6522
Port Macquarie | 719/2 | 33 | Lake Cathie ZS | Laurieton ZS | 12 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0
Port Macquarie | 765 | 33 | Rocks Ferry ZS | Koree ZS | 9 | 4.5146 | 4.5363 | 4.5435 | 4.7435 | 5.0097 | 11 | 5.208 | 5.2568 | 5.3051 | 5.5436 | 5.8372
Port Macquarie | 784 | 33 | Koree ZS | Byabarra ZS | 9 | 1.1807 | 1.1864 | 1.1883 | 1.2406 | 1.3102 | 11 | 1.282 | 1.294 | 1.3059 | 1.3646 | 1.4369
Stroud | 9C9/3 | 33 | Stroud 132/33kV STS | Dungog ZS | 27 | 7.8238 | 7.8803 | 7.9249 | 7.9886 | 8.0414 | 27 | 5.2521 | 5.2819 | 5.319 | 5.3552 | 5.397
Stroud | 9C9/2 | 33 | Dungog ZS | Martins Creek ZS | 21 | 6.0516 | 6.071 | 6.0756 | 6.1031 | 6.109 | 27 | 4.0715 | 4.1242 | 4.181 | 4.2362 | 4.295
Stroud | STR4B3/1 | 33 | Stroud 132/33kV STS | Booral ZS | 7 | 5.1851 | 5.2098 | 5.241 | 5.2653 | 5.2971 | 12 | 7.2142 | 7.2809 | 7.3571 | 7.4454 | 7.5261
Stroud | STR4B3/2 | 33 | Booral ZS | Bulahdelah ZS | 7 | 3.7197 | 3.7375 | 3.7598 | 3.7773 | 3.8001 | 12 | 5.1991 | 5.2471 | 5.302 | 5.3657 | 5.4239
Stroud | STR4B4 | 33 | Stroud 132/33kV STS | Dungog ZS | 4 | 2.7082 | 2.7278 | 2.7432 | 2.7653 | 2.7836 | 6 | 1.7507 | 1.7606 | 1.773 | 1.7851 | 1.799
Stroud | STR4B5/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 7.3643 | 7.3994 | 7.4437 | 7.4782 | 7.5235 | 19 | 7.9397 | 8.013 | 8.0969 | 8.1941 | 8.283
Stroud | STR4B5/2 | 33 | Wards River Sw Stn | Stratford Tee | 19 | 8.2014 | 8.3037 | 8.3945 | 8.5103 | 8.6008 | 21 | 7.5976 | 7.5901 | 7.5986 | 7.5958 | 7.5953
Stroud | STR4B5/2a | 33 | Stratford Tee | Stratford Coal ZS | 7 | 5.1033 | 5.1974 | 5.28 | 5.3816 | 5.4574 | 12 | 4.9075 | 4.9019 | 4.911 | 4.9056 | 4.9066
Stroud | STR4B5/3 | 33 | Stratford Tee | Gloucester ZS | 19 | 2.9362 | 2.9374 | 2.9423 | 2.9499 | 2.9606 | 21 | 2.5023 | 2.5056 | 2.5092 | 2.5164 | 2.5195
Stroud | STR4B6/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 8.4915 | 8.532 | 8.583 | 8.6228 | 8.675 | 19 | 9.1891 | 9.274 | 9.371 | 9.4835 | 9.5864
Stroud | STR4B6/2 | 33 | Wards River Sw Stn | Gloucester ZS | 17 | 5.6998 | 5.702 | 5.7115 | 5.7263 | 5.7471 | 19 | 4.8574 | 4.8637 | 4.8708 | 4.8848 | 4.8907
Stroud | STR4B7 | 33 | Stroud 132/33kV STS | Dungog ZS | 7 | 4.0624 | 4.0917 | 4.1149 | 4.1479 | 4.1753 | 12 | 3.1625 | 3.1805 | 3.2029 | 3.2247 | 3.2498
Stroud | STR4B8 | 33 | Stroud 132/33kV STS | Bulahdelah ZS | 7 | 4.6966 | 4.719 | 4.7473 | 4.7693 | 4.7981 | 12 | 6.1664 | 6.2233 | 6.2884 | 6.3639 | 6.433
Stroud | 3801 | 33 | Bulahdelah ZS | Pacific Palms ZS | 7 | 4.0034 | 4.0034 | 4.0005 | 3.9909 | 3.9999 | 12 | 4.7228 | 4.7766 | 4.8207 | 4.8718 | 4.9439
Stroud | 3803 | 33 | Bulahdelah ZS | Bungwahl Sw Stn | 7 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Stroud | BLH4B4 | 33 | Bulahdelah ZS | Hawks Nest 132/33kV STS | 7 | 0.26301 | 0.26426 | 0.26585 | 0.26708 | 0.2687 | 12 | 0.36273 | 0.36608 | 0.36991 | 0.37435 | 0.37841
Stroud | 7J1 | 33 | Ausgrid Recloser 33175 (Patterson) | Martins Creek Tee | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0
Stroud | 7J1/2 | 33 | Martins Creek Tee | Martins Creek ZS | 4 | 2.4289 | 2.4285 | 2.4249 | 2.4195 | 2.4174 | 7 | 1.7003 | 1.7239 | 1.7477 | 1.7757 | 1.801
Stroud | 7J1/3 | 33 | Martins Creek Tee | Gresford ZS | 4 | 2.4289 | 2.4285 | 2.4249 | 2.4195 | 2.4174 | 7 | 1.7003 | 1.7239 | 1.7477 | 1.7757 | 1.801
Taree | 861 | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 9.5149 | 9.527 | 9.6315 | 9.6601 | 9.71 | 69 | 8.4852 | 8.5722 | 8.6576 | 8.7474 | 8.8136
Taree | 863:WTE | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 9.8565 | 9.869 | 9.9772 | 10.0069 | 10.0585 | 69 | 8.713 | 8.8023 | 8.89 | 8.9823 | 9.0502
Taree | 867 | 66 | TransGrid Taree 132/66/33kV STS | Hallidays Point ZS | 34 | 13.3697 | 13.3867 | 13.5334 | 13.5737 | 13.6437 | 39 | 17.7676 | 17.9498 | 18.1286 | 18.3168 | 18.4553
Taree | 867/1 | 66 | Hallidays Point Tee | Tuncurry ZS | 39 | 13.3697 | 13.3867 | 13.5334 | 13.5737 | 13.6437 | 43 | 11.7312 | 11.8515 | 11.9695 | 12.0938 | 12.1852
Taree | 868/1 | 66 | TransGrid Taree 132/66/33kV STS | Bohnock Tee | 36 | 15.663 | 15.6829 | 15.8549 | 15.9021 | 15.9841 | 41 | 21.4692 | 21.6893 | 21.9054 | 22.1328 | 22.3002
Taree | 868/2 | 66 | Bohnock Tee | Bohnock ZS | 16 | 5.8844 | 6.0329 | 6.1651 | 6.3242 | 6.446 | 26 | 6.8999 | 7.0203 | 7.1794 | 7.3253 | 7.4633
Taree | 868/3 | 66 | Bohnock Tee | Hallidays Point ZS | 38 | 11.4667 | 11.4813 | 11.6071 | 11.6417 | 11.7017 | 43 | 14.8633 | 15.0157 | 15.1653 | 15.3227 | 15.4386
Taree | 872 | 66 | Tuncurry ZS | Forster ZS | 30 | 6.7336 | 6.7422 | 6.8161 | 6.8364 | 6.8717 | 37 | 9.3963 | 9.4927 | 9.5872 | 9.6868 | 9.76
Taree | 86C | 66 | Tuncurry ZS | Forster ZS | 42 | 5.9041 | 5.9116 | 5.9764 | 5.9942 | 6.0252 | 46 | 8.3713 | 8.4571 | 8.5414 | 8.63 | 8.6953
Taree | 86R | 66 | Hallidays Point ZS | Tuncurry ZS | 38 | 11.2227 | 11.237 | 11.3602 | 11.394 | 11.4528 | 43 | 15.5466 | 15.7061 | 15.8625 | 16.0272 | 16.1484
Taree | 7G2/1 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Tee | 22 | 6.604 | 6.6014 | 6.6077 | 6.6118 | 6.6173 | 27 | 5.6405 | 5.6982 | 5.7546 | 5.8163 | 5.8676
Taree | 7G2/2 | 33 | Kanangra Tee | Coopernook ZS | 7 | 5.6473 | 5.6451 | 5.6505 | 5.654 | 5.6587 | 12 | 5.0844 | 5.1364 | 5.1873 | 5.2428 | 5.2891
Taree | 7G2/3 | 33 | Coopernook ZS | Harrington ZS | 8 | 3.1608 | 3.2133 | 3.2568 | 3.3133 | 3.363 | 13 | 3.5769 | 3.6849 | 3.788 | 3.9048 | 4.0011
Taree | 7G4 | 33 | Bootawa ZS | Wingham ZS | 18 | 2.6231 | 2.622 | 2.6246 | 2.6262 | 2.6284 | 21 | 2.4363 | 2.4612 | 2.4856 | 2.5122 | 2.5343
Taree | 7G5 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Dr ZS | 17 | 9.7208 | 9.717 | 9.7263 | 9.7323 | 9.7404 | 17 | 8.3681 | 8.4537 | 8.5374 | 8.6288 | 8.7049
Taree | 7G1 | 33 | TransGrid Taree 132/66/33kV STS | Bootawa ZS | 17 | 7.0977 | 7.0949 | 7.1018 | 7.1061 | 7.112 | 19 | 5.614 | 5.6715 | 5.7276 | 5.789 | 5.84
Taree | 7G3 | 33 | TransGrid Taree 132/66/33kV STS | Wingham ZS | 18 | 7.4681 | 7.4651 | 7.4723 | 7.4769 | 7.4831 | 20 | 6.0907 | 6.153 | 6.2139 | 6.2805 | 6.3359
Terranora | 757 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 119 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 141.4214
Terranora | 758 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 119 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 142.8356
Terranora | 9501 | 66 | Terranora 110/66kV STS | Cudgen ZS | 59 | 24.1331 | 24.306 | 24.5006 | 24.6508 | 24.8 | 66 | 23.5092 | 23.6917 | 23.8575 | 24.0513 | 24.2602
Terranora | 9502 | 66 | Terranora 110/66kV STS | Murwillumbah ZS | 61 | 9.6578 | 9.6985 | 9.7415 | 9.7759 | 9.837 | 68 | 10.9697 | 11.0101 | 11.0714 | 11.125 | 11.2059
Terranora | 9503 | 66 | Terranora 110/66kV STS | Banora Pt ZS | 59 | 30.9241 | 30.9953 | 31.0975 | 31.2165 | 31.359 | 66 | 24.2457 | 24.3969 | 24.5747 | 24.7483 | 24.9271
Terranora | 9504 | 66 | Terranora 110/66kV STS | Condong Sw Stn | 61 | 8.692 | 8.7286 | 8.7673 | 8.7983 | 8.8533 | 68 | 9.9725 | 10.0091 | 10.0649 | 10.1136 | 10.1872
Terranora | 9505 | 66 | Cudgen ZS | Banora Point ZS | 53 | 1.2173 | 1.2207 | 1.2251 | 1.2297 | 1.2358 | 59 | 1.056 | 1.0617 | 1.0689 | 1.0757 | 1.0835
Terranora | 9508 | 66 | Terranora 110/66kV STS | Tweed Heads ZS | 41 | 17.1106 | 17.1845 | 17.2972 | 17.3987 | 17.5123 | 46 | 12.2684 | 12.3039 | 12.3394 | 12.3808 | 12.4042
Terranora | 9510 | 66 | Banora Point ZS | Tweed Heads South ZS | 43 | 14.914 | 14.9657 | 15.0283 | 15.1035 | 15.1964 | 50 | 13.1565 | 13.1925 | 13.2523 | 13.3042 | 13.3905
Terranora | 9514 | 66 | Condong Sw Stn | Murwillumbah ZS | 61 | 16.4182 | 16.4874 | 16.5605 | 16.6191 | 16.7228 | 68 | 17.9504 | 18.0164 | 18.1168 | 18.2045 | 18.3369
Terranora | 9516 | 66 | Tweed Head South ZS | Tweed Heads ZS | 43 | 4.074 | 4.0915 | 4.1184 | 4.1426 | 4.1696 | 50 | 2.9211 | 2.9295 | 2.938 | 2.9478 | 2.9534
Terranora | 9406 | 33 | Cudgen ZS | Casuarina Sw Stn | 17 | 11.0155 | 11.053 | 11.0769 | 11.1461 | 11.1624 | 19 | 11.7559 | 11.9847 | 12.213 | 12.434 | 12.6777
Terranora | 9407 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Terranora | 9409 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 11.0155 | 11.053 | 11.0769 | 11.1461 | 11.1624 | 20 | 11.7559 | 11.9847 | 12.213 | 12.434 | 12.6777
Armidale | 661/1 | 66 | TransGrid Armidale 330/132/66kV STS | Hillgrove Tee | 20 | 0.82521 | 0.83034 | 0.83519 | 0.84018 | 0.84682 | 24 | 0.9379 | 0.9434 | 0.94783 | 0.94884 | 0.95354
Armidale | 661/2 | 66 | Hillgrove Tee | Hillgrove ZS | 16 | 0.35366 | 0.35586 | 0.35794 | 0.36008 | 0.36292 | 20 | 0.38369 | 0.38594 | 0.38775 | 0.38816 | 0.39008
Armidale | 661/3 | 66 | Hillgrove Tee | Oaky ZS | 20 | 0.50102 | 0.50413 | 0.50708 | 0.51011 | 0.51414 | 24 | 0.55422 | 0.55746 | 0.56008 | 0.56068 | 0.56345
Armidale | 662/1 | 66 | TransGrid Armidale 330/132/66kV STS | Uralla Tee | 12 | 5.8535 | 5.8776 | 5.8901 | 5.9096 | 5.9271 | 17 | 7.5792 | 7.6362 | 7.6988 | 7.7786 | 7.8397
Armidale | 662/2 | 66 | Uralla Tee | Uralla ZS | 9 | 3.0078 | 3.0118 | 3.0145 | 3.0195 | 3.0313 | 15 | 3.8297 | 3.8426 | 3.8561 | 3.8838 | 3.8962
Armidale | 662/4 | 66 | Uralla Tee | Walcha South ZS | 9 | 2.8594 | 2.8794 | 2.8889 | 2.9032 | 2.909 | 15 | 3.7698 | 3.8111 | 3.8577 | 3.9076 | 3.954
Armidale | 664 | 66 | TransGrid Armidale 330/132/66kV STS | Galloway St ZS | 28 | 13.616 | 13.7006 | 13.7807 | 13.863 | 13.9725 | 34 | 21.3587 | 21.4838 | 21.5846 | 21.6076 | 21.7146
Armidale | 665 | 66 | TransGrid Armidale 330/132/66kV STS | Madgwick Dr ZS | 21 | 8.7531 | 8.8075 | 8.859 | 8.9119 | 8.9823 | 39 | 11.9796 | 12.0498 | 12.1063 | 12.1192 | 12.1793
Armidale | 66C | 66 | Miller St ZS | Madgwick Dr ZS | 21 | 1.7388 | 1.7496 | 1.7599 | 1.7704 | 1.7844 | 39 | 3.2827 | 3.3019 | 3.3174 | 3.3209 | 3.3374
Armidale | 66F | 66 | Galloway St ZS | Miller St ZS | 15 | 6.248 | 6.2869 | 6.3236 | 6.3614 | 6.4116 | 25 | 8.3985 | 8.4477 | 8.4874 | 8.4964 | 8.5385
Bathurst | 81H | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 62 | 7.6996 | 7.7512 | 7.7693 | 7.8439 | 7.8415 | 69 | 8.5889 | 8.684 | 8.8127 | 8.8989 | 9.0232
Bathurst | 81G | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 64 | 10.9995 | 11.0731 | 11.099 | 11.2056 | 11.2021 | 71 | 12.2698 | 12.4057 | 12.5896 | 12.7127 | 12.8903
Bathurst | 81F | 66 | TransGrid Panorama 132/66kV STS | Russell St ZS | 64 | 25.8158 | 25.766 | 25.7653 | 25.8195 | 25.878 | 71 | 31.3904 | 31.4244 | 31.5244 | 31.5863 | 31.6502
Bathurst | 81J | 66 | Raglan ZS | Russell St ZS | 64 | 4.9354 | 4.9259 | 4.9257 | 4.9361 | 4.9473 | 71 | 6.0011 | 6.0076 | 6.0267 | 6.0386 | 6.0508
Bathurst | 81L | 66 | TransGrid Panorama 132/66kV STS | Raglan ZS | 64 | 15.945 | 15.9143 | 15.9139 | 15.9474 | 15.9835 | 71 | 19.3882 | 19.4092 | 19.471 | 19.5092 | 19.5487
Bathurst | 81C | 66 | TransGrid Panorama 132/66kV STS | Blayney ZS | 19 | 12.8063 | 12.8595 | 12.9387 | 13.0132 | 13.081 | 22 | 15.8496 | 15.9722 | 16.1247 | 16.2159 | 16.3218
Bathurst | 66:MAN | 66 | Blayney ZS | Mandurama ZS | 9 | 2.1664 | 2.1645 | 2.1631 | 2.1693 | 2.1679 | 15 | 2.4918 | 2.5051 | 2.5191 | 2.5298 | 2.5422
Beryl | 94M/4 | 132 | TransGrid 94M Mudgee Tee | Mudgee ZS | 128 | 23.5414 | 23.507 | 23.7044 | 23.7157 | 23.6525 | 143 | 24.2146 | 24.6469 | 25.0214 | 25.4414 | 25.8417
Beryl | 851 | 66 | TransGrid Beryl 132/66kV STS | Gulgong ZS | 28 | 2.9148 | 2.9222 | 2.9201 | 2.9261 | 2.9465 | 32 | 3.4559 | 3.4657 | 3.4613 | 3.4687 | 3.4697
Beryl | 851 | 66 | Gulgong ZS | Mudgee ZS | 28 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0
Beryl | 852 | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Beryl | 86J | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 61 | 13.1525 | 13.1603 | 13.1363 | 13.1261 | 13.0979 | 68 | 13.8517 | 14.0146 | 14.1559 | 14.2918 | 14.4493
Beryl | 85A | 66 | Dunedoo ZS | Coonabarabran ZS | 11 | 8.9754 | 8.9921 | 8.9742 | 8.961 | 8.9478 | 19 | 9.4627 | 9.5474 | 9.6267 | 9.7029 | 9.7881
Beryl | 80L | 66 | Ulan Sw Stn | Ulan Town ZS | 15 | 2.4105 | 2.4102 | 2.4125 | 2.416 | 2.4253 | 25 | 3.0031 | 3.0889 | 3.1804 | 3.2731 | 3.3431
Beryl | 80R | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 64 | 44.3844 | 44.3696 | 44.413 | 44.4605 | 44.4853 | 71 | 42.9844 | 43.043 | 43.0516 | 43.0976 | 43.2439
Beryl | 80U | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 61 | 32.513 | 32.8843 | 33.3155 | 33.7763 | 34.1635 | 68 | 35.1091 | 36.1566 | 36.9663 | 38.0263 | 38.8762
Beryl | 80T | 66 | Ulan Sw Stn | Moolarben No1 Mine ZS | 43 | 31.49 | 31.6459 | 31.7848 | 31.9512 | 32.0968 | 54 | 32.3985 | 32.9304 | 33.512 | 34.0152 | 34.5389
Beryl | 80W | 66 | Moolarben No1 Mine ZS | Moolarben No2 Mine ZS | 43 | 13.8534 | 13.843 | 13.8495 | 13.8715 | 13.8752 | 54 | 14.5051 | 14.5924 | 14.6724 | 14.7916 | 14.9219
Beryl | 80X | 66 | Moolarben No2 Mine ZS | Wilpinjong Mine ZS | 61 | 5.2899 | 5.2883 | 5.2924 | 5.2919 | 5.2951 | 68 | 5.4331 | 5.4385 | 5.4388 | 5.4497 | 5.4466
Broken Hill | X4 | 220 | TransGrid Broken Hill 220/22kV STS | Perilya Mine | 213 | 24.6277 | 24.6293 | 24.6235 | 24.6166 | 24.6076 | 238 | 24.2512 | 24.246 | 24.2649 | 24.2482 | 24.2356
Broken Hill | 5B1:PPL | 66 | Pinnacles Place ZS | Mt Gipps ZS | 19 | 6.8504 | 8.1543 | 9.5691 | 9.6238 | 9.7349 | 33 | 6.3164 | 7.5581 | 8.8547 | 8.9015 | 8.9564
Broken Hill | 5B1:MTG | 66 | Mt Gipps ZS | Sunset Strip ZS | 19 | 4.9643 | 6.2269 | 7.6266 | 7.6459 | 7.7252 | 33 | 4.8426 | 6.0031 | 7.2671 | 7.2698 | 7.2735
Broken Hill | 5B1:SUN | 66 | Sunset Strip ZS | Menindee ZS | 6 | 0.88053 | 0.88286 | 0.88736 | 0.89479 | 0.9025 | 9 | 0.71034 | 0.71203 | 0.71417 | 0.7172 | 0.71756
Dubbo | 94J/3 | 132 | 94J Tee | Dubbo South ZS | 106 | 42.9606 | 43.0732 | 49.0583 | 55.088 | 55.3195 | 119 | 37.4694 | 42.6555 | 47.9291 | 47.9923 | 48.0478
Dubbo | 943/2 | 132 | Dubbo South ZS | Narromine South Sw Stn | 106 | 30.5423 | 30.6224 | 34.8774 | 39.1642 | 39.3287 | 119 | 25.3565 | 28.866 | 32.4348 | 32.4776 | 32.5151
Dubbo | 94W/1 | 132 | Dubbo 132/66kV STS | Nevertire Tee | 128 | 138.7446 | 138.7712 | 138.8136 | 138.789 | 138.8214 | 143 | 119.1704 | 119.2214 | 119.2117 | 119.2527 | 119.2677
Dubbo | 94W/2 | 132 | Nevertire Tee | Nevertire ZS | 124 | 6.7097 | 6.7181 | 6.7154 | 6.7545 | 6.7639 | 139 | 8.381 | 8.3372 | 8.375 | 8.3513 | 8.3538
Dubbo | 94W/3 | 132 | Nevertire Tee | Nevertire Sw Stn | 128 | 144.9569 | 144.9569 | 144.9569 | 144.9569 | 144.9569 | 143 | 125.4407 | 125.4407 | 125.4407 | 125.4407 | 125.4407
Dubbo | 9GX | 132 | Nevertire Sw Stn | Nyngan 132/66kV STS | 128 | 55.1672 | 55.322 | 55.5657 | 55.8146 | 56.0562 | 143 | 47.7589 | 47.9791 | 48.2326 | 48.4958 | 48.6791
Dubbo | 9GP | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 12.1785 | 12.2349 | 12.2555 | 12.2134 | 12.2117 | 139 | 12.5598 | 12.6813 | 12.7867 | 12.917 | 13.1106
Dubbo | 9GR | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GT | 132 | Dubbo West ZS | Narromine South Sw Stn | 140 | 42.6772 | 42.7734 | 42.8407 | 42.8079 | 42.8214 | 157 | 41.7456 | 41.9584 | 42.1858 | 42.4707 | 42.7299
Dubbo | 9GU | 132 | Narromine South Sw Stn | Nyngan 132/66kV STS | 106 | 67.1946 | 67.2601 | 67.3523 | 67.3597 | 67.3819 | 119 | 64.2128 | 64.4147 | 64.6845 | 65.0259 | 65.1715
Dubbo | 9GW | 132 | Dubbo 132/66kV STS | Dubbo West ZS | 140 | 33.2273 | 33.3145 | 37.9435 | 42.6072 | 42.7862 | 157 | 32.9472 | 37.5074 | 42.1446 | 42.2002 | 42.249
Dubbo | 812 | 66 | Yarrandale ZS | Gilgandra ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Dubbo | 815 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 24 | 10.1993 | 10.185 | 10.1061 | 10.0578 | 10.0024 | 28 | 8.9758 | 8.9346 | 8.918 | 8.8978 | 8.872
Dubbo | 816 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 24 | 10.1993 | 10.185 | 10.1061 | 10.0578 | 10.0024 | 28 | 8.9758 | 8.9346 | 8.918 | 8.8978 | 8.872
Dubbo | 813:EUL | 66 | Eulomogo ZS | Geurie Tee | 12 | 1.5016 | 1.4981 | 1.5108 | 1.5142 | 1.5169 | 18 | 1.2272 | 1.2286 | 1.2255 | 1.2312 | 1.2316
Dubbo | 813/1:GUE | 66 | Geurie Tee | Geurie ZS | 16 | 1.5016 | 1.4981 | 1.5108 | 1.5142 | 1.5169 | 27 | 1.2272 | 1.2286 | 1.2255 | 1.2312 | 1.2316
Dubbo | 814/1 | 66 | Gilgandra ZS | Gulargambone ZS | 11 | 7.5894 | 7.6306 | 7.6665 | 7.7047 | 7.7383 | 19 | 6.8224 | 6.8407 | 6.8617 | 6.8785 | 6.9089
Dubbo | 814/2 | 66 | Gulargambone ZS | Coonamble ZS | 11 | 5.9406 | 5.9866 | 6.0305 | 6.0743 | 6.1178 | 19 | 5.3522 | 5.3849 | 5.418 | 5.4465 | 5.4896
Dubbo | 81M | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 9.4089 | 9.4446 | 9.4601 | 9.5034 | 9.5231 | 39 | 8.7275 | 8.7383 | 8.7536 | 8.7744 | 8.7652
Dubbo | 81P | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 61 | 9.9581 | 9.9836 | 10.0078 | 10.0303 | 10.0522 | 68 | 9.0001 | 9.0195 | 9.0427 | 9.0718 | 9.0973
Dubbo | 81R | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 9.4089 | 9.4446 | 9.4601 | 9.5034 | 9.5231 | 39 | 8.7275 | 8.7383 | 8.7536 | 8.7744 | 8.7652
Dubbo | 81X | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 28 | 12.171 | 12.2021 | 12.2317 | 12.2593 | 12.286 | 34 | 11.0001 | 11.0239 | 11.0521 | 11.0878 | 11.119
Dubbo | 81T | 66 | Yarrandale ZS | Gilgandra ZS | 43 | 14.5847 | 14.6505 | 14.7206 | 14.7835 | 14.8494 | 54 | 13.2201 | 13.2751 | 13.3378 | 13.4088 | 13.4744
Forbes | 858 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 13.935 | 13.9903 | 14.0284 | 14.0525 | 14.1059 | 34 | 11.5347 | 11.5539 | 11.5762 | 11.5927 | 11.6075
Forbes | 859 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Forbes | 893/5 | 66 | TransGrid Forbes 132/66kV STS | Payten's Bridge ZS | 12 | 5.8119 | 5.7996 | 5.8327 | 5.8125 | 5.8264 | 18 | 4.1812 | 4.2121 | 4.2017 | 4.2315 | 4.2352
Forbes | 894:CDN | 66 | Condobolin ZS | Lake Cargelligo ZS | 15 | 3.6735 | 3.6856 | 3.6947 | 3.7137 | 3.725 | 25 | 3.4062 | 3.4083 | 3.4178 | 3.4223 | 3.4291
Forbes | 896:WJL | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 20 | 25.4558 | 25.4558 | 25.4558 | 25.4558 | 25.4558 | 24 | 28.2843 | 28.2843 | 28.2843 | 28.2843 | 28.2843
Forbes | 897:CDN | 66 | West Jemalong ZS | Condobolin ZS | 20 | 10.8891 | 10.9261 | 10.878 | 10.894 | 10.8623 | 24 | 10.6453 | 10.6731 | 10.6871 | 10.7038 | 10.7197
Forbes | 89H | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 43 | 42.4264 | 42.4264 | 42.4264 | 42.4264 | 42.4264 | 54 | 43.8406 | 43.8406 | 43.8406 | 43.8406 | 43.8406
Glen Innes | 886 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 70 | 5.0884 | 5.118 | 5.1258 | 5.1446 | 5.1704 | 78 | 6.6614 | 6.759 | 6.8732 | 6.9702 | 7.0892
Glen Innes | 887 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 19 | 6.0571 | 6.0923 | 6.1016 | 6.124 | 6.1547 | 33 | 7.9295 | 8.0458 | 8.1817 | 8.2972 | 8.4388
Glen Innes | 6NY | 66 | Glen Innes ZS | Guyra ZS | 11 | 3.7743 | 3.8509 | 3.9169 | 4.0142 | 4.0876 | 19 | 4.53 | 4.584 | 4.6423 | 4.688 | 4.7436
Glen Innes | 6NE | 66 | Glen Innes ZS | Emmaville ZS | 17 | 1.0244 | 1.0303 | 1.0319 | 1.0357 | 1.0409 | 30 | 1.239 | 1.2572 | 1.2784 | 1.2964 | 1.3186
Glen Innes | 6AE/A | 66 | Pindari ZS | Ashford ZS | 17 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0
Glen Innes | 6AE/E | 66 | Emmaville ZS | Pindari ZS | 17 | 0.3563 | 0.35837 | 0.35892 | 0.36024 | 0.36204 | 30 | 0.39356 | 0.39933 | 0.40608 | 0.41181 | 0.41884
Gunnedah | 877 | 66 | TransGrid Gunnedah 132/66kV STS | Keepit Dam ZS | 10 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 16 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 0.28284
Gunnedah | 878/1 | 66 | Gunnedah ZS | Emerald Hill Sw Stn | 24 | 19.5742 | 19.4981 | 19.4194 | 19.3419 | 19.2683 | 29 | 20.9549 | 20.9796 | 21.0119 | 21.0343 | 21.0724
Gunnedah | 878/5 | 66 | Emerald Hill Sw Stn | Boggabri ZS | 24 | 3.2622 | 3.2547 | 3.251 | 3.258 | 3.2737 | 29 | 4.8655 | 4.938 | 5.0149 | 5.0835 | 5.1724
Gunnedah | 88K | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 20.3783 | 20.373 | 20.3613 | 20.3823 | 20.4012 | 68 | 20.5561 | 20.7697 | 20.9684 | 21.1258 | 21.3505
Gunnedah | 88L | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 20.3783 | 20.373 | 20.3613 | 20.3823 | 20.4012 | 68 | 20.5561 | 20.7697 | 20.9684 | 21.1258 | 21.3505
Inverell | 734 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 16.9656 | 17.2512 | 17.5539 | 17.8511 | 18.1487 | 71 | 19.4126 | 19.6365 | 20.0886 | 20.4445 | 20.6701
Inverell | 735 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 17.2393 | 17.5294 | 17.837 | 18.139 | 18.4414 | 71 | 19.7257 | 19.9533 | 20.4126 | 20.7742 | 21.0034
Inverell | 6AB | 66 | Borthwick St ZS | Ashford ZS | 17 | 6.1911 | 6.2953 | 6.4057 | 6.5142 | 6.6228 | 30 | 5.7142 | 5.7801 | 5.9132 | 6.0179 | 6.0843
Inverell | 6AF/A | 66 | Ashford ZS | Wallangra ZS | 11 | 0.85512 | 0.86952 | 0.88477 | 0.89975 | 0.91475 | 19 | 1.0176 | 1.0293 | 1.053 | 1.0717 | 1.0835
Inverell | 6AF/F | 66 | Wallangra ZS | Coolatai Sw Stn | 11 | 0.7183 | 0.73039 | 0.74321 | 0.75579 | 0.76839 | 19 | 0.86104 | 0.87098 | 0.89103 | 0.90681 | 0.91682
Inverell | 6AX | 66 | Ashford ZS | Texas ZS | 9 | 5.1649 | 5.2519 | 5.344 | 5.4345 | 5.5251 | 15 | 3.8747 | 3.9194 | 4.0096 | 4.0806 | 4.1257
Inverell | 6BC | 66 | Borthwick St ZS | Copeton ZS | 21 | 0.78671 | 0.79995 | 0.81399 | 0.82777 | 0.84157 | 41 | 0.97846 | 0.98975 | 1.0125 | 1.0305 | 1.0418
Inverell | 6BD | 66 | Borthwick St ZS | Bundarra ZS | 14 | 0.88933 | 0.9043 | 0.92016 | 0.93574 | 0.95134 | 21 | 1.2133 | 1.2273 | 1.2555 | 1.2778 | 1.2919
Inverell | 6BW | 66 | Borthwick St ZS | Warialda ZS | 15 | 6.8068 | 6.9213 | 7.0428 | 7.162 | 7.2814 | 25 | 6.7709 | 6.849 | 7.0067 | 7.1308 | 7.2095
Inverell | 6FH | 66 | Coolatai Sw Stn | Yallaroi ZS | 20 | 2.1549 | 2.1912 | 2.2296 | 2.2674 | 2.3052 | 39 | 2.2309 | 2.2566 | 2.3086 | 2.3495 | 2.3754
Inverell | 6FW | 66 | Warialda ZS | Coolatai Sw Stn | 11 | 1.6418 | 1.6695 | 1.6988 | 1.7275 | 1.7563 | 19 | 1.3307 | 1.3461 | 1.377 | 1.4014 | 1.4169
Inverell | 6HG | 66 | Yallaroi ZS | Goondiwindi ZS | 20 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Inverell | 6WK | 66 | Warialda ZS | Bingara ZS | 11 | 2.6338 | 2.6781 | 2.7251 | 2.7712 | 2.8174 | 19 | 2.8571 | 2.8901 | 2.9566 | 3.009 | 3.0422
Molong | 8C1 | 66 | TransGrid Molong 132/66kV STS | Cumnock / Orange West Tee | 61 | 2.3299 | 2.3506 | 2.3926 | 2.4415 | 2.4537 | 68 | 1.8268 | 1.8697 | 1.923 | 1.9759 | 2.0205
Molong | 8C1/3 | 66 | Cumnock / Orange West Tee | Cumnock ZS | 9 | 2.3299 | 2.3506 | 2.3926 | 2.4415 | 2.4537 | 15 | 1.8268 | 1.8697 | 1.923 | 1.9759 | 2.0205
Molong | 8C1/4 | 66 | Cumnock / Orange West Tee | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Moree | 876 | 66 | TransGrid Moree 132/66kV STS | Moree Solar Farm | 70 | 57.267 | 57.3225 | 57.3997 | 57.3033 | 57.3133 | 78 | 57.7685 | 57.7937 | 57.7838 | 57.6781 | 57.7534
Moree | 87J | 66 | Moree Solar Farm | Bellata ZS | 25 | 1.1403 | 1.143 | 1.1473 | 1.1461 | 1.1491 | 27 | 0.91462 | 0.92873 | 0.9445 | 0.95648 | 0.97034
Moree | 721 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 10.2691 | 10.3975 | 10.5395 | 10.6614 | 10.7788 | 71 | 9.2564 | 9.4065 | 9.4663 | 9.5752 | 9.654
Moree | 722 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 10.8307 | 10.9661 | 11.1159 | 11.2445 | 11.3682 | 71 | 9.7626 | 9.9209 | 9.984 | 10.0988 | 10.1819
Moree | 881/1 | 66 | TransGrid Moree 132/66kV STS | Ashley Tee | 15 | 5.5167 | 5.492 | 5.5198 | 5.5179 | 5.5883 | 25 | 9.7254 | 9.7685 | 9.7487 | 9.7326 | 9.755
Moree | 881/2 | 66 | Ashley Tee | Ashley ZS | 10 | 2.6565 | 2.623 | 2.6415 | 2.6342 | 2.6934 | 16 | 3.8199 | 3.8795 | 3.8479 | 3.8289 | 3.858
Moree | 6PU | 66 | Ashley Tee | Mungindi ZS | 10 | 2.6351 | 2.6397 | 2.6465 | 2.6505 | 2.6614 | 16 | 5.7115 | 5.6979 | 5.7078 | 5.7098 | 5.7041
Moree | 723:WTR/1 | 66 | TransGrid Moree 132/66kV STS | Wathagar ZS | 12 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 19 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Moree | 723:WTR/2 | 66 | Wathagar ZS | Wenna ZS | 15 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 25 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Narrabri | 879 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 18 | 3.8909 | 3.8948 | 3.8989 | 3.9003 | 3.895 | 22 | 5.1438 | 5.1864 | 5.2435 | 5.3003 | 5.3411
Narrabri | 882 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 64 | 7.5656 | 7.5732 | 7.5811 | 7.5839 | 7.5737 | 71 | 10.0019 | 10.0847 | 10.1957 | 10.3061 | 10.3855
Narrabri | 885 | 66 | Burren Junction ZS | Merrywinebone ZS | 15 | 1.5118 | 1.5294 | 1.5469 | 1.5668 | 1.5871 | 25 | 2.553 | 2.5618 | 2.5602 | 2.5599 | 2.5568
Narrabri | 833:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 7.6497 | 7.6554 | 7.6363 | 7.6375 | 7.6378 | 43 | 8.7242 | 8.7129 | 8.6894 | 8.6897 | 8.6645
Narrabri | 834:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 7.6497 | 7.6554 | 7.6363 | 7.6375 | 7.6378 | 43 | 8.7242 | 8.7129 | 8.6894 | 8.6897 | 8.6645
Narrabri | 861/1 | 66 | TransGrid Narrabri 132/66kV STS | Wilga Park ZS | 64 | 34.8266 | 34.9406 | 35.0431 | 34.8488 | 35.0098 | 71 | 37.2632 | 37.5679 | 38.2925 | 38.7983 | 39.3462
Narrabri | 861/2 | 66 | Wilga Park ZS | Walgett ZS | 64 | 11.6782 | 11.7777 | 11.8614 | 11.9587 | 12.0418 | 71 | 11.157 | 11.3611 | 11.528 | 11.7187 | 11.8935
Narrabri | 88F | 66 | Narrabri Coal Tee | Boggabri ZS | 24 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0
Narrabri | 878/3 | 66 | TransGrid Narrabri 132/66kV STS | Narrabri Coal Tee | 61 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 68 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 26.4458
Narrabri | 88C | 66 | Narrabri Coal Tee | Narrabri Coal | 61 | 26.163 | 26.163 | 26.163 | 26.163 | 26.163 | 68 | 26.163 | 26.163 | 26.163 | 26.163 | 26.163
Narrabri | 880/1 | 66 | Wee Waa ZS | Burren Junction ZS | 13 | 3.1171 | 3.1152 | 3.1219 | 3.1232 | 3.1241 | 18 | 3.7663 | 3.7715 | 3.7717 | 3.7722 | 3.7728
Narrabri | 880/2 | 66 | Burren Junction ZS | Walgett ZS | 13 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Narrabri | 890:BRE | 66 | Walgett ZS | Brewarrina ZS | 15 | 2.813 | 2.8515 | 2.8878 | 2.9202 | 2.9629 | 25 | 2.4101 | 2.4347 | 2.4548 | 2.479 | 2.4973
Narrabri | 895:LGR | 66 | Walgett ZS | Lightning Ridge ZS | 15 | 3.1357 | 3.1586 | 3.1714 | 3.1911 | 3.2152 | 25 | 3.1278 | 3.1514 | 3.1826 | 3.2077 | 3.2324
Nyngan | 9UT | 132 | Nyngan 132/66kV STS | Nyngan Solar Farm | 106 | 35.3552 | 35.5001 | 35.7369 | 36.0184 | 36.2873 | 119 | 28.3744 | 28.5194 | 28.662 | 28.7942 | 28.9198
Nyngan | 9UW | 132 | Nyngan Solar Farm | Scrubby Valley Sw Stn | 106 | 35.3552 | 35.5001 | 35.7369 | 36.0184 | 36.2873 | 119 | 28.3744 | 28.5194 | 28.662 | 28.7942 | 28.9198
Nyngan | 946/2 | 132 | Scrubby Valley Sw Stn | Cobar CSA ZS | 106 | 21.7864 | 21.9872 | 22.2816 | 22.5519 | 22.9221 | 119 | 18.2073 | 18.2275 | 18.2917 | 18.3425 | 18.3791
Nyngan | 946/3 | 132 | Scrubby Valley Sw Stn | Cobar Peak ZS | 102 | 15.6132 | 15.6811 | 15.7541 | 15.9004 | 15.9536 | 114 | 11.1187 | 11.2622 | 11.3603 | 11.4584 | 11.5695
Nyngan | 94R | 132 | Cobar CSA ZS | Cobar Elura ZS | 128 | 2.125 | 2.1335 | 2.1417 | 2.1663 | 2.2038 | 143 | 2.0129 | 1.9202 | 1.9198 | 1.8973 | 1.855
Nyngan | 811 | 66 | Nyngan 132/66kV STS | Cobar Town ZS | 10 | 7.5246 | 7.4802 | 7.4241 | 7.3761 | 7.3148 | 16 | 7.1479 | 7.1505 | 7.1584 | 7.1506 | 7.1555
Nyngan | 854 | 66 | Nyngan 132/66kV STS | Nyngan Town ZS | 15 | 7.5041 | 7.5005 | 7.4585 | 7.4173 | 7.3923 | 25 | 6.9659 | 7.1026 | 7.2612 | 7.4168 | 7.5849
Nyngan | 820/1:NYN | 66 | Nyngan Town ZS | Nevertire Tee | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Nyngan | 820:NVE | 66 | Nyngan 132/66kV STS | Nevertire ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/1 | 66 | Nyngan 132/66kV STS | Girilambone Tee | 28 | 14.8994 | 15.025 | 15.156 | 15.2727 | 15.3946 | 34 | 15.1753 | 15.3452 | 15.4959 | 15.6593 | 15.8552
Nyngan | 855/1a | 66 | Girilambone Tee | Girilambone ZS | 24 | 11.3666 | 11.4115 | 11.463 | 11.4994 | 11.5423 | 29 | 11.6366 | 11.8112 | 11.9755 | 12.1501 | 12.3294
Nyngan | 855/2 | 66 | Girilambone Tee | Byrock Tee | 28 | 7.5072 | 7.6438 | 7.7774 | 7.9204 | 8.0547 | 34 | 7.6055 | 7.6327 | 7.6527 | 7.6734 | 7.7329
Nyngan | 855/3 | 66 | Byrock Tee | Bourke ZS | 28 | 7.1536 | 7.2943 | 7.4306 | 7.5802 | 7.7178 | 34 | 7.2919 | 7.318 | 7.3386 | 7.3582 | 7.4174
Nyngan | 855/3a | 66 | Byrock Tee | Byrock ZS | 15 | 0.11386 | 0.11431 | 0.11519 | 0.11497 | 0.11513 | 25 | 0.080177 | 0.080322 | 0.080816 | 0.081066 | 0.081217
Nyngan | 855/4 | 66 | Girilambone ZS | Tritton Mine ZS | 24 | 9.8531 | 9.8958 | 9.9363 | 9.9785 | 10.0153 | 29 | 10.1035 | 10.2514 | 10.3905 | 10.5371 | 10.692
Oberon | 94C | 132 | TransGrid Wallerawang 330/132/66kV STS | Oberon 132 ZS | 128 | 31.1387 | 32.1113 | 33.0095 | 33.9593 | 34.9375 | 143 | 34.1302 | 34.7676 | 35.4611 | 36.1434 | 36.8582
Oberon | 856 | 66 | TransGrid Wallerawang 330/132/66kV STS | Oberon Town ZS | 28 | 5.4821 | 5.5665 | 5.6598 | 5.7563 | 5.8894 | 32 | 6.438 | 6.4358 | 6.4556 | 6.4529 | 6.4667
Oberon | 81B | 33 | Oberon Town ZS | Burraga ZS | 8 | 0.44904 | 0.44973 | 0.44809 | 0.44886 | 0.44949 | 13 | 0.51779 | 0.51877 | 0.51888 | 0.52089 | 0.52183
Orange | 94G | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 85.6327 | 100.6028 | 111.8735 | 111.9702 | 115.8364 | 142 | 99.8554 | 102.4376 | 110.9306 | 111.0123 | 114.8911
Orange | 9MC | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 85.6327 | 100.6028 | 111.8735 | 111.9702 | 115.8364 | 142 | 99.8554 | 102.4376 | 110.9306 | 111.0123 | 114.8911
Orange | 807 | 66 | TransGrid Orange 132/66kV STS | Orange West & South Tee | 61 | 12.6007 | 12.5621 | 12.4915 | 12.446 | 12.3399 | 68 | 14.653 | 14.7508 | 14.8541 | 14.9862 | 15.105
Orange | 807/2 | 66 | Orange West & South Tee | Orange South ZS | 63 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0
Orange | 807/3 | 66 | Orange West & South Tee | Orange West ZS | 62 | 12.6007 | 12.5621 | 12.4915 | 12.446 | 12.3399 | 69 | 14.653 | 14.7508 | 14.8541 | 14.9862 | 15.105
Orange | 818/1 | 66 | TransGrid Orange 132/66kV STS | Blayney ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Orange | 8C2 | 66 | TransGrid Orange 132/66kV STS | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Orange | 8F1 | 66 | TransGrid Orange 132/66kV STS | Orange South ZS | 63 | 18.2296 | 18.6702 | 19.0518 | 19.5415 | 20.0605 | 70 | 24.4497 | 24.6995 | 24.9623 | 25.2335 | 25.4993
Orange | 8M1 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 11 | 10.168 | 10.289 | 10.3529 | 10.4671 | 10.6243 | 19 | 12.0644 | 12.219 | 12.3471 | 12.5234 | 12.6332
Orange | 8M2 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 21 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Parkes | 300 | 132 | TransGrid Parkes 132/66kV STS | North Parkes Mine ZS | 87 | 33.8077 | 40.1035 | 89.6025 | 94.1293 | 98.6212 | 108 | 34.7449 | 41.0527 | 90.5829 | 95.1108 | 99.6693
Parkes | 898 | 66 | TransGrid Parkes 132/66kV STS | Trundle ZS | 11 | 6.7882 | 6.7882 | 6.7882 | 6.7882 | 6.7882 | 17 | 6.364 | 6.364 | 6.364 | 6.364 | 6.364
Parkes | 899 | 66 | Parkes Town ZS | Peak Hill ZS | 13 | 9.7742 | 10.3521 | 10.9208 | 11.491 | 12.0657 | 20 | 10.3366 | 10.3999 | 10.4891 | 10.5481 | 10.6645
Parkes | 89G | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 68 | 14.1435 | 14.4775 | 14.8076 | 15.1355 | 15.4368 | 76 | 13.7175 | 13.8463 | 13.9812 | 14.0893 | 14.2255
Parkes | 89L | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 38 | 12.7291 | 13.0298 | 13.3269 | 13.622 | 13.8931 | 43 | 12.3458 | 12.4616 | 12.5831 | 12.6804 | 12.803
Parkes | 89M | 66 | Peak Hill ZS | Tomingley Mine ZS | 17 | 8.5045 | 9.0919 | 9.6733 | 10.2547 | 10.8377 | 28 | 9.2349 | 9.3106 | 9.4105 | 9.4811 | 9.6112
Tamworth | 801 | 66 | Transgrid Tamworth 132/66kV STS | Oxley Vale ZS | 63 | 14.2687 | 14.4949 | 14.6341 | 14.8409 | 14.9641 | 70 | 14.0341 | 14.3051 | 14.5951 | 14.8636 | 15.1485
Tamworth | 803 | 66 | Transgrid Tamworth 132/66kV STS | South Tamworth ZS | 70 | 28.1733 | 28.1917 | 28.2216 | 28.2778 | 28.2769 | 78 | 27.9454 | 28.1742 | 28.4223 | 28.6726 | 28.9858
Tamworth | 804 | 66 | Transgrid Tamworth 132/66kV STS | Nundle ZS | 8 | 1.4937 | 1.4703 | 1.4542 | 1.429 | 1.4148 | 13 | 1.6628 | 1.6895 | 1.7117 | 1.7377 | 1.7608
Tamworth | 806 | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 38 | 11.8778 | 11.8754 | 11.8781 | 11.8815 | 11.8741 | 47 | 9.9306 | 10.0116 | 10.096 | 10.1829 | 10.2635
Tamworth | 873 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 15.206 | 15.1506 | 15.167 | 15.1861 | 15.1609 | 61 | 13.221 | 13.2183 | 13.2646 | 13.2962 | 13.3468
Tamworth | 874 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 15.8266 | 15.769 | 15.786 | 15.8059 | 15.7797 | 61 | 13.7607 | 13.7578 | 13.806 | 13.8389 | 13.8915
Tamworth | 803/2 | 66 | South Tamworth ZS | Oxley Vale ZS | 63 | 4.7562 | 4.8316 | 4.878 | 4.947 | 4.988 | 70 | 4.678 | 4.7684 | 4.865 | 4.9545 | 5.0495
Tamworth | 806/1 | 66 | Goddard Lane ZS | Attunga ZS | 18 | 11.0908 | 11.0746 | 11.0642 | 11.0593 | 11.0253 | 33 | 8.5464 | 8.5918 | 8.6305 | 8.6746 | 8.7071
Tamworth | 806/1 | 66 | Attunga ZS | Manilla ZS | 18 | 7.6547 | 7.6384 | 7.6277 | 7.6193 | 7.5956 | 33 | 6.1939 | 6.2361 | 6.2729 | 6.3134 | 6.3453
Tamworth | 806/2 | 66 | Manilla ZS | Upper Manilla ZS | 18 | 2.6738 | 2.6603 | 2.6408 | 2.6336 | 2.6223 | 33 | 2.5084 | 2.5222 | 2.5349 | 2.5463 | 2.5572
Tamworth | 806/4 | 66 | Upper Manilla ZS | Barraba ZS | 15 | 2.278 | 2.2758 | 2.2642 | 2.2697 | 2.272 | 25 | 2.2964 | 2.3096 | 2.3254 | 2.3364 | 2.3503
Tamworth | 80C | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 61 | 10.5332 | 10.531 | 10.5334 | 10.5364 | 10.5298 | 68 | 8.8064 | 8.8782 | 8.9531 | 9.0301 | 9.1016
Tamworth | 813:CLA | 66 | Transgrid Tamworth 132/66kV STS | Currububula ZS | 28 | 14.8981 | 14.8649 | 14.8579 | 14.8274 | 14.8268 | 34 | 13.2218 | 13.4473 | 13.6696 | 13.8862 | 14.1357
Tamworth | 813/1:QDI | 66 | Currububula ZS | Werris Creek ZS | 28 | 13.6255 | 13.6078 | 13.6117 | 13.5943 | 13.6068 | 34 | 12.1814 | 12.3956 | 12.6088 | 12.8135 | 13.052
Tamworth | 813/2:QDI | 66 | Werris Creek ZS | Quirindi ZS | 28 | 11.5135 | 11.502 | 11.5147 | 11.5136 | 11.5414 | 34 | 10.339 | 10.5615 | 10.7866 | 11.0011 | 11.2463
Tamworth | 870/1:KTL | 66 | Transgrid Tamworth 132/66kV STS | Kootingal Tee | 14 | 6.6867 | 6.7421 | 6.7962 | 6.8447 | 6.8908 | 21 | 6.3711 | 6.4716 | 6.557 | 6.6817 | 6.79
Tamworth | 870/2:KTL | 66 | Kootingal Tee | Kootingal ZS | 12 | 6.0081 | 6.0555 | 6.1053 | 6.1515 | 6.1908 | 20 | 5.6426 | 5.7394 | 5.8211 | 5.942 | 6.0462
Tamworth | 870/3:KTL | 66 | Kootingal Tee | Bendemeer ZS | 13 | 0.69303 | 0.70046 | 0.70422 | 0.70646 | 0.71259 | 21 | 0.73352 | 0.73657 | 0.7397 | 0.74292 | 0.74648
Tamworth | 798 | 33 | Quirindi ZS | Murrurundi ZS | 4 | 2.7679 | 2.7659 | 2.772 | 2.7785 | 2.783 | 6 | 2.544 | 2.5872 | 2.6363 | 2.6839 | 2.7324
Tamworth | 799/1 | 33 | Quirindi ZS | Caroona Tee | 6 | 3.0831 | 3.1041 | 3.1188 | 3.1338 | 3.1448 | 10 | 2.5398 | 2.544 | 2.5477 | 2.5507 | 2.5555
Tamworth | 799/2 | 33 | Caroona Tee | Caroona ZS | 4 | 0.96544 | 0.96387 | 0.96306 | 0.96219 | 0.96022 | 6 | 0.67697 | 0.67839 | 0.68011 | 0.68431 | 0.68719
Tamworth | 799/3 | 33 | Caroona Tee | Spring Ridge ZS | 3 | 0.63273 | 0.63956 | 0.64478 | 0.65244 | 0.65946 | 5 | 0.64641 | 0.64771 | 0.6493 | 0.64763 | 0.64992
Tamworth | 799/4 | 33 | Spring Ridge ZS | Colly Blue ZS | 3 | 1.2361 | 1.2545 | 1.268 | 1.2795 | 1.2895 | 5 | 0.97469 | 0.97556 | 0.97575 | 0.97624 | 0.97601
Wellington | 945/3 | 132 | TransGrid Line 945 Wellington 132kV Tee | Wellington 132kV ZS | 124 | 8.9336 | 8.9658 | 8.9588 | 8.9736 | 9.0167 | 139 | 9.054 | 9.1252 | 9.2291 | 9.3355 | 9.4172
Wellington | 947/1 | 132 | TransGrid Line 947 Burrendong Tee | Burrendong Hydro | 36 | 6.6286 | 6.6309 | 6.6325 | 6.6338 | 6.6376 | 64 | 8.8925 | 9.0232 | 9.0775 | 9.1582 | 9.2102
Wellington | 94F | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 88.0473 | 88.523 | 110.4066 | 132.9358 | 133.0682 | 194 | 80.8707 | 103.1397 | 125.3242 | 125.43 | 125.3598
Wellington | 94J | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 80.6035 | 80.3589 | 80.1504 | 80.0514 | 79.8137 | 194 | 80.7915 | 81.1104 | 81.5114 | 81.8585 | 82.1305
Wellington | 805 | 66 | Wellington 132kV ZS | Mumbil ZS | 11 | 1.3495 | 1.3653 | 1.3771 | 1.3977 | 1.4142 | 19 | 1.1217 | 1.1223 | 1.123 | 1.121 | 1.1224
Wellington | 813:WGN | 66 | Wellington 132kV ZS | Geurie Tee | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Albury | 997/1 | 132 | Union Rd ZS | Corowa ZS | 128 | 71.0689 | 71.2491 | 70.6693 | 70.7395 | 71.7269 | 143 | 78.7879 | 79.2016 | 78.8055 | 78.391 | 78.7235
Albury | 997/2 | 132 | Corowa ZS | Mulwala ZS | 128 | 82.2791 | 82.5032 | 82.0489 | 82.1873 | 83.284 | 143 | 89.0796 | 89.5095 | 89.1661 | 88.7412 | 89.0976
Albury | 99E | 132 | Union Rd ZS | Jelbart ZS | 148 | 18.5927 | 18.5441 | 18.4742 | 18.3748 | 18.3076 | 164 | 17.0705 | 17.2993 | 17.5155 | 17.7571 | 17.9668
Albury | 99G | 132 | Union Rd ZS | Jelbart ZS | 148 | 18.5927 | 18.5441 | 18.4742 | 18.3748 | 18.3076 | 164 | 17.0705 | 17.2993 | 17.5155 | 17.7571 | 17.9668
Bega | 84G | 66 | Bega 132/66kV STS | Eden South ZS | 61 | 6.7697 | 6.7616 | 6.7485 | 6.7358 | 6.7238 | 68 | 7.9483 | 8.0195 | 8.1028 | 8.1765 | 8.258
Bega | 84H | 66 | Eden South ZS | Edrom ZS | 38 | 2.3356 | 2.3416 | 2.3523 | 2.3527 | 2.3645 | 43 | 2.2684 | 2.2661 | 2.2643 | 2.2555 | 2.2516
Bega | 84M | 66 | Bega 132/66kV STS | Maher St ZS | 61 | 9.2335 | 9.2531 | 9.269 | 9.2751 | 9.3162 | 68 | 11.3545 | 11.5445 | 11.7456 | 11.9478 | 12.1334
Bega | 89A | 66 | Bega 132/66 | Pambula ZS | 38 | 10.4207 | 10.3972 | 10.3826 | 10.3729 | 10.3566 | 43 | 15.4114 | 15.4909 | 15.6104 | 15.7061 | 15.8106
Bega | 84P | 66 | Bega 132/66kV STS | Maher St ZS | 38 | 9.2335 | 9.2531 | 9.269 | 9.2751 | 9.3162 | 43 | 11.3545 | 11.5445 | 11.7456 | 11.9478 | 12.1334
Bega | 89F | 66 | Pambula ZS | Eden South ZS | 16 | 2.6251 | 2.6223 | 2.6168 | 2.6111 | 2.606 | 26 | 2.916 | 2.944 | 2.9756 | 3.0041 | 3.0359
Bega | 7802/1 | 33 | Maher St ZS | Brogo ZS | 12 | 4.306 | 4.3045 | 4.316 | 4.324 | 4.3434 | 24 | 6.033 | 6.246 | 6.4469 | 6.6661 | 6.8488
Bega | 7802/2 | 33 | Brogo ZS | Cobargo ZS | 10 | 3.8202 | 3.8199 | 3.8227 | 3.8208 | 3.8275 | 19 | 5.0795 | 5.1747 | 5.2498 | 5.3276 | 5.4215
Bega | 84R | 33 | Maher St ZS | Quira ZS | 6 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0
Bega | 7814 | 33 | Cobargo ZS | Bermagui ZS | 5 | 2.6237 | 2.6225 | 2.6253 | 2.6257 | 2.629 | 9 | 3.3766 | 3.4419 | 3.491 | 3.5466 | 3.6039
Buronga | 87G | 66 | Dareton ZS | Ellerslie ZS | 67 | 8.3129 | 8.3159 | 8.3061 | 8.3299 | 8.3575 | 78 | 6.8344 | 6.8735 | 6.8828 | 6.9087 | 6.9136
Buronga | 87H/1 | 66 | Ellerslie ZS | Ginkgo Snapper Tee | 45 | 6.6965 | 6.6976 | 6.6868 | 6.7105 | 6.7507 | 56 | 6.3439 | 6.3781 | 6.3867 | 6.4135 | 6.4171
Buronga | 87H/2 | 66 | Ginkgo Snapper Tee | Ginkgo ZS | 20 | 6.6996 | 6.7132 | 6.7084 | 6.7296 | 6.7791 | 39 | 6.7322 | 6.7669 | 6.7821 | 6.8069 | 6.8149
Buronga | 87H/3 | 66 | Ginkgo Snapper Tee | Snapper ZS | 12 | 0.28813 | 0.27507 | 0.26853 | 0.27199 | 0.26424 | 19 | 0.3337 | 0.33677 | 0.33113 | 0.33747 | 0.33323
Buronga | 83U | 66 | Powercor Mildura ZS (NSW Border) | Buronga ZS | 22 | 21.4724 | 21.9893 | 22.7001 | 23.0549 | 23.5198 | 43 | 16.9925 | 17.2067 | 17.157 | 17.2527 | 17.3482
Buronga | 83W | 66 | Buronga ZS | Dareton ZS | 22 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0
Buronga | Merbein - Dareton Line | 66 | Powercor Mildura ZS (NSW Border) | Dareton ZS | 49 | 11.0161 | 10.8797 | 10.7206 | 10.7003 | 10.7102 | 61 | 9.6261 | 9.5951 | 9.6802 | 9.7442 | 9.7673
Coleambally | CLY1526 | 33 | Coleambally 132/33kV STS | Coleambally Tee | 10 | 1.8805 | 1.8637 | 1.8461 | 1.8306 | 1.8252 | 19 | 1.835 | 1.827 | 1.8222 | 1.8294 | 1.8233
Coleambally | CLY1526 | 33 | Coleambally Tee | Coleambally ZS | 10 | 1.7095 | 1.6943 | 1.6782 | 1.6642 | 1.6592 | 19 | 1.6682 | 1.6609 | 1.6565 | 1.6631 | 1.6576
Coleambally | CLY1526 | 33 | Coleambally Tee | Egansford ZS | 8 | 1.007 | 0.98309 | 0.96987 | 0.94877 | 0.93161 | 13 | 0.9937 | 0.99079 | 1.0045 | 1.0041 | 1.0215
Coleambally | CLY1530 | 33 | Coleambally 132/33kV STS | Ringwood Rd ZS | 8 | 5.2059 | 5.1955 | 5.1784 | 5.1633 | 5.1651 | 13 | 4.0549 | 4.0902 | 4.1377 | 4.1833 | 4.2262
Coleambally | CLY1530 | 33 | Ringwood Rd ZS | Darlington Point ZS | 8 | 3.4266 | 3.4265 | 3.4226 | 3.4157 | 3.4252 | 13 | 2.735 | 2.7981 | 2.8816 | 2.9522 | 3.0238
Cooma | 974 | 132 | TransGrid Cooma 132/66kV STS | Bega 132/66kV STS | 128 | 15.9375 | 15.926 | 15.9086 | 15.9586 | 15.9018 | 143 | 22.6446 | 22.7108 | 22.7688 | 22.6546 | 22.7746
Cooma | 97R | 132 | TransGrid Cooma 132/66kV STS | Steeple Flat 132/66kV STS | 140 | 86.7981 | 86.9149 | 86.8046 | 87.0068 | 86.9362 | 157 | 72.7295 | 72.364 | 72.8148 | 72.506 | 71.9981
Cooma | 82D | 66 | TransGrid Cooma 132/66kV STS | Jindabyne East ZS | 20 | 4.7086 | 4.7584 | 4.8136 | 4.8682 | 4.9201 | 39 | 11.2652 | 11.4421 | 11.6312 | 11.7836 | 11.9741
Cooma | 84J | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 70 | 5.1395 | 5.1392 | 5.139 | 5.1317 | 5.1292 | 78 | 6.8682 | 6.9697 | 7.056 | 7.1587 | 7.2519
Cooma | 84L | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 64 | 5.1395 | 5.1392 | 5.139 | 5.1317 | 5.1292 | 71 | 6.8682 | 6.9697 | 7.056 | 7.1587 | 7.2519
Cooma | 82J/1 | 66 | Snowy Adit 132/66/11kV ZS | Snowy Lookout Sw Stn | 12 | 3.9158 | 3.9223 | 3.9522 | 3.9323 | 3.8813 | 20 | 7.5245 | 7.7282 | 8.0067 | 8.2234 | 8.4908
Cooma | 82J/2 | 66 | Jindabyne ZS | Snowy Lookout Sw Stn | 12 | 3.8128 | 3.8195 | 3.8499 | 3.8299 | 3.7784 | 19 | 7.0396 | 7.2442 | 7.5197 | 7.7373 | 8.0039
Cooma | 82R | 66 | Jindabyne East ZS | Jindabyne ZS | 20 | 2.2706 | 2.2688 | 2.2702 | 2.2676 | 2.2673 | 39 | 6.0727 | 6.1396 | 6.226 | 6.2804 | 6.3588
Cooma | 888/1 | 66 | TransGrid Cooma 132/66kV STS | Rhine Falls Sw Stn | 16 | 1.5092 | 1.5289 | 1.547 | 1.5639 | 1.5798 | 25 | 2.197 | 2.1953 | 2.1974 | 2.1977 | 2.2091
Cooma | 888/3 | 66 | Rhine Falls Sw Stn | Adaminaby ZS | 16 | 1.1409 | 1.1616 | 1.181 | 1.1993 | 1.2164 | 25 | 1.7344 | 1.7293 | 1.7285 | 1.7255 | 1.734
Cooma | 888/4 | 66 | Rhine Falls Sw Stn | Eucumbene Tee | 15 | 0.27164 | 0.27196 | 0.27177 | 0.27214 | 0.27185 | 25 | 0.36572 | 0.37049 | 0.37474 | 0.37834 | 0.38294
Cooma | 888/6 | 66 | Eucumbene Tee | Eucumbene ZS | 15 | 0.13866 | 0.13886 | 0.13867 | 0.13887 | 0.13865 | 25 | 0.23562 | 0.24027 | 0.24437 | 0.24825 | 0.25269
Cooma | 888/7 | 66 | Eucumbene Tee | Snowy Adit 132/66/11kV ZS | 20 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Cooma | 849/1 | 33 | Adaminaby ZS | Providence Portal ZS | 7 | 0.08946 | 0.08849 | 0.089144 | 0.090012 | 0.089285 | 12 | 0.2685 | 0.26853 | 0.26603 | 0.26728 | 0.27515
Cowra | 865 | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 9.6027 | 9.6186 | 9.6283 | 9.6496 | 9.7117 | 25 | 7.8976 | 7.9784 | 8.0452 | 8.121 | 8.1917
Cowra | 863:CWD | 66 | TransGrid Cowra 132/66kV STS | Canowindra ZS | 9 | 5.8474 | 5.8627 | 5.8793 | 5.8888 | 5.8857 | 15 | 4.9741 | 5.0181 | 5.0643 | 5.109 | 5.1541
Cowra | 866:COW | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 9.6027 | 9.6186 | 9.6283 | 9.6496 | 9.7117 | 25 | 7.8976 | 7.9784 | 8.0452 | 8.121 | 8.1917
Cowra | 891/1 | 66 | TransGrid Cowra 132/66kV STS | Wyangala Dam Tee | 20 | 30.7478 | 30.7544 | 30.7618 | 30.7705 | 30.7794 | 24 | 31.0592 | 31.0644 | 31.0645 | 31.066 | 31.0692
Cowra | 891/2 | 66 | Wyangala Dam Tee | Wyangala Dam | 19 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 33 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 31.8198
Cowra | 891/5 | 66 | Monteagle Tee | Monteagle ZS | 13 | 0.8666 | 0.86419 | 0.86098 | 0.85814 | 0.85294 | 22 | 0.91609 | 0.91893 | 0.92359 | 0.92585 | 0.93176
Cowra | 891/6 | 66 | Monteagle Tee | Young ZS | 19 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0
Cowra | 891/7 | 66 | Bendick Murrell Tee | Bendick Murrell ZS | 19 | 1.6979 | 1.7058 | 1.7164 | 1.7213 | 1.7313 | 33 | 1.5424 | 1.5395 | 1.5444 | 1.5503 | 1.5494
Cowra | 891:BMU | 66 | Wyangala Dam Tee | Bendick Murrell Tee | 19 | 2.4359 | 2.4412 | 2.4483 | 2.4504 | 2.455 | 33 | 2.3354 | 2.3354 | 2.3439 | 2.3506 | 2.3537
Cowra | 891:BMU | 66 | Bendick Murrell Tee | Monteagle Tee | 19 | 0.8666 | 0.86419 | 0.86098 | 0.85814 | 0.85294 | 33 | 0.91609 | 0.91893 | 0.92359 | 0.92585 | 0.93176
Cowra | 893/1 | 66 | TransGrid Cowra 132/66kV STS | Grenfell Tee | 12 | 4.4159 | 4.4198 | 4.4181 | 4.4084 | 4.4095 | 18 | 4.6714 | 4.7583 | 4.8091 | 4.87 | 4.9433
Cowra | 893/4 | 66 | Grenfell Tee | Payten's Bridge ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Cowra | 893/6 | 66 | Grenfell Tee | Grenfell ZS | 12 | 4.4159 | 4.4198 | 4.4181 | 4.4084 | 4.4095 | 18 | 4.6714 | 4.7583 | 4.8091 | 4.87 | 4.9433
Darlington Point | 99N | 132 | TransGrid Darlington Point 330/132kV STS | Hillston ZS | 128 | 13.2855 | 13.3455 | 13.4036 | 13.4282 | 13.5395 | 143 | 12.6216 | 12.9073 | 13.1372 | 13.4056 | 13.6758
Darlington Point | 99R | 132 | TransGrid Darlington Point 330/132kV STS | Hay 132 ZS | 128 | 10.2599 | 10.2776 | 10.2537 | 10.2449 | 10.2492 | 143 | 14.1834 | 14.2085 | 14.2508 | 14.2731 | 14.2617
Darlington Point | HAT 22 | 33 | Hay 132 ZS | Hay ZS | 8 | 4.5264 | 4.5527 | 4.5731 | 4.6032 | 4.6346 | 14 | 6.973 | 7.0226 | 7.0511 | 7.0914 | 7.134
Darlington Point | HAT 32 | 33 | Hay 132 ZS | Hay ZS | 8 | 1.1316 | 1.1382 | 1.1433 | 1.1508 | 1.1586 | 14 | 1.7433 | 1.7557 | 1.7628 | 1.7728 | 1.7835
Darlington Point | HAT 42 | 33 | Hay 132 ZS | Carrathool ZS | 7 | 6.9224 | 6.9284 | 6.9036 | 6.8896 | 6.8857 | 12 | 7.3478 | 7.3617 | 7.383 | 7.3957 | 7.3903
Darlington Point | HIL1117 | 33 | Hillston ZS | Ivanhoe ZS | 8 | 5.5467 | 5.5702 | 5.6273 | 5.651 | 5.7117 | 14 | 4.1353 | 4.1769 | 4.2085 | 4.2463 | 4.2878
Deniliquin | 844 | 66 | TransGrid Deniliquin 132/66kV STS | Barham ZS | 11 | 5.4463 | 5.4899 | 5.5235 | 5.5612 | 5.6092 | 19 | 4.879 | 4.9394 | 4.9725 | 5.0185 | 5.0651
Deniliquin | 845 | 66 | TransGrid Deniliquin 132/66kV STS | Deniliquin ZS | 38 | 20.7147 | 20.8804 | 21.0081 | 21.1517 | 21.3342 | 43 | 18.5325 | 18.7622 | 18.888 | 19.0626 | 19.2394
Deniliquin | 822/1 | 66 | TransGrid Deniliquin 132/66kV STS | Murgha ZS | 11 | 7.1221 | 7.1791 | 7.223 | 7.2724 | 7.3351 | 19 | 6.9591 | 7.0454 | 7.0926 | 7.1582 | 7.2246
Deniliquin | 822/2 | 66 | Murgha ZS | Moulamein ZS | 11 | 5.9584 | 6.006 | 6.0428 | 6.0841 | 6.1366 | 19 | 5.938 | 6.0116 | 6.0519 | 6.1078 | 6.1645
Deniliquin | 84Y | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 66 | 8.0066 | 8.0706 | 8.12 | 8.1755 | 8.246 | 66 | 4.6899 | 4.748 | 4.7798 | 4.824 | 4.8687
Deniliquin | MM61 | 66 | Moulamein ZS | Koraleigh ZS | 15 | 3.9567 | 3.9884 | 4.0128 | 4.0402 | 4.0751 | 25 | 2.7988 | 2.8335 | 2.8525 | 2.8788 | 2.9055
Deniliquin | No.6 Moama | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 34 | 5.586 | 5.6307 | 5.6651 | 5.7038 | 5.7531 | 39 | 3.3283 | 3.3695 | 3.3921 | 3.4235 | 3.4552
Finley | 9R4 | 132 | TransGrid Finley 132/66kV STS | Mulwala ZS | 140 | 92.294 | 92.5633 | 92.1244 | 92.2749 | 93.4266 | 157 | 97.4116 | 97.9212 | 97.6592 | 97.3129 | 97.7638
Finley | 84A | 66 | TransGrid Finley 132/66kV STS | Jerilderie ZS | 15 | 3.012 | 3.0199 | 3.0268 | 3.0343 | 3.0403 | 25 | 3.9155 | 3.9373 | 3.9584 | 3.9748 | 4.0084
Finley | 84B | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 4.2403 | 4.2403 | 4.2553 | 4.2578 | 4.2598 | 70 | 3.9591 | 3.9854 | 4.0084 | 4.0378 | 4.0736
Finley | 84C | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 7.8748 | 7.8749 | 7.9028 | 7.9074 | 7.911 | 70 | 7.3527 | 7.4014 | 7.4442 | 7.4987 | 7.5653
Goulburn | 972 | 132 | TransGrid Marulan 330/132kV STS | Goulburn 132/66/33kV STS | 180 | 58.3392 | 57.4235 | 56.2617 | 55.0308 | 53.8696 | 202 | 55.2891 | 52.924 | 50.5489 | 48.6521 | 46.3718
Goulburn | 9UR | 132 | TransGrid Marulan 330/132kV STS | Taralga Wind Farm | 140 | 103.8596 | 104.105 | 104.2248 | 104.2905 | 104.482 | 157 | 110.3329 | 110.1071 | 110.0604 | 110.4221 | 110.3546
Goulburn | 843 | 66 | Clinton St ZS | Goulburn North ZS | 46 | 4.2685 | 4.2965 | 4.3119 | 4.3605 | 4.4124 | 52 | 5.3827 | 5.4534 | 5.528 | 5.6072 | 5.6652
Goulburn | 82K/2 | 66 | Woodlawn ZS | Bungendore ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Goulburn | 840:GOU | 66 | Goulburn 132/66/33kV STS | Goulburn North ZS | 61 | 7.3967 | 7.2967 | 7.3302 | 7.3889 | 7.3026 | 68 | 10.9963 | 10.9544 | 10.9452 | 11.0332 | 11.0469
Goulburn | 841:GBN | 66 | Goulburn North ZS | Crookwell ZS | 9 | 3.7885 | 3.7846 | 3.7939 | 3.7924 | 3.8106 | 13 | 4.3458 | 4.3436 | 4.3491 | 4.3323 | 4.3339
Goulburn | 850:GOU | 66 | Goulburn 132/66/33kV STS | Woodlawn ZS | 28 | 7.8109 | 7.8176 | 7.8783 | 7.8728 | 7.9009 | 34 | 7.1336 | 7.2108 | 7.2125 | 7.2724 | 7.3185
Goulburn | 86M/1 | 66 | Goulburn 132/66/33kV STS | Marulan North Tee | 25 | 12.3956 | 12.4383 | 12.4941 | 12.5601 | 12.6203 | 29 | 13.0301 | 13.2432 | 13.4474 | 13.6639 | 13.8709
Goulburn | 86M/2 | 66 | Marulan North Tee | Marulan South ZS | 25 | 7.5538 | 7.548 | 7.5584 | 7.5814 | 7.5855 | 29 | 7.6014 | 7.6594 | 7.7173 | 7.7849 | 7.8399
Goulburn | 86L | 66 | Marulan North Tee | Marulan North ZS | 12 | 6.2708 | 6.3187 | 6.3656 | 6.4119 | 6.472 | 19 | 6.9466 | 7.1295 | 7.3011 | 7.4759 | 7.6529
Goulburn | 870:GOU | 66 | Goulburn 132/66/33kV STS | Clinton St ZS | 34 | 18.1965 | 18.133 | 18.1643 | 18.2894 | 18.2551 | 41 | 24.6618 | 24.7909 | 24.9652 | 25.2538 | 25.4117
Goulburn | GOU12 | 33 | Goulburn 132/66/33kV STS | Brisbane Grove ZS | 7 | 2.3301 | 2.3537 | 2.3781 | 2.3857 | 2.4004 | 12 | 2.6387 | 2.6598 | 2.6767 | 2.6964 | 2.7117
Griffith | 79C/1 | 33 | TransGrid Griffith 132/33kV STS | Widgelli / Willbriggie Tee | 10 | 6.2167 | 6.2205 | 6.2163 | 6.2168 | 6.2165 | 19 | 5.7841 | 5.913 | 6.0436 | 6.1593 | 6.2804
Griffith | 79C/2 | 33 | Widgelli / Willbriggie Tee | Widgelli ZS | 10 | 1.2062 | 1.207 | 1.2061 | 1.2063 | 1.2062 | 19 | 0.99512 | 1.0173 | 1.0398 | 1.0597 | 1.0805
Griffith | 79C/3 | 33 | Widgelli / Willbriggie Tee | Willbriggie Tee | 10 | 5.0105 | 5.0136 | 5.0101 | 5.0106 | 5.0103 | 19 | 4.789 | 4.8957 | 5.0039 | 5.0996 | 5.1999
Griffith | 79C/4 | 33 | Willbriggie Tee | Willbriggie ZS | 10 | 4.4538 | 4.4565 | 4.4534 | 4.4539 | 4.4536 | 19 | 4.2292 | 4.3235 | 4.419 | 4.5035 | 4.5921
Griffith | 79C/5 | 33 | Willbriggie Tee | 79C / 79P Tee | 10 | 0.55672 | 0.55706 | 0.55668 | 0.55673 | 0.5567 | 19 | 0.49756 | 0.50864 | 0.51988 | 0.52983 | 0.54025
Griffith | 79F | 33 | TransGrid Griffith 132/33kV STS | Yenda ZS | 22 | 12.155 | 12.1625 | 12.1542 | 12.1553 | 12.1547 | 27 | 8.5207 | 8.7105 | 8.903 | 9.0733 | 9.2517
Griffith | 79G | 33 | Beelbangera ZS | Griffith ZS | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0
Griffith | 79J | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0
Griffith | 79L | 33 | TransGrid Griffith 132/33kV STS | Beelbangera ZS | 10 | 13.5468 | 13.5552 | 13.5459 | 13.5472 | 13.5464 | 19 | 8.0853 | 8.2654 | 8.4481 | 8.6097 | 8.779
Griffith | 79M | 33 | TransGrid Griffith 132/33kV STS | Hanwood ZS | 22 | 13.9598 | 14.0279 | 14.0652 | 14.1022 | 14.1731 | 27 | 12.3794 | 12.4168 | 12.557 | 12.6409 | 12.8065
Griffith | 79P | 33 | TransGrid Griffith 132/33kV STS | Warrawidgee Tee | 22 | 9.557 | 9.5629 | 9.5563 | 9.5572 | 9.5567 | 27 | 7.5878 | 7.7568 | 7.9282 | 8.0799 | 8.2388
Griffith | 79W | 33 | Warrawidgee Tee | Warrawidgee ZS | 6 | 2.2269 | 2.2283 | 2.2267 | 2.2269 | 2.2268 | 9 | 1.7415 | 1.7802 | 1.8196 | 1.8544 | 1.8909
Griffith | 79W | 33 | Warrawidgee Tee | Nericon Tee | 21 | 6.6806 | 6.6848 | 6.6802 | 6.6808 | 6.6804 | 27 | 5.3487 | 5.4679 | 5.5887 | 5.6957 | 5.8076
Griffith | 79W | 33 | Nericon Tee | Nericon ZS | 6 | 2.9692 | 2.971 | 2.969 | 2.9692 | 2.9691 | 9 | 1.8658 | 1.9074 | 1.9496 | 1.9869 | 2.0259
Griffith | 79R | 33 | TransGrid Griffith 132/33kV STS | Tharbogang ZS | 31 | 13.6219 | 13.6775 | 13.7406 | 13.7874 | 13.819 | 34 | 10.2127 | 10.2613 | 10.3175 | 10.3745 | 10.4425
Griffith | 79U | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 23.5002 | 23.5686 | 23.4953 | 23.572 | 23.4998 | 56 | 20.6461 | 20.6767 | 20.6586 | 20.7207 | 20.6584
Harden - Murrumburrah | 836 | 66 | TransGrid Murrumburrah 132/66kV STS | Cootamundra ZS | 12 | 9.3033 | 9.3388 | 9.3023 | 9.3045 | 9.3084 | 18 | 8.6314 | 8.7113 | 8.789 | 8.8576 | 8.9222
Harden - Murrumburrah | 837 | 66 | TransGrid Murrumburrah 132/66kV STS | Jugiong ZS | 12 | 1.6593 | 1.6651 | 3.4799 | 3.4911 | 3.5026 | 18 | 1.4916 | 1.4796 | 3.2672 | 3.2553 | 3.245
Harden - Murrumburrah | 847 | 66 | TransGrid Murrumburrah 132/66kV STS | Boorowa ZS | 10 | 6.0119 | 6.0118 | 6.0094 | 6.0052 | 5.9956 | 16 | 6.3679 | 6.5022 | 6.6326 | 6.7568 | 6.8852
Harden - Murrumburrah | 823/3 | 66 | Bogalara Sw Stn | Marilba ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 830/1:PCR | 66 | Bogalara Sw Stn | Parsons Creek ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 838/3 | 66 | Jugiong ZS | Bogalara Sw Stn | 12 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 83A | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 4.4217 | 4.4057 | 4.3746 | 4.3641 | 4.35 | 25 | 4.8422 | 4.8795 | 4.9124 | 4.9589 | 4.993
Harden - Murrumburrah | 83D | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 890:YOU | 66 | TransGrid Murrumburrah 132/66kV STS | Young ZS | 24 | 15.9013 | 15.9559 | 15.9101 | 15.9242 | 15.947 | 28 | 17.8521 | 18.0698 | 18.2855 | 18.5427 | 18.7466
Moruya North | 98H | 132 | Endeavour Energy Evans Lane Sw Stn | Moruya North 132/33kV STS | 180 | 17.9538 | 18.0346 | 18.0422 | 18.0877 | 18.1786 | 202 | 24.6657 | 24.7344 | 24.7952 | 24.943 | 25.0333
Moruya North | 98M | 132 | Endeavour Energy Evans Lane Sw Stn | Batemans Bay ZS | 50 | 22.6085 | 22.7102 | 22.7198 | 22.7771 | 22.8916 | 62 | 30.8591 | 30.945 | 31.021 | 31.206 | 31.319
Moruya North | 98T | 132 | Batemans Bay ZS | Moruya North 132/33kV STS | 61 | 4.068 | 4.0863 | 4.088 | 4.0983 | 4.1189 | 70 | 6.1395 | 6.1566 | 6.1717 | 6.2085 | 6.231
Moruya North | 7703 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 30 | 6.806 | 6.8366 | 6.8395 | 6.8568 | 6.8912 | 34 | 9.5324 | 9.5589 | 9.5824 | 9.6396 | 9.6745
Moruya North | 7704 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 26 | 8.6444 | 8.6833 | 8.687 | 8.7089 | 8.7527 | 30 | 12.1174 | 12.1512 | 12.181 | 12.2537 | 12.298
Moruya North | 7706 | 33 | Moruya North 132/33kV STS | Mossy Point ZS | 25 | 5.8673 | 5.8937 | 5.8962 | 5.911 | 5.9407 | 28 | 8.186 | 8.2088 | 8.229 | 8.278 | 8.308
Moruya North | 7712 | 33 | Bodalla Tee | Bodalla ZS | 10 | 1.2126 | 1.218 | 1.2185 | 1.2216 | 1.2278 | 19 | 1.6157 | 1.6202 | 1.6241 | 1.6338 | 1.6397
Moruya North | 7713 | 33 | Bodalla Tee | Narooma ZS | 21 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0
Moruya North | 7817 | 33 | Narooma Tee | Cobargo ZS | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/1 | 33 | Moruya Town ZS | Tuross Tee | 17 | 2.9336 | 2.9468 | 2.9481 | 2.9555 | 2.9704 | 19 | 4.6854 | 4.6985 | 4.71 | 4.7381 | 4.7552
Moruya North | 7711/2 | 33 | Tuross Tee | Tuross ZS | 7 | 1.7211 | 1.7288 | 1.7295 | 1.7339 | 1.7426 | 12 | 3.0159 | 3.0243 | 3.0317 | 3.0498 | 3.0608
Moruya North | 7711/3 | 33 | Tuross Tee | Bodalla Tee | 21 | 1.1735 | 1.1787 | 1.1792 | 1.1822 | 1.1881 | 27 | 1.6157 | 1.6202 | 1.6241 | 1.6338 | 1.6397
Moruya North | 7715/1 | 33 | Moruya Town ZS | Narooma Tee | 30 | 5.789 | 5.8151 | 5.8175 | 5.8322 | 5.8615 | 34 | 8.6707 | 8.6948 | 8.7162 | 8.7682 | 8.7999
Moruya North | 7715/2 | 33 | Narooma Tee | Narooma ZS | 10 | 5.4761 | 5.5007 | 5.5031 | 5.5169 | 5.5447 | 19 | 8.186 | 8.2088 | 8.229 | 8.278 | 8.308
Morven | 996/1 | 132 | TransGrid 132kV Line 996 Tee | Morven 132/66kV STS | 45 | 7.337 | 7.4226 | 7.5308 | 7.6323 | 7.7601 | 86 | 7.7102 | 7.7723 | 7.8219 | 7.8722 | 7.9223
Morven | 83M/3 | 66 | Morven 132/66kV STS | Culcairn ZS | 15 | 3.7916 | 3.7978 | 3.7954 | 3.8018 | 3.8079 | 25 | 4.439 | 4.465 | 4.495 | 4.515 | 4.5466
Morven | 83M/4 | 66 | Morven 132/66kV STS | Holbrook ZS | 15 | 3.4449 | 3.4511 | 3.4502 | 3.4541 | 3.4526 | 25 | 3.3125 | 3.3143 | 3.3117 | 3.3187 | 3.3239
Munyang | 56 | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 2.4998 | 2.5309 | 2.55 | 2.5788 | 2.6027 | 23 | 15.7128 | 15.7548 | 15.7837 | 15.7864 | 15.8301
Munyang | 57A | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.74088 | 0.75167 | 0.7711 | 0.78383 | 0.79296 | 23 | 5.4942 | 5.5228 | 5.5552 | 5.5887 | 5.6302
Munyang | 57B | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.49392 | 0.50111 | 0.51406 | 0.52255 | 0.52864 | 23 | 3.6628 | 3.6819 | 3.7035 | 3.7258 | 3.7535
Munyang | No.1 Perisher | 33 | TransGrid Munyang 132/33kV STS | Smiggin Sw Stn | 38 | 2.4998 | 2.5309 | 2.55 | 2.5788 | 2.6027 | 41 | 15.7128 | 15.7548 | 15.7837 | 15.7864 | 15.8301
Munyang | No.2 Perisher | 33 | TransGrid Munyang 132/33kV STS | Blue Cow Tee | 38 | 1.7328 | 1.7449 | 1.7748 | 1.8113 | 1.822 | 49 | 14.4137 | 14.446 | 14.5018 | 14.5522 | 14.6169
Munyang | No.2 Perisher | 33 | Blue Cow Tee | Smiggin Sw Stn | 38 | 1.2348 | 1.2528 | 1.2852 | 1.3064 | 1.3216 | 49 | 9.157 | 9.2047 | 9.2587 | 9.3145 | 9.3836
Munyang | 60/2 | 33 | Bullocks Portal ZS | Bullocks Flat ZS | 19 | 2.1873 | 2.2145 | 2.2313 | 2.2565 | 2.2774 | 23 | 15.7128 | 15.7548 | 15.7837 | 15.7864 | 15.8301
Munyang | 58 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.70711 | 0.70711 | 0.70711 | 0.70711 | 0.70711 | 14 | 14.1421 | 14.1421 | 14.1421 | 14.1421 | 14.1421
Munyang | 59 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 1.515 | 1.5292 | 1.5441 | 1.5575 | 1.5711 | 14 | 6.815 | 6.8149 | 6.811 | 6.797 | 6.7984
Munyang | Bullocks Portal Line | 33 | Perisher ZS | Bullocks Portal ZS | 20 | 2.4998 | 2.5309 | 2.55 | 2.5788 | 2.6027 | 23 | 15.7128 | 15.7548 | 15.7837 | 15.7864 | 15.8301
Queanbeyan | 97Y | 132 | TransGrid Williamsdale 330/132kV STS | Googong Town ZS | 91 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 975 | 132 | TransGrid Queanbeyan 132/66kV STS | Googong Town ZS | 41 | 8.0895 | 8.3332 | 8.5764 | 8.8236 | 9.0722 | 79 | 12.5084 | 13.0848 | 13.6507 | 14.2092 | 14.8108
Queanbeyan | 82A | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 12.9672 | 13.0776 | 10.0314 | 10.1807 | 10.358 | 37 | 16.772 | 13.599 | 13.6936 | 13.806 | 13.8862
Queanbeyan | 82B | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 9.7254 | 9.8082 | 7.5236 | 7.6355 | 7.7685 | 37 | 12.579 | 10.1992 | 10.2702 | 10.3545 | 10.4147
Queanbeyan | 82F | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 49 | 12.9012 | 12.8812 | 12.4011 | 12.3893 | 12.3966 | 49 | 19.1784 | 18.8406 | 18.8704 | 18.9582 | 19.0276
Queanbeyan | 82G | 66 | TransGrid Queanbeyan 132/66kV STS | Captains Flat ZS | 12 | 6.5353 | 6.8671 | 7.2046 | 7.5567 | 7.9155 | 19 | 8.0708 | 8.4399 | 8.8475 | 9.1596 | 9.5553
Queanbeyan | 82K/1 | 66 | TransGrid Queanbeyan 132/66kV STS | Sutton / Bungendore Tee | 28 | 11.9273 | 11.9519 | 12.058 | 12.1089 | 12.1589 | 34 | 15.3197 | 15.6129 | 15.9261 | 16.2289 | 16.5195
Queanbeyan | 82K/1 | 66 | Sutton / Bungendore Tee | Bungendore ZS | 28 | 8.1545 | 8.1508 | 8.2496 | 8.2837 | 8.3247 | 34 | 10.1109 | 10.2462 | 10.3869 | 10.5217 | 10.6635
Queanbeyan | 82K/3 | 66 | Sutton / Bungendore Tee | Sutton ZS | 28 | 3.7839 | 3.8143 | 3.8241 | 3.8433 | 3.8554 | 34 | 5.2135 | 5.3721 | 5.5454 | 5.7144 | 5.8642
Queanbeyan | 82M | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 830:QSH | 66 | Queanbeyan South ZS | Googong Dam ZS | 15 | 0.95098 | 0.95935 | 0.96563 | 0.96447 | 0.96905 | 25 | 1.1439 | 1.1364 | 1.1443 | 1.1456 | 1.1416
Steeple Flat | 97C | 132 | Steeple Flat 132/66kV STS | Boco Rock Wind Farm | 140 | 114.8496 | 114.933 | 114.8266 | 115.0834 | 114.9268 | 157 | 109.4424 | 109.1783 | 109.7019 | 109.2541 | 108.896
Steeple Flat | 97R | 132 | Steeple Flat 132/66kV STS | Bega 132/66kV STS | 140 | 16.3634 | 16.3517 | 16.3337 | 16.3851 | 16.3268 | 157 | 23.5195 | 23.5883 | 23.6485 | 23.5299 | 23.6545
Steeple Flat | 810/3 | 66 | Steeple Flat 132/66kV STS | Brown Mountain Hydro | 70 | 4.3946 | 4.3929 | 4.3934 | 4.3918 | 4.3961 | 78 | 4.6983 | 4.6984 | 4.7096 | 4.7176 | 4.7053
Steeple Flat | 810/4 | 66 | Steeple Flat 132/66kV STS | Bombala ZS | 21 | 4.2645 | 4.2688 | 4.2794 | 4.2808 | 4.2907 | 25 | 4.9979 | 5.0418 | 5.1002 | 5.1457 | 5.2015
Steeple Flat | S839 | 66 | Brown Mountain Hydro | Quira ZS | 70 | 1.2095 | 1.2015 | 1.2004 | 1.2021 | 1.1933 | 78 | 1.5628 | 1.5646 | 1.5637 | 1.5581 | 1.5565
Temora | 901 | 132 | Temora 132/66 STS | Wyalong Switching Station | 108 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0
Temora | 9JW | 132 | Wyalong Switching Station | West Wyalong Switching Station | 108 | 72.4547 | 72.4547 | 72.4547 | 72.4547 | 72.4547 | 135 | 72.4547 | 72.4547 | 72.4547 | 72.4547 | 72.4547
Temora | 9JX | 132 | West Wyalong Switching Station | Lake Cowal | 108 | 35.6414 | 35.6809 | 35.7429 | 35.6827 | 35.69 | 135 | 37.3555 | 37.3625 | 37.4267 | 37.5155 | 37.5747
Temora | 4 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Temora | 5 | 66 | Temora 132/66 STS | Ariah Park Tee | 21 | 11.4983 | 11.7171 | 12.7117 | 12.9527 | 13.2503 | 25 | 12.0573 | 12.4384 | 13.7479 | 14.1733 | 14.5353
Temora | 6 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 7.1433 | 7.1233 | 7.1035 | 7.1006 | 7.1193 | 25 | 6.9086 | 6.9896 | 7.0715 | 7.1577 | 7.2463
Temora | 20-60 | 66 | Ariah Park Tee | West Wyalong ZS | 21 | 9.5819 | 9.7642 | 10.5931 | 10.7939 | 11.042 | 25 | 10.0478 | 10.3653 | 11.4566 | 11.811 | 12.1128
Temora | 60-70 | 66 | West Wyalong ZS | Anona ZS | 7 | 1.3057 | 1.3216 | 1.34 | 1.3561 | 1.3732 | 12 | 1.1616 | 1.1651 | 1.1734 | 1.1776 | 1.184
Temora | 80-140 | 66 | Ariah Park Tee | Ariah Park ZS | 15 | 1.9164 | 1.9528 | 2.1186 | 2.1588 | 2.2084 | 25 | 2.0096 | 2.0731 | 2.2913 | 2.3622 | 2.4226
Temora | 80-140 | 66 | Ariah Park ZS | Ardlethan ZS | 11 | 0.77769 | 0.77929 | 0.78008 | 0.77963 | 0.78212 | 19 | 0.7021 | 0.70912 | 0.7162 | 0.72212 | 0.72916
Temora | 835/J | 66 | Junee Reefs ZS | Junee ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Temora | 835/T | 66 | Temora 132/66 STS | Junee Reefs ZS | 12 | 0.19266 | 0.1946 | 0.19726 | 0.20035 | 0.20503 | 18 | 0.21219 | 0.21392 | 0.2157 | 0.21772 | 0.22007
Tumut | 827 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 13.0185 | 12.8395 | 12.7253 | 12.707 | 12.6699 | 34 | 13.7855 | 13.8603 | 13.8454 | 13.8879 | 13.9034
Tumut | 828 | 66 | TransGrid Tumut 132/66kV STS | Gundagai South ZS | 11 | 7.0965 | 7.0745 | 7.0752 | 7.0813 | 7.0746 | 19 | 6.6477 | 6.7179 | 6.7866 | 6.8507 | 6.9221
Tumut | 829 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Tumut | 831 | 66 | Gundagai South ZS | Nangus ZS | 11 | 1.1672 | 1.1557 | 1.1463 | 1.1402 | 1.1328 | 19 | 0.92173 | 0.9308 | 0.94068 | 0.94664 | 0.96137
Tumut | 848 | 66 | Adelong Tee | Adelong ZS | 12 | 1.3686 | 1.3633 | 1.3717 | 1.3632 | 1.3668 | 19 | 1.3029 | 1.3049 | 1.3057 | 1.309 | 1.3105
Tumut | 830/2:GUN | 66 | Gundagai South ZS | Parsons Creek ZS | 11 | 0.22056 | 0.21969 | 0.21849 | 0.21717 | 0.21575 | 19 | 0.2186 | 0.21775 | 0.21683 | 0.21574 | 0.21519
Tumut | 848/1 | 66 | Adelong Tee | Batlow ZS | 21 | 8.7745 | 8.7768 | 8.7787 | 8.7937 | 8.8071 | 25 | 10.0804 | 10.074 | 10.0774 | 10.0825 | 10.0733
Tumut | 848/2 | 66 | Batlow ZS | Tumbarumba ZS | 22 | 7.6416 | 7.6468 | 7.6567 | 7.6723 | 7.6887 | 26 | 8.5177 | 8.5151 | 8.517 | 8.5231 | 8.5104
Tumut | 848/3 | 66 | TransGrid Tumut 132/66kV STS | Adelong Tee | 21 | 9.8694 | 9.8674 | 9.8759 | 9.8838 | 9.8997 | 25 | 11.1227 | 11.1178 | 11.1214 | 11.1284 | 11.1197
Tumut | 850:TAL | 66 | TransGrid Tumut 132/66kV STS | Talbingo ZS | 18 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 22 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 19.6576
Wagga (Copland St) | 83L | 66 | Hammond Ave ZS | Bomen ZS | 54 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Uranquinty ZS | 28 | 7.9058 | 7.9277 | 7.9563 | 7.9954 | 8.0287 | 34 | 7.2238 | 7.2952 | 7.3584 | 7.4226 | 7.4968
Wagga (Copland St) | 840/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bulgary ZS | 15 | 3.438 | 3.4422 | 3.4455 | 3.4509 | 3.4659 | 25 | 3.0972 | 3.1037 | 3.1049 | 3.1101 | 3.1114
Wagga (Copland St) | 840/2 | 66 | Bulgary ZS | Lockhart ZS | 15 | 3.2809 | 3.2846 | 3.287 | 3.2935 | 3.3089 | 24 | 2.9708 | 2.9771 | 2.9788 | 2.9848 | 2.9869
Wagga (Copland St) | 840/3 | 66 | Lockhart Tee | Kywong ZS | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M/1 | 66 | Uranquinty ZS | Henty ZS | 15 | 2.3613 | 2.3722 | 2.3857 | 2.3999 | 2.4276 | 25 | 2.2921 | 2.2923 | 2.2957 | 2.2919 | 2.2952
Wagga (Copland St) | 83M/2 | 66 | Henty ZS | Culcairn ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8W9 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Ashmont ZS | 34 | 26.4265 | 26.4411 | 26.3271 | 26.2687 | 26.2172 | 39 | 24.9393 | 25.1182 | 25.3004 | 25.448 | 25.6469
Wagga (Copland St) | 8WF/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bourkelands ZS | 34 | 11.8751 | 11.949 | 12.0497 | 12.1143 | 12.1962 | 39 | 10.9627 | 11.0648 | 11.1873 | 11.2829 | 11.3938
Wagga (Copland St) | 8WM | 66 | Hammond Ave ZS | Morrow St ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WO | 66 | Ashmont ZS | Bourkelands ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WP | 66 | Morrow St ZS | Cartwrights Hill ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WR | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 7.4396 | 7.4758 | 7.4534 | 7.4452 | 7.4509 | 60 | 8.0029 | 8.1656 | 8.3062 | 8.4549 | 8.6112
Wagga (Copland St) | 8WT | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 7.0104 | 7.0445 | 7.0234 | 7.0157 | 7.0211 | 60 | 7.5412 | 7.6945 | 7.827 | 7.9671 | 8.1144
Wagga (Copland St) | 8WG | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Kooringal ZS | 34 | 17.2985 | 17.5401 | 17.7853 | 18.0867 | 18.2599 | 39 | 15.7671 | 15.8415 | 15.9127 | 15.949 | 15.9993
Wagga (Copland St) | 8WF/2 | 66 | Bourkelands ZS | Kooringal ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga North | 99U | 132 | TransGrid Wagga North 132/66kV STS | Sebastopol Sw Stn | 128 | 106.066 | 106.066 | 106.066 | 106.066 | 106.066 | 143 | 108.6116 | 108.6116 | 108.6116 | 108.6116 | 108.6116
Wagga North | 9J6 | 132 | Sebastopol Sw Stn | Temora 132/66 STS | 128 | 29.0573 | 29.1627 | 30.391 | 30.4991 | 30.6769 | 143 | 30.1313 | 30.6039 | 32.2761 | 32.8275 | 33.2939
Wagga North | 9J5/1 | 132 | TransGrid Wagga North 132/66kV STS | Junee 132/66/11kV ZS | 140 | 36.982 | 37.1162 | 38.6795 | 38.817 | 39.0433 | 157 | 39.9415 | 40.5679 | 42.7846 | 43.5156 | 44.1337
Wagga North | 9J5/2 | 132 | Junee 132/66/11kV ZS | Temora 132/66 STS | 140 | 27.422 | 27.5207 | 28.8866 | 28.9944 | 29.1697 | 157 | 26.7773 | 27.2643 | 29.0179 | 29.5892 | 30.068
Wagga North | 30-90 | 66 | Junee ZS | Coolamon ZS | 6 | 4.96 | 4.9626 | 4.9622 | 4.9759 | 4.9625 | 9 | 4.5621 | 4.6097 | 4.6414 | 4.6824 | 4.7183
Wagga North | 834:JUN | 66 | Junee ZS | Bethungra ZS | 11 | 1.0596 | 1.0553 | 1.0508 | 1.046 | 1.0404 | 19 | 1.0213 | 1.0234 | 1.0251 | 1.0261 | 1.0287
Wagga North | 83C | 66 | TransGrid Wagga North 132/66kV STS | Oura ZS | 24 | 3.7845 | 3.7769 | 3.7675 | 3.771 | 3.7681 | 28 | 3.3704 | 3.3835 | 3.4011 | 3.4199 | 3.4349
Wagga North | 83C | 66 | Oura ZS | Forest Hill ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga North | 83G | 66 | TransGrid Wagga North 132/66kV STS | Bomen ZS | 34 | 17.62 | 17.7479 | 17.8634 | 21.1356 | 26.5933 | 39 | 16.673 | 16.8984 | 20.2988 | 25.8458 | 40.5831
Wagga North | 83J | 66 | Bomen ZS | Cartwrights Hill ZS | 34 | 8.7214 | 8.8638 | 9.0035 | 9.1467 | 9.307 | 39 | 8.5335 | 8.7736 | 9.0542 | 9.3065 | 9.5955
Wagga North | 850:BET | 66 | Bethungra ZS | Cootamundra ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Wagga North | CHI2527 | 33 | Cartwrights Hill ZS | Euberta ZS | 4 | 1.7695 | 1.7593 | 1.7411 | 1.7364 | 1.7293 | 6 | 1.3759 | 1.3815 | 1.3765 | 1.3742 | 1.3739
Wagga North | CHI2527 | 33 | Euberta ZS | Ganmurra ZS | 4 | 0.53935 | 0.52993 | 0.51805 | 0.50959 | 0.49913 | 6 | 0.50488 | 0.50739 | 0.50581 | 0.50409 | 0.5034
Wagga North | Mates Gully | 33 | Oura ZS | Mates Gully ZS | 3 | 1.622 | 1.6104 | 1.6006 | 1.5884 | 1.5854 | 6 | 1.506 | 1.5025 | 1.5015 | 1.4964 | 1.4935
Wagga North | Mates Gully | 33 | Mates Gully ZS | Tarcutta ZS | 4 | 1.0447 | 1.0416 | 1.0397 | 1.0351 | 1.0368 | 7 | 1.0138 | 1.0165 | 1.0195 | 1.0211 | 1.0244
Wagga North | 8WJ | 66 | TransGrid Wagga North 132/66kV STS | Forest Hill ZS | 34 | 5.1788 | 5.1361 | 5.1323 | 5.1104 | 5.1002 | 39 | 5.1429 | 5.1282 | 5.1141 | 5.0975 | 5.1131
Yanco | 840/4 | 66 | Narrandra ZS | Kywong ZS | 16 | 0.42433 | 0.4304 | 0.43702 | 0.44427 | 0.45123 | 25 | 0.3045 | 0.3115 | 0.31641 | 0.31931 | 0.32404
Yanco | 841:YNC | 66 | TransGrid Yanco 132/33/66kV STS | Narrandera ZS | 15 | 10.1922 | 10.2686 | 10.2899 | 10.3641 | 10.4373 | 25 | 8.4053 | 8.5421 | 8.6365 | 8.7772 | 8.913
Yanco | 7L3 | 33 | TransGrid Yanco 132/33/66kV STS | Cudgel ZS | 8 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 13 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Yanco | 7L6 | 33 | TransGrid Yanco 132/33/66kV STS | Whitton / Murrami Tee | 15 | 6.6755 | 6.6273 | 6.5675 | 6.5464 | 6.4822 | 18 | 5.2861 | 5.3136 | 5.3168 | 5.3218 | 5.3274
Yanco | 7L6 | 33 | Whitton / Murrami Tee | Whitton ZS | 8 | 4.0116 | 3.9924 | 3.9559 | 3.9614 | 3.9384 | 13 | 2.6121 | 2.6245 | 2.6083 | 2.6044 | 2.5916
Yanco | 7L6 | 33 | Whitton / Murrami Tee | Murrami ZS | 8 | 1.4314 | 1.4314 | 1.4367 | 1.4415 | 1.4393 | 13 | 1.3593 | 1.3897 | 1.4218 | 1.4466 | 1.4813
Yanco | 7L5 | 33 | TransGrid Yanco 132/33/66kV STS | Yanco ZS | 8 | 11.5112 | 11.4824 | 11.49 | 11.4842 | 11.4729 | 13 | 9.0214 | 9.0573 | 9.098 | 9.1404 | 9.1818
Yanco | 7L5 | 33 | Yanco ZS | Leeton ZS | 6 | 8.9867 | 8.9571 | 8.956 | 8.9447 | 8.9257 | 9 | 7.9041 | 7.8911 | 7.8846 | 7.8776 | 7.8736
Yanco | 7L4 | 33 | TransGrid Yanco 132/33/66kV STS | Leeton ZS | 31 | 9.7356 | 9.7035 | 9.7024 | 9.6901 | 9.6695 | 34 | 8.2335 | 8.2199 | 8.2131 | 8.2059 | 8.2016
Yass | 971(1) | 132 | TransGrid Yass 330/132/66kV STS | Cullerin Range Wind Farm | 106 | 75.9504 | 75.9048 | 75.9595 | 76.1098 | 76.1416 | 119 | 78.8268 | 78.6799 | 78.8868 | 78.9293 | 78.8604
Yass | 971(2) | 132 | Cullerin Range Wind Farm | Gunning Wind Farm | 140 | 48.3761 | 48.2899 | 48.3071 | 48.424 | 48.3929 | 157 | 49.4709 | 49.4284 | 49.5775 | 49.6211 | 49.5383
Yass | 971(3) | 132 | Cullerin Range Wind Farm | Goulburn 132/66/33kV STS | 106 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0
Yass | 976/2 (M) | 132 | TransGrid 132kV Line 976/2(Y) / Murrumbateman Tee | Murrumbateman ZS | 42 | 6.1175 | 6.1216 | 6.1259 | 6.1751 | 6.1889 | 82 | 7.404 | 7.5369 | 7.6757 | 7.823 | 7.9586
Yass | 824 | 66 | TransGrid Yass 330/132/66kV STS | Yass ZS | 12 | 13.4553 | 13.5441 | 13.5848 | 13.6784 | 13.7793 | 18 | 16.246 | 16.3942 | 16.5186 | 16.6294 | 16.7716
Yass | 823/5 | 66 | Yass ZS | Marilba ZS | 12 | 1.4017 | 1.4008 | 1.4152 | 1.4217 | 1.431 | 18 | 1.5993 | 1.626 | 1.6444 | 1.6679 | 1.6932

## BSP
Connection Point | Forecast PF | Summer Forecast (MVA) |  |  |  |  | Forecast PF | Winter Forecast (MVA) |  |  |  |  | Major Embedded Generation (MW)
|  | 23/24 | 24/25 | 25/26 | 26/27 | 27/28 |  | 2024 | 2025 | 2026 | 2027 | 2028
Albury (Corowa) | 0.98834 | 14.6685 | 14.5939 | 14.6056 | 14.5961 | 14.6271 | 0.99719 | 13.0566 | 13.0694 | 13.1241 | 13.1234 | 13.14 | 30
Albury (Mulwala) | 0.98886 | 13.02 | 13.0494 | 13.0537 | 13.0584 | 13.0921 | 0.99664 | 10.7105 | 10.8012 | 10.9029 | 10.9944 | 11.1017 | 0
Albury (Union Rd + Jelbart) | 0.99483 | 87.062 | 87.5953 | 88.3337 | 89.0069 | 89.6698 | 0.99504 | 80.7091 | 81.543 | 82.4755 | 83.4575 | 84.454 | 0
Armidale | 0.98791 | 29.6774 | 29.8825 | 30.0541 | 30.224 | 30.4633 | 0.9981 | 42.7055 | 42.9644 | 43.1481 | 43.1877 | 43.4138 | 10
Balranald | 0.99934 | 3.8266 | 3.8375 | 3.8466 | 3.8516 | 3.8684 | 0.97553 | 2.7431 | 2.7551 | 2.7569 | 2.7677 | 2.7808 | 0
Beryl | 0.97484 | 78.3395 | 78.7207 | 79.0262 | 79.0787 | 79.4872 | 0.97296 | 84.0663 | 84.0174 | 84.3926 | 84.1218 | 84.2951 | 87
Boambee South | 0.99503 | 17.1334 | 17.2019 | 17.2872 | 17.3866 | 17.4561 | 0.99284 | 17.8701 | 18.1173 | 18.3288 | 18.6088 | 18.8025 | 0
Broken Hill 22kV | 0.98991 | 39.5119 | 40.9273 | 42.3549 | 42.3414 | 42.208 | 0.99861 | 36.6913 | 38.1481 | 39.6458 | 39.6773 | 39.728 | 50
Casino | 0.97084 | 27.9041 | 28.1275 | 28.1968 | 28.4402 | 28.5775 | 0.99059 | 23.6842 | 23.8712 | 24.0302 | 24.2265 | 24.3701 | 0
Coffs Harbour | 0.94752 | 61.8567 | 62.0668 | 65.6679 | 65.8793 | 66.0307 | 0.99622 | 62.0973 | 62.9586 | 67.2351 | 68.1117 | 68.9669 | 0
Coleambally | 0.96694 | 12.169 | 12.2595 | 12.3083 | 12.3831 | 12.4587 | 0.95418 | 9.7633 | 9.8363 | 9.9387 | 9.9731 | 10.0804 | 5
Cooma 132kV | 0.89944 | 35.7365 | 35.6981 | 35.6963 | 35.7853 | 35.6664 | 0.93073 | 52.1411 | 52.2782 | 52.4514 | 52.2094 | 52.4376 | 118
Cooma 66kV | 0.99671 | 14.0697 | 14.0818 | 14.0527 | 14.1272 | 14.1228 | 0.98448 | 23.6828 | 23.7644 | 23.8188 | 23.7673 | 23.9221 | 1.1
Cowra | 0.98357 | 30.023 | 30.6231 | 31.2865 | 32.03 | 32.503 | 0.99499 | 26.9037 | 27.1795 | 27.4357 | 27.7322 | 28.0082 | 22.5
Darlington Point | 0.90114 | 23.5605 | 23.7856 | 24.0194 | 24.1623 | 24.4261 | 0.93892 | 22.898 | 23.556 | 24.2737 | 24.9504 | 25.8265 | 85
Deniliquin | 0.98755 | 47.0097 | 47.4045 | 47.6505 | 48.059 | 48.417 | 0.99262 | 38.1024 | 38.6136 | 38.8356 | 39.1674 | 39.5533 | 0
Dorrigo | 0.98291 | 2.4444 | 2.4281 | 2.4101 | 2.4021 | 2.3975 | 0.99124 | 2.7235 | 2.7183 | 2.7178 | 2.7196 | 2.7176 | 0
Dunoon | 0.98427 | 6.4977 | 6.5536 | 6.6075 | 6.7012 | 6.7378 | 0.99111 | 6.9176 | 6.9902 | 7.074 | 7.1574 | 7.2348 | 0
Evans Lane | 0.99627 | 39.2314 | 39.3932 | 39.4073 | 39.5033 | 39.6863 | 0.99943 | 53.8676 | 54.0185 | 54.1427 | 54.4682 | 54.6658 | 0
Finley 132kV | 0.99233 | 92.4011 | 92.6956 | 92.4251 | 92.3816 | 93.6087 | 0.98798 | 97.5063 | 98.0954 | 97.7637 | 97.385 | 97.8226 | 0
Finley 66kV | 0.99363 | 15.1606 | 15.1465 | 15.1567 | 15.1653 | 15.2026 | 0.99027 | 14.5122 | 14.9927 | 15.4805 | 15.9423 | 16.4637 | 2.5
Forbes | 0.99182 | 31.6888 | 31.8137 | 31.6771 | 31.7174 | 31.6123 | 0.99566 | 25.2121 | 25.2775 | 25.3043 | 25.3482 | 25.394 | 54.1
Glen Innes | 0.95678 | 11.1632 | 11.229 | 11.2457 | 11.2881 | 11.3515 | 0.98729 | 14.5809 | 14.7998 | 15.0416 | 15.257 | 15.5234 | 5.5
Griffith | 0.99851 | 92.8921 | 92.9778 | 92.8904 | 92.883 | 92.9015 | 0.9947 | 62.3045 | 63.6722 | 65.0756 | 66.3258 | 67.6113 | 0
Gunnedah 66kV | 0.97375 | 23.4518 | 23.4078 | 23.3315 | 23.2872 | 23.2606 | 0.97977 | 25.4217 | 25.6999 | 26.0108 | 26.3157 | 26.5931 | 7
Hawks Nest | 0.99478 | 8.5788 | 8.6525 | 8.6626 | 8.746 | 8.749 | 0.99682 | 8.4231 | 8.5138 | 8.6074 | 8.7156 | 8.8147 | 0
Herons Ck | 0.98968 | 12.1345 | 12.16 | 12.1748 | 12.2122 | 12.2742 | 0.99722 | 11.679 | 11.94 | 12.1963 | 12.4977 | 12.7711 | 0
Inverell | 0.97063 | 34.4086 | 34.9871 | 35.5919 | 36.2042 | 36.8195 | 0.9809 | 39.2457 | 39.7334 | 40.6361 | 41.3788 | 41.8283 | 22.5
Kempsey 33kV | 0.993 | 29.8876 | 30.2396 | 30.7074 | 31.1734 | 31.5628 | 0.99857 | 31.1582 | 31.656 | 32.0844 | 32.6066 | 33.0636 | 0
Koolkhan | 0.97267 | 54.1205 | 54.4668 | 54.8954 | 55.4729 | 55.916 | 0.97952 | 46.3501 | 46.5725 | 46.8517 | 47.1095 | 47.4193 | 0
Lismore 132kV | 0.99278 | 85.73 | 85.3742 | 85.5344 | 85.791 | 86.045 | 0.99145 | 66.3434 | 66.3973 | 66.5392 | 66.6582 | 66.7279 | 37.5
Macksville | 0.99755 | 9.0435 | 9.0949 | 9.1947 | 9.2495 | 9.3224 | 0.99845 | 9.6444 | 9.6834 | 9.7382 | 9.7798 | 9.8351 | 0
Manildra | 0.95011 | 10.2532 | 10.2603 | 10.2766 | 10.3056 | 10.2978 | 0.96421 | 9.9857 | 9.9852 | 9.9891 | 9.9799 | 9.9814 | 48.5
Marulan | 0.98944 | 51.0368 | 52.4401 | 53.8447 | 55.3967 | 56.8572 | 0.98801 | 61.5764 | 63.8914 | 66.5239 | 68.9404 | 71.4035 | 118
Merbein | 0.9211 | 11.4716 | 11.3275 | 11.2096 | 11.1712 | 11.176 | 0.991 | 9.7114 | 9.6948 | 9.7837 | 9.8245 | 9.8698 | 0
Mildura | 0.95165 | 21.5388 | 22.0239 | 22.7355 | 23.0606 | 23.5728 | 0.99643 | 17.0039 | 17.2232 | 17.1717 | 17.2815 | 17.3662 | 3.3
Molong | 0.95249 | 4.9452 | 4.9689 | 5.0382 | 5.0588 | 5.1472 | 0.91254 | 5.6998 | 5.891 | 6.0704 | 6.2481 | 6.4144 | 30
Moree | 0.99659 | 26.821 | 27.1392 | 27.5169 | 27.8253 | 28.1354 | 0.99627 | 36.212 | 36.8066 | 37.0639 | 37.4846 | 37.8038 | 67
Morven | 0.995 | 7.3554 | 7.4444 | 7.5503 | 7.6483 | 7.7806 | 0.99605 | 7.7386 | 7.8028 | 7.8521 | 7.8977 | 7.9523 | 0
Mudgee | 0.98996 | 23.7377 | 23.7205 | 23.9093 | 23.9348 | 23.8677 | 0.997 | 24.2356 | 24.6711 | 25.0426 | 25.4586 | 25.8653 | 0
Mullumbimby | 0.99624 | 52.998 | 54.5799 | 56.0726 | 57.4566 | 58.8539 | 0.99853 | 62.7294 | 63.5768 | 64.4472 | 65.2153 | 66.2275 | 0
Munyang | 0.9248 | 3.7337 | 3.7458 | 3.7707 | 3.7876 | 3.8015 | 0.94652 | 29.8002 | 30.0572 | 30.1496 | 30.3318 | 30.593 | 0
Murrumbateman | 0.99011 | 6.142 | 6.1547 | 6.1564 | 6.2058 | 6.2251 | 0.99955 | 7.4053 | 7.5384 | 7.6781 | 7.8263 | 7.9617 | 0
Murrumburrah | 0.99381 | 35.4758 | 35.3816 | 37.1296 | 37.0715 | 37.1146 | 0.99756 | 39.8359 | 39.7711 | 41.4935 | 41.4975 | 41.6344 | 0
Nambucca | 0.98649 | 7.1115 | 7.1696 | 7.2454 | 7.3059 | 7.3764 | 0.99403 | 8.64 | 8.6873 | 8.7443 | 8.8073 | 8.8567 | 0
Narrabri | 0.98353 | 37.1324 | 37.1561 | 37.1825 | 37.2226 | 37.1684 | 0.9864 | 43.9358 | 43.8272 | 43.9613 | 44.1149 | 44.2691 | 16
Orange 132kV | 0.99088 | 171.6958 | 201.6214 | 224.1485 | 224.3103 | 231.9199 | 0.99158 | 199.7741 | 204.9205 | 221.9583 | 222.1358 | 229.9007 | 0
Orange 66kV | 0.95307 | 52.8572 | 53.1972 | 53.5058 | 53.6498 | 53.8771 | 0.95831 | 67.3943 | 67.968 | 68.7332 | 69.1118 | 69.712 | 0
Panorama | 0.99521 | 69.4088 | 69.5085 | 69.6264 | 69.6087 | 69.51 | 0.98945 | 76.7409 | 77.4897 | 78.2411 | 79.157 | 79.8767 | 10
Parkes 132kV | 0.97961 | 33.9709 | 40.2707 | 89.7046 | 94.2462 | 98.7236 | 0.98017 | 34.9296 | 41.239 | 90.7079 | 95.2326 | 99.786 | 0
Parkes 66kV | 0.96573 | 27.8669 | 27.9367 | 27.9204 | 27.9175 | 28.0018 | 0.98611 | 30.3748 | 30.9771 | 31.5877 | 32.2839 | 32.902 | 10
Port Macquarie | 0.99375 | 69.6795 | 70.0228 | 70.0859 | 73.2135 | 77.2892 | 0.99558 | 80.1906 | 80.9733 | 81.7008 | 85.3691 | 89.8972 | 0
Queanbeyan 132kV | 0.94247 | 8.8507 | 9.1631 | 9.5144 | 9.7904 | 10.149 | 0.98343 | 10.7948 | 11.4169 | 11.9719 | 12.6428 | 13.1876 | 0
Queanbeyan 66kV | 0.9963 | 52.5829 | 52.7822 | 58.4382 | 64.0633 | 69.45 | 0.99735 | 68.9338 | 75.0662 | 81.5169 | 87.8908 | 94.0724 | 0
Raleigh | 0.98597 | 9.4061 | 9.3874 | 9.3929 | 9.3876 | 9.3911 | 0.9983 | 11.1222 | 11.3176 | 11.4901 | 11.6705 | 11.8492 | 0
Robinvale | 0.97761 | 6.1993 | 6.2626 | 6.3264 | 6.3742 | 6.4367 | 0.97404 | 3.086 | 3.0812 | 3.0907 | 3.0909 | 3.0833 | 0
Snowy Adit | 0.96143 | 4.0691 | 4.0698 | 4.0997 | 4.0935 | 4.0499 | 0.99067 | 7.5953 | 7.7974 | 8.079 | 8.2957 | 8.5665 | 0
Stroud | 0.98082 | 37.7943 | 37.925 | 38.1428 | 38.3483 | 38.5394 | 0.99507 | 40.4992 | 40.8536 | 41.2535 | 41.7482 | 42.1978 | 0
Tamworth | 0.99201 | 111.9101 | 111.8747 | 111.7023 | 111.248 | 111.1659 | 0.99636 | 103.5713 | 104.9797 | 106.2007 | 107.8433 | 108.9979 | 0
Taree 33kV | 0.98616 | 31.1891 | 31.2142 | 31.2297 | 31.2528 | 31.2796 | 0.98556 | 26.6817 | 26.9372 | 27.2156 | 27.5126 | 27.722 | 0
Taree 66kV | 0.99656 | 48.8257 | 48.8991 | 49.4409 | 49.5867 | 49.8457 | 0.99723 | 57.0369 | 57.5865 | 58.142 | 58.7636 | 59.2056 | 0
Tenterfield | 0.98214 | 4.2759 | 4.2952 | 4.3338 | 4.3438 | 4.3692 | 0.99528 | 5.6654 | 5.7196 | 5.7748 | 5.8281 | 5.8928 | 0
Terranora | 0.9945 | 114.7322 | 116.4335 | 118.296 | 119.4589 | 121.4803 | 0.99916 | 92.9977 | 93.9038 | 94.7568 | 95.7317 | 96.7357 | 30
Tumut | 0.94725 | 30.7176 | 30.7174 | 30.7998 | 30.9014 | 30.9236 | 0.97717 | 32.0897 | 32.1302 | 32.1598 | 32.2075 | 32.3565 | 14
Upper Tumut | 0.99382 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 1.1117 | 0.99973 | 2.0192 | 2.0192 | 2.0192 | 2.0192 | 2.0192 | 0
Wagga 66kV | 0.9923 | 76.8094 | 76.8542 | 76.8151 | 77.1273 | 76.6345 | 0.99847 | 77.7339 | 77.9719 | 77.9517 | 78.1725 | 78.2249 | 0
Wagga North 132kV | 0.97792 | 66.3739 | 66.6158 | 69.3731 | 69.6455 | 70.0477 | 0.99066 | 70.1036 | 71.1954 | 75.0633 | 76.3578 | 77.4728 | 263
Wagga North 66kV | 0.9848 | 21.8773 | 21.7254 | 21.883 | 25.3437 | 31.0859 | 0.99382 | 23.8266 | 24.0263 | 27.7307 | 33.703 | 49.9281 | 0
Waggamba | 0.99358 | 19.3351 | 19.3818 | 19.3715 | 19.3701 | 19.3993 | 0.99821 | 23.836 | 23.8842 | 23.9294 | 23.9327 | 23.9567 | 0
Wallerawang 132kV | 0.85692 | 35.5489 | 36.1987 | 36.9747 | 37.8198 | 38.6633 | 0.8683 | 36.4204 | 37.124 | 37.9581 | 38.6556 | 39.4533 | 0
Wallerawang 66kV | 0.99763 | 5.2476 | 5.3332 | 5.4018 | 5.4913 | 5.5702 | 0.98744 | 6.2326 | 6.2796 | 6.3239 | 6.3688 | 6.4217 | 0
Wellington 132kV | 0.99703 | 168.2216 | 168.6331 | 191.9453 | 215.4263 | 216.3555 | 0.99798 | 161.5748 | 183.9354 | 206.6769 | 206.9159 | 207.1621 | 256.3
Yanco | 0.96525 | 41.5633 | 41.6733 | 41.7886 | 41.82 | 41.9811 | 0.9829 | 34.6536 | 34.6953 | 34.7057 | 34.7726 | 34.7768 | 10
Yass 132kV | 0.88899 | 48.7407 | 49.5007 | 49.8814 | 50.6482 | 50.9721 | 0.98859 | 38.6655 | 39.3898 | 40.4845 | 41.1627 | 42.0749 | 76.5
Yass 66kV | 0.97749 | 13.8075 | 13.9081 | 14.1385 | 14.2643 | 14.4227 | 0.9881 | 16.456 | 16.8391 | 17.2044 | 17.6723 | 18.0538 | 0

## ZS Export
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 23/24 | 24/25 | 25/26 | 26/27 | 27/28
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 33 | -0.99862 | 8.3347 | 8.891 | 9.4146 | 9.9105 | 10.3828 | 13.0061 | 44
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 33 | -0.68861 | 8.0203 | 8.5653 | 9.0776 | 9.5624 | 10.0239 | 12.2954 | 50
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 16.5 | -0.9989 | 8.718 | 9.3132 | 9.8727 | 10.402 | 10.9057 | 13.5074 | 43
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | -0.9196 | 10.1056 | 10.7774 | 11.4097 | 12.0087 | 12.5793 | 18.9371 | 35
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 220 | 0.72548 | 27.3888 | 27.3888 | 27.3888 | 27.3888 | 27.3888 | 0 | 647
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 33 | -0.99385 | 6.0845 | 6.5767 | 7.0345 | 7.4643 | 7.8707 | 8.204 | 26
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 27.5 | 0.99759 | 2.6367 | 2.8239 | 2.9994 | 3.1652 | 3.3228 | 3.9968 | 22
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 33 | -0.99958 | 8.2546 | 8.8022 | 9.3177 | 9.8061 | 10.2714 | 12.5318 | 28
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 22 | -0.98812 | 7.4563 | 7.9602 | 8.434 | 8.8825 | 9.3095 | 12.2065 | 34
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 33 | -0.73636 | 14.5957 | 15.6875 | 16.708 | 17.6697 | 18.5817 | 22.5388 | 41
Lismore | Ballina 132kV | 132/66 | 75/112 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lismore | Dunoon | 132/11 | 10 | 10 |  | 11 | -0.94009 | 3.4196 | 3.6611 | 3.8877 | 4.1018 | 4.3052 | 6.2776 | 24
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.82238 | 7.6423 | 8.1569 | 8.641 | 9.0993 | 9.5357 | 14.42 | 16
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 11 | 0.33441 | 2.9838 | 3.1675 | 3.341 | 3.506 | 3.6636 | 5.7633 | 27
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 17.6 | -0.95325 | 3.7152 | 3.95 | 4.1715 | 4.3819 | 4.5827 | 6.2778 | 17
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 264 | 0.87415 | 29.712 | 29.712 | 29.712 | 29.712 | 29.712 | 0 | 24
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 25.3 | -0.98893 | 8.2469 | 8.8644 | 9.4416 | 9.9855 | 10.5012 | 12.7913 | 29
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 52.8 | -0.87756 | 4.7197 | 5.0101 | 5.2847 | 5.5456 | 5.7948 | 0 | 17
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 33 | 0.95044 | 5.9544 | 6.3969 | 6.8108 | 7.2009 | 7.5709 | 12.2673 | 35
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 11 | -0.98966 | 4.9273 | 5.2875 | 5.6248 | 5.9429 | 6.2448 | 9.1451 | 25
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | -0.99228 | 5.6905 | 6.1051 | 6.4933 | 6.8595 | 7.2072 | 10.1454 | 26
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 11 | -0.79262 | 3.7303 | 3.9917 | 4.2369 | 4.4687 | 4.689 | 5.9561 | 25
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 2.75 | 0 | 0.32609 | 0.34318 | 0.35947 | 0.37504 | 0.39 | 0.7542 | 16
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 33 | -0.63281 | 8.8177 | 9.429 | 10.0031 | 10.5459 | 11.0622 | 14.647 | 33
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 3.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.96048 | 0.32999 | 0.34901 | 0.36705 | 0.38424 | 0.40069 | 0.6948 | 26
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 5.5 | -0.77781 | 0.28029 | 0.29653 | 0.31193 | 0.3266 | 0.34064 | 0.48025 | 25
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.80731 | 0.29439 | 0.31495 | 0.33425 | 0.35249 | 0.36984 | 0.5622 | 19
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 27.5 | -0.58612 | 5.9306 | 6.3394 | 6.7233 | 7.0865 | 7.432 | 9.4489 | 28
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 26.95 | -0.86319 | 6.1639 | 6.5286 | 6.8741 | 7.2029 | 7.5174 | 10.5735 | 16
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | -0.50882 | 1.5576 | 1.6774 | 1.7892 | 1.8944 | 1.9941 | 2.0852 | 23
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.076696 | 5.8774 | 6.2843 | 6.6664 | 7.0278 | 7.3715 | 8.9575 | 42
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.66 | 0.95 | 0.13725 | 0.14432 | 0.15106 | 0.15751 | 0.1637 | 0.2795 | 10
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.55 | 0.79444 | 0.13758 | 0.14738 | 0.15657 | 0.16525 | 0.1735 | 0.2306 | 13
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | -0.96425 | 0.39836 | 0.42108 | 0.44264 | 0.4632 | 0.48288 | 0.99187 | 14
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 25.3 | -0.925 | 6.2256 | 6.7077 | 7.1573 | 7.5803 | 7.9809 | 8.7522 | 39
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 33 | 1 | 4.9284 | 5.3154 | 5.6761 | 6.0152 | 6.3361 | 7.1941 | 24
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 50.6 | 0.97718 | 9.0951 | 9.885 | 10.6162 | 11.3002 | 11.9451 | 13.0245 | 27
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 33 | 0.92349 | 5.5227 | 6.0276 | 6.4933 | 6.9278 | 7.3366 | 8.6443 | 47
Coffs Harbour | Dorrigo | 66/11, 132/11 | 7.5/10 | 10 |  | 11 | 0.45429 | 1.1101 | 1.1788 | 1.2437 | 1.3054 | 1.3643 | 1.9091 | 26
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 17.6 | -0.99879 | 4.6576 | 5.0487 | 5.4116 | 5.7517 | 6.0728 | 6.1738 | 40
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 6.875 | 0.95 | 1.35 | 1.4315 | 1.5086 | 1.582 | 1.6521 | 2.4421 | 17
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 26.95 | -0.38075 | 4.6784 | 5.1272 | 5.5397 | 5.9236 | 6.284 | 6.1675 | 36
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.24333 | 0.32234 | 0.35749 | 0.38948 | 0.41903 | 0.44664 | 0.3738 | 10
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 33 | -0.97918 | 8.0546 | 8.7459 | 9.3865 | 9.986 | 10.5516 | 10.7102 | 38
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 33 | -0.99827 | 5.3447 | 5.7939 | 6.2107 | 6.6013 | 6.97 | 8.0251 | 28
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 25.3 | -0.78994 | 4.1992 | 4.5431 | 4.8627 | 5.1626 | 5.446 | 6.1774 | 29
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 33 | -0.88775 | 5.1751 | 5.5652 | 5.9297 | 6.2731 | 6.5986 | 8.6323 | 14
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.4 | -0.99975 | 0.79904 | 0.86455 | 0.92544 | 0.98257 | 1.0365 | 1.3291 | 37
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.3 | -0.78534 | 0.58105 | 0.61942 | 0.65556 | 0.6898 | 0.72242 | 1.2006 | 33
Kempsey | North St | 33/11 | 10 | 16 |  | 11 | 0.90209 | 3.6038 | 3.8516 | 4.0843 | 4.3045 | 4.514 | 6.1199 | 40
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 16.5 | -0.63802 | 3.1679 | 3.4331 | 3.6792 | 3.9098 | 4.1276 | 5.0632 | 14
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 5.5 | 0.81717 | 1.2813 | 1.3864 | 1.4841 | 1.5758 | 1.6624 | 2.1242 | 34
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 13.75 | -0.78457 | 4.2285 | 4.6653 | 5.0646 | 5.4346 | 5.781 | 5.0239 | 58
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 33 | 1 | 6.9166 | 7.4385 | 7.9261 | 8.3854 | 8.8209 | 10.8993 | 10
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.24993 | 0.45735 | 0.48009 | 0.50181 | 0.52263 | 0.54265 | 1.0349 | 14
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 33 | -0.99371 | 14.9027 | 16.4246 | 17.8169 | 19.108 | 20.3173 | 18.5356 | 56
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 3.85 | 0.99745 | 1.1579 | 1.2489 | 1.3336 | 1.4133 | 1.4887 | 2.0199 | 33
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 8.8 | 0.98792 | 4.6922 | 5.1088 | 5.4939 | 5.8537 | 6.1927 | 5.9601 | 28
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 22 | 0.97532 | 3.6544 | 3.9638 | 4.2507 | 4.5195 | 4.7731 | 5.0149 | 56
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 16.5 | 0 | 5.7222 | 6.1852 | 6.6159 | 7.0202 | 7.4024 | 9.3872 | 32
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.4 | -0.69459 | 0.83005 | 0.89293 | 0.95166 | 1.007 | 1.0594 | 1.5279 | 18
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | -0.78891 | 0.2961 | 0.30961 | 0.32255 | 0.335 | 0.34699 | 0.7455 | 13
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.4 | 0.31804 | 1.7245 | 1.8529 | 1.973 | 2.0862 | 2.1935 | 2.8619 | 16
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 22 | -0.99563 | 4.2873 | 4.6032 | 4.8988 | 5.1776 | 5.442 | 6.8964 | 21
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 7.7 | -0.99912 | 3.8024 | 4.1503 | 4.4713 | 4.7707 | 5.0524 | 5.4396 | 51
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 5.5 | 0.86393 | 0.70039 | 0.7483 | 0.79332 | 0.83592 | 0.87646 | 1.3564 | 9
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.15 | -0.89703 | 1.1676 | 1.2357 | 1.3001 | 1.3616 | 1.4204 | 2.0884 | 27
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.95912 | 6.6292 | 7.2491 | 7.8201 | 8.3522 | 8.8523 | 9.2662 | 26
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 17.6 | -0.78977 | 5.1287 | 5.6084 | 6.0502 | 6.4619 | 6.8488 | 6.7641 | 38
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 6.875 | -0.99533 | 2.7407 | 2.9694 | 3.1818 | 3.3808 | 3.5687 | 3.481 | 58
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 27.5 | -0.24254 | 3.972 | 4.2599 | 4.5296 | 4.7841 | 5.0257 | 6.3045 | 19
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 17.6 | 0.99996 | 2.5116 | 2.7245 | 2.922 | 3.1069 | 3.2815 | 3.4698 | 39
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 22 | 0.97823 | 4.9388 | 5.3183 | 5.6725 | 6.0059 | 6.3217 | 7.4333 | 13
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 11 | 0.44649 | 3.6754 | 3.9836 | 4.2697 | 4.5377 | 4.7908 | 5.5829 | 24
Stroud | Booral | 33/11 | 3 | 2.5 |  | 2.75 | 0.95 | 0.46863 | 0.49661 | 0.5231 | 0.54831 | 0.57241 | 1.0648 | 11
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.27196 | 1.196 | 1.2696 | 1.3391 | 1.4052 | 1.4683 | 2.1467 | 10
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.89351 | 2.4016 | 2.5759 | 2.7391 | 2.8931 | 3.0393 | 4.0945 | 24
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.72852 | 3.1489 | 3.3959 | 3.6261 | 3.8425 | 4.0474 | 4.7219 | 21
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.15 | -0.21801 | 0.72479 | 0.77703 | 0.82597 | 0.87217 | 0.91605 | 1.3169 | 22
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 8.8 | -0.85166 | 1.1619 | 1.2346 | 1.3032 | 1.3684 | 1.4306 | 2.1099 | 32
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.034812 | 1.5071 | 1.6242 | 1.7335 | 1.8362 | 1.9335 | 2.6233 | 19
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 66 | 0.95757 | 0.19082 | 0.19082 | 0.19082 | 0.19082 | 0.19082 | 0.0046 | 1360
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 5.5 | 0.98724 | 0.91897 | 0.97228 | 1.0228 | 1.071 | 1.1171 | 1.6438 | 17
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.918 | 3.836 | 4.1053 | 4.358 | 4.5968 | 4.8238 | 5.3491 | 16
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply | [5 empty] | -0.99118 | 3.9773 | 4.1687 | 4.35 | 4.5226 | 4.6876 | 2.0992 | 22
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 2.75 | 0.94897 | 0.87583 | 0.92777 | 0.97696 | 1.0238 | 1.0686 | 1.4551 | 28
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 13.75 | -0.91397 | 4.4001 | 4.7367 | 5.0509 | 5.3467 | 5.6269 | 6.7566 | 21
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.22949 | 0.11265 | 0.12103 | 0.12886 | 0.13624 | 0.14324 | 0.1922 | 10
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 13.75 | -0.91191 | 3.5823 | 3.8942 | 4.183 | 4.4531 | 4.7077 | 4.6702 | 22
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.9892 | 2.9667 | 3.181 | 3.3817 | 3.5712 | 3.7512 | 4.6055 | 20
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 3.85 | 0.95 | 0.089506 | 0.093859 | 0.098019 | 0.10201 | 0.10585 | 0.1464 | 9
Armidale | Uralla | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 1.6842 | 1.8153 | 1.9375 | 2.0525 | 2.1614 | 2.6505 | 11
Armidale | Walcha South 66/22kV | 66/22 | 8 | 3 |  | 3.3 | 0.86374 | 0.35187 | 0.36028 | 0.3685 | 0.37654 | 0.38442 | 0.7496 | 18
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.3 | 0.26479 | 0.54638 | 0.58429 | 0.61989 | 0.65355 | 0.68556 | 0.83565 | 24
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.95 | 0.52428 | 0.55442 | 0.583 | 0.61024 | 0.63631 | 0.9686 | 27
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | -0.51362 | 0.067981 | 0.070698 | 0.073314 | 0.075841 | 0.078285 | 0.1286 | 6
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 22 | -0.19612 | 3.1131 | 3.3074 | 3.4908 | 3.6651 | 3.8314 | 5.706 | 24
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 5.5 | 0.48793 | 1.6155 | 1.7158 | 1.8105 | 1.9004 | 1.9864 | 2.6854 | 25
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0126
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.95 | 0.29169 | 0.30521 | 0.31815 | 0.33059 | 0.34257 | 0.6892 | 22
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.3 | -0.63372 | 0.86534 | 0.92164 | 0.9747 | 1.025 | 1.073 | 1.671 | 27
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 33 | -0.67607 | 6.6408 | 7.0097 | 7.3602 | 7.6947 | 8.0152 | 11.9755 | 22
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | -0.11684 | 0.32806 | 0.34874 | 0.36825 | 0.38678 | 0.40446 | 0.6509 | 29
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.65 | 0.95 | 0.0053341 | 0.0056159 | 0.0058842 | 0.0061409 | 0.0063872 | 0 | 75
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 5.5 | 0.95 | 0.50881 | 0.528 | 0.54651 | 0.56442 | 0.58178 | 1.2147 | 21
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 5.5 | 0 | 0.13562 | 0.13864 | 0.1416 | 0.14449 | 0.14733 | 0.2811 | 2
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | -0.17256 | 0.044506 | 0.046193 | 0.04782 | 0.049393 | 0.050918 | 0.1188 | 9
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.4 | -0.13298 | 1.053 | 1.1105 | 1.1652 | 1.2175 | 1.2676 | 2.0892 | 17
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.95 | 0.29392 | 0.30258 | 0.311 | 0.3192 | 0.32719 | 0.8643 | 16
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 16.5 | -0.97325 | 8.8458 | 8.9862 | 9.1209 | 9.2504 | 9.3754 | 5.3587 | 14
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.944 | 0.53806 | 0.54928 | 0.56027 | 0.57106 | 0.58164 | 2.3685 | 13
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.98157 | 0.16793 | 0.17039 | 0.17281 | 0.17519 | 0.17755 | 0.4279 | 10
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 2.75 | 0.74366 | 0.15241 | 0.15429 | 0.15614 | 0.15797 | 0.15978 | 0.5026 | 14
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 33 | -0.17888 | 5.7619 | 6.0522 | 6.3292 | 6.5945 | 6.8496 | 12.2256 | 27
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.95 | 0.37227 | 0.3905 | 0.40792 | 0.42463 | 0.4407 | 1.0272 | 14
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.95 | 0.10231 | 0.10384 | 0.10534 | 0.10682 | 0.10828 | 0.2327 | 2
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | -0.95029 | 5.0209 | 5.0211 | 5.0212 | 5.0213 | 5.0214 | 0.0456 | 1760
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.39307 | 0.34083 | 0.36521 | 0.38805 | 0.40962 | 0.43012 | 1.1385 | 3
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 5.5 | 1 | 0.23093 | 0.23789 | 0.24465 | 0.25122 | 0.25763 | 0.6226 | 4
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 5.5 | -0.83205 | 1.1611 | 1.2865 | 1.4006 | 1.5062 | 1.6048 | 2.2111 | 42
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0 | 0.25659 | 0.27603 | 0.29419 | 0.31129 | 0.3275 | 0.59358 | 10
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.76822 | 3.8584 | 4.0363 | 4.2066 | 4.3703 | 4.5281 | 7.9882 | 20
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 11 | 0.011235 | 1.1977 | 1.2799 | 1.3572 | 1.4303 | 1.4998 | 2.5107 | 19
Narrabri | Wee Waa | 66/22 | 10 | 16 |  | 11 | 0.93248 | 1.0976 | 1.1566 | 1.2126 | 1.2662 | 1.3177 | 2.6556 | 28
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.15 | 0.70711 | 0.60435 | 0.63272 | 0.65987 | 0.68595 | 0.71107 | 1.3567 | 10
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.91141 | 6.4162 | 6.9739 | 7.4902 | 7.9731 | 8.4284 | 9.4065 | 28
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027
Tamworth | Attunga | 66/11 | 5 | 8 |  | 5.5 | 0.95 | 0.87974 | 0.92463 | 0.96745 | 1.0084 | 1.0478 | 1.2213 | 2
Tamworth | Barraba | 66/11 | 5 | 5 |  | 5.5 | 0.99752 | 0.76181 | 0.81338 | 0.86186 | 0.90776 | 0.95145 | 1.5665 | 24
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.1 | 0.91261 | 0.27479 | 0.2912 | 0.30673 | 0.32151 | 0.33564 | 0.4782 | 23
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.2 | 0.87287 | 0.019655 | 0.020548 | 0.021404 | 0.022226 | 0.02302 | 0.0795 | 3
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.65 | 0.67146 | 0.12943 | 0.13541 | 0.14114 | 0.14665 | 0.15195 | 0.3286 | 20
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.95 | 0.22541 | 0.23199 | 0.23839 | 0.24461 | 0.25069 | 0.4739 | 27
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 33 | 0.92452 | 1.8807 | 2.0381 | 2.1842 | 2.3212 | 2.4505 | 2.6697 | 13
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 17.6 | -0.24254 | 2.196 | 2.3464 | 2.4878 | 2.6216 | 2.7488 | 3.5458 | 16
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.9 | 1.1919 | 1.2678 | 1.3395 | 1.4075 | 1.4723 | 2.0197 | 23
Tamworth | Murrurundi | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.68189 | 0.898 | 0.96417 | 1.0261 | 1.0845 | 1.1398 | 1.3808 | 15
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 2.75 | 0.59927 | 0.45199 | 0.47134 | 0.48992 | 0.50782 | 0.52512 | 0.91465 | 20
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 33 | 0 | 6.5492 | 7.0914 | 7.5951 | 8.0673 | 8.5134 | 8.9196 | 8
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.95719 | 1.5362 | 1.6337 | 1.7258 | 1.8131 | 1.8965 | 2.5589 | 12
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.97881 | 0.056565 | 0.058517 | 0.060406 | 0.062238 | 0.064017 | 0.1576 | 9
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 50.6 | 0.99234 | 5.9605 | 6.4123 | 6.8343 | 7.2317 | 7.6084 | 8.8689 | 7
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 33 | 0.98478 | 7.1614 | 7.7353 | 8.2695 | 8.7713 | 9.2458 | 10.7096 | 19
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.86847 | 0.039125 | 0.04107 | 0.042927 | 0.044707 | 0.046419 | 0.1016 | 13
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 6.875 | 0.95 | 0.62641 | 0.66712 | 0.70549 | 0.74188 | 0.77656 | 1.0287 | 5
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 14.3 | -0.29914 | 2.229 | 2.3412 | 2.4482 | 2.5507 | 2.6492 | 5.447 | 15
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 11 | -0.52918 | 1.8958 | 2.002 | 2.1028 | 2.199 | 2.2912 | 3.3866 | 26
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | -0.91037 | 1.1327 | 1.2303 | 1.3207 | 1.4053 | 1.4851 | 1.7292 | 5
Beryl | Mudgee | 66/22, 132/22 | 18/30 | 30 |  | 33 | 0.28121 | 8.1449 | 8.7783 | 9.369 | 9.9245 | 10.4506 | 13.7005 | 18
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 2.75 | 0 | 0.82639 | 0.87429 | 0.9197 | 0.96298 | 1.0044 | 1.3496 | 13
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 2.75 | 0.95 | 0.38483 | 0.42531 | 0.46226 | 0.49647 | 0.52847 | 0.52139 | 15
Wellington | Wellington 11kV | 132/11, 66/11 | 10 | 15 |  | 11 | 0.87432 | 2.442 | 2.6667 | 2.874 | 3.0672 | 3.249 | 4.303 | 7
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 11 | -0.44693 | 1.5158 | 1.6107 | 1.7003 | 1.7855 | 1.8668 | 3.0315 | 12
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 33 | 0.93834 | 3.038 | 3.2482 | 3.4456 | 3.6324 | 3.81 | 4.9032 | 7
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 33 | -0.97929 | 15.1325 | 15.8318 | 16.4801 | 17.0872 | 17.6601 | 11.4656 | 1250
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 25.3 | -0.97908 | 5.9575 | 6.4001 | 6.8141 | 7.2043 | 7.5744 | 9.1961 | 36
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 33 | -0.62403 | 7.6827 | 8.2216 | 8.7273 | 9.2053 | 9.6597 | 12.8055 | 17
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | -0.29562 | 0.41999 | 0.44706 | 0.47259 | 0.4968 | 0.51988 | 0.84383 | 28
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 13.2 | -0.82195 | 1.9524 | 2.0725 | 2.1861 | 2.294 | 2.3971 | 3.8779 | 15
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.95 | 0.41906 | 0.44406 | 0.46772 | 0.49025 | 0.51178 | 0.9057 | 36
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 26.4 | -0.99725 | 9.5314 | 9.7194 | 9.8979 | 10.0681 | 10.2312 | 6.6888 | 565
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 11 | -0.063109 | 1.3955 | 1.4733 | 1.5473 | 1.6178 | 1.6854 | 2.9493 | 19
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 27.5 | 0.89755 | 0.93162 | 0.99022 | 1.0455 | 1.0981 | 1.1482 | 1.7417 | 7
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.37139 | 0.80858 | 0.84053 | 0.87131 | 0.90104 | 0.92982 | 2.2559 | 2
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.39248 | 0.22283 | 0.22672 | 0.23054 | 0.23431 | 0.23801 | 0.6548 | 48
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.1 | 0 | 0.020482 | 0.021438 | 0.022353 | 0.023233 | 0.02408 | 0.0426 | 23
Nyngan | Cobar CSA | 132/11 | 15/18 | 30/45 |  | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Town | 66/22 | 8/11 | 10/13 |  | 12.1 | 0.95 | 2.2866 | 2.4485 | 2.6003 | 2.7437 | 2.88 | 3.8283 | 20
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 11 | -0.20362 | 1.632 | 1.7054 | 1.7758 | 1.8435 | 1.9088 | 2.2354 | 13
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply | [5 empty] | -0.95792 | 49.6735 | 51.8533 | 53.8797 | 55.7812 | 57.5783 | 18.7411 | 1
Broken Hill | Wilcannia 33kV | [5 empty] | -0.077023 | 0.11438 | 0.11528 | 0.11617 | 0.11705 | 0.11793 | 0.2973 | 8
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 5.5 | -0.97624 | 0.50073 | 0.54133 | 0.5791 | 0.61454 | 0.64805 | 0.8644 | 4
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.65 | 0.17044 | 0.20779 | 0.21073 | 0.21363 | 0.21649 | 0.21932 | 0.6556 | 7
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.65 | 0.70711 | 0.12094 | 0.13081 | 0.13999 | 0.14861 | 0.15675 | 0.204 | 16
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | -0.81373 | 0.27487 | 0.31549 | 0.35144 | 0.38404 | 0.41408 | 0.1145 | 14
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.4 | 0.006252 | 0.11264 | 0.11287 | 0.11309 | 0.11331 | 0.11353 | 0.1932 | 30
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 3.85 | -0.53845 | 0.24343 | 0.27092 | 0.29586 | 0.31887 | 0.34032 | 0.5009 | 12
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 11 | -0.99854 | 6.8169 | 7.3794 | 7.902 | 8.3922 | 8.8552 | 8.3632 | 58
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 33 | 0.94 | 4.2749 | 4.6757 | 5.0448 | 5.3886 | 5.7118 | 5.9488 | 33
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 33 | 0.55632 | 7.7543 | 8.5332 | 9.2466 | 9.9088 | 10.5295 | 9.5786 | 25
Orange | Orange West | 66/11 | 30 | 30 |  | 33 | -0.9965 | 7.0705 | 7.6924 | 8.2677 | 8.8055 | 9.3123 | 8.7468 | 19
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 2.75 | 0 | 0.44026 | 0.45875 | 0.47653 | 0.49366 | 0.51022 | 1.1495 | 23
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 26.4 | -0.75319 | 0.81482 | 0.84827 | 0.88045 | 0.9115 | 0.94153 | 1.7197 | 28
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.4 | 0.97115 | 1.1866 | 1.2837 | 1.3739 | 1.4585 | 1.5385 | 2.0182 | 12
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 22 | 0.90599 | 2.6551 | 2.8914 | 3.1098 | 3.3138 | 3.5059 | 3.8296 | 25
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 2.75 | -0.97958 | 0.82463 | 0.87796 | 0.92823 | 0.97592 | 1.0214 | 1.4182 | 24
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 33 | 0.80166 | 8.2687 | 9.0163 | 9.7065 | 10.3507 | 10.9572 | 9.6868 | 30
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 66 | 0 | 4.1574 | 4.5605 | 4.9308 | 5.2751 | 5.5983 | 8.0582 | 18
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 22 | -0.98915 | 7.5439 | 8.2204 | 8.8454 | 9.429 | 9.9785 | 10.7693 | 30
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 49.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 16.5 | 0.87261 | 1.7966 | 1.9254 | 2.0462 | 2.1602 | 2.2685 | 2.8956 | 39
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 33 | -0.98567 | 6.2984 | 6.7116 | 7.1008 | 7.4698 | 7.8213 | 9.9435 | 7
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 11 | -0.99571 | 5.1011 | 5.1478 | 5.1918 | 5.2337 | 5.2736 | 1.2628 | 1547
Parkes | Trundle | 66/22 | 8 | 5 |  | 5.5 | 0.99 | 5.0953 | 5.1431 | 5.1888 | 5.2327 | 5.275 | 1.92 | 1712
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 11 | 0.75657 | 1.7503 | 1.8185 | 1.8842 | 1.9477 | 2.0092 | 3.7778 | 21
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 33 | 0.44721 | 3.5446 | 3.7932 | 4.0265 | 4.247 | 4.4566 | 6.8347 | 33
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 7.7 | 0.62405 | 1.1091 | 1.1491 | 1.1877 | 1.2251 | 1.2614 | 2.5896 | 17
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 5.5 | 0.95 | 0.52098 | 0.55193 | 0.58123 | 0.60912 | 0.63579 | 1.0442 | 18
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.4 | 0.8732 | 0.33328 | 0.36023 | 0.38529 | 0.40882 | 0.43107 | 0.4008 | 8
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.76822 | 7.5084 | 8.1605 | 8.7643 | 9.3291 | 9.8616 | 10.228 | 24
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.3 | -0.91531 | 0.69363 | 0.74482 | 0.79271 | 0.83787 | 0.88071 | 0.9812 | 10
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.70711 | 3.1311 | 3.3962 | 3.642 | 3.8723 | 4.0896 | 4.538 | 12
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 13.75 | -0.99966 | 4.6483 | 5.108 | 5.5297 | 5.9214 | 6.2887 | 5.3181 | 20
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 13.75 | -0.58321 | 2.9466 | 3.2075 | 3.4487 | 3.6741 | 3.8864 | 4.4811 | 15
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | -0.9844 | 1.617 | 1.7735 | 1.9172 | 2.0508 | 2.1763 | 1.9698 | 20
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 5.5 | -0.83222 | 0.40131 | 0.4307 | 0.4582 | 0.48415 | 0.50877 | 0.5827 | 47
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 22 | 0.92199 | 3.3239 | 3.5295 | 3.7237 | 3.9084 | 4.0846 | 5.4267 | 44
Cooma | Eucumbene | 66/11 | 0.6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0556
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 33 | 0 | 1.871 | 2.0381 | 2.1924 | 2.3366 | 2.4724 | 2.8324 | 41
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0 | 0.17509 | 0.19654 | 0.21586 | 0.2336 | 0.25008 | 0.1494 | 5
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 11 | -0.99135 | 1.5875 | 1.7387 | 1.8777 | 2.0072 | 2.1288 | 1.885 | 23
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.65158 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 0.99136 | 0.036618 | 0.041258 | 0.045427 | 0.049244 | 0.052786 | 0.1388 | 9
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 0 | 0.058312 | 0.066103 | 0.073069 | 0.079426 | 0.08531 | 0 | 20
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 11 | 0.95 | 0.087547 | 0.098492 | 0.10834 | 0.11736 | 0.12574 | 0.0698 | 7
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0.8576 | 1.1046 | 1.1046 | 1.1046 | 1.1046 | 1.1046 | 0 | 982
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.98276 | 0.056933 | 0.06454 | 0.071341 | 0.077548 | 0.083293 | 0.0302 | 5
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Bermagui | 33/11 | 5 | 5 |  | 5.5 | -0.96228 | 1.6441 | 1.7937 | 1.9317 | 2.0605 | 2.1817 | 2.2342 | 15
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0 | 0.30645 | 0.34079 | 0.37198 | 0.40075 | 0.42759 | 0.4297 | 17
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 2.75 | -0.98948 | 0.92725 | 0.99649 | 1.0612 | 1.1222 | 1.1801 | 1.5723 | 65
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.89359 | 1.43 | 1.5261 | 1.6165 | 1.7022 | 1.7837 | 2.4547 | 11
Bega | Edrom | 66/11 | 5 | 5 |  | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.89443 | 4.3778 | 4.6883 | 4.9795 | 5.2546 | 5.5159 | 7.2377 | 11
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 17.6 | 0.11043 | 5.3382 | 5.7918 | 6.2125 | 6.6064 | 6.9781 | 9.0965 | 34
Bega | Quira | 66/11 | 5 |  |  | 0 | -0.054645 | 0.53247 | 0.58226 | 0.62811 | 0.67084 | 0.711 | 0.84258 | 14
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 14.3 | 0.90645 | 0.74711 | 0.80978 | 0.86794 | 0.92244 | 0.97389 | 1.2676 | 26
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | -0.57106 | 4.6005 | 4.6005 | 4.6005 | 4.6005 | 4.6005 | 0 | 608
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.64018 | 0.18539 | 0.19893 | 0.2116 | 0.22356 | 0.23491 | 0.364 | 21
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 2.75 | -0.98894 | 0.65634 | 0.69341 | 0.72859 | 0.76215 | 0.79429 | 1.1938 | 12
Tumut | Batlow | 66/11 | 5 | 5 |  | 5.5 | 0.24254 | 0.66776 | 0.71226 | 0.75413 | 0.7938 | 0.83158 | 1.0949 | 28
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 8.8 | 0.98058 | 1.3826 | 1.4619 | 1.537 | 1.6087 | 1.6772 | 2.9837 | 25
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.1 | -0.98172 | 0.33217 | 0.3619 | 0.38936 | 0.41501 | 0.43916 | 0.4682 | 11
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.81373 | 0.030305 | 0.030501 | 0.030696 | 0.03089 | 0.031082 | 0.0692 | 5
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | -0.88858 | 0.23561 | 0.24924 | 0.26216 | 0.27447 | 0.28626 | 0.3241 | 26
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 8.8 | 1 | 1.4906 | 1.56 | 1.6265 | 1.6903 | 1.7519 | 2.6564 | 6
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 33 | 0.8779 | 3.207 | 3.4274 | 3.6345 | 3.8304 | 4.0168 | 5.6464 | 10
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0 | 4.2616 | 4.6022 | 4.9192 | 5.2171 | 5.4988 | 6.723 | 37
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 5.5 | 0.86938 | 1.7218 | 1.8576 | 1.9842 | 2.1031 | 2.2157 | 2.4958 | 36
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 11 | 0.70711 | 0.472 | 0.472 | 0.472 | 0.472 | 0.472 | 0 | 406
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 33 | 0 | 7.9558 | 8.8011 | 9.572 | 10.2853 | 10.9522 | 8.2182 | 28
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 33 | 0.98619 | 5.0225 | 5.4666 | 5.8772 | 6.2609 | 6.6224 | 6.3858 | 13
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 33 | -0.98333 | 11.133 | 12.1806 | 13.145 | 14.0432 | 14.8874 | 13.1815 | 21
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 8.8 | 0.99 | 2.0784 | 2.2187 | 2.3506 | 2.4755 | 2.5944 | 3.5049 | 21
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 2.75 | -0.48269 | 1.1923 | 1.2797 | 1.3615 | 1.4386 | 1.5118 | 1.8459 | 21
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 20.9 | 0.98407 | 4.7627 | 5.1661 | 5.5402 | 5.8906 | 6.2212 | 5.6599 | 14
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0.819 | 1.8101 | 1.9138 | 2.0122 | 2.106 | 2.1958 | 3.386 | 7
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 33 | 0.87819 | 2.2973 | 2.473 | 2.637 | 2.7914 | 2.9377 | 2.9038 | 17
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.99879 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 0 | 115
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 16.5 | 0 | 4.5965 | 4.9481 | 5.2763 | 5.5853 | 5.8781 | 0 | 17
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 16.5 | 0.99402 | 1.5759 | 1.7088 | 1.832 | 1.9474 | 2.0564 | 2.2553 | 5
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.96754 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 15.4 | 0.97863 | 7.2669 | 7.3346 | 7.3972 | 7.4557 | 7.5108 | 1.189 | 8212
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | -0.92968 | 0.80198 | 0.84205 | 0.8803 | 0.91696 | 0.9522 | 1.2267 | 3
Cowra | Canowindra | 66/11 | 5 | 8 |  | 5.5 | -0.85434 | 2.0103 | 2.1944 | 2.3641 | 2.5225 | 2.6715 | 3.2063 | 14
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 33 | 0.48043 | 5.3435 | 5.7876 | 6.2001 | 6.5867 | 6.9519 | 9.2977 | 24
Cowra | Grenfell | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 2.1125 | 2.2873 | 2.4497 | 2.602 | 2.7458 | 3.3739 | 50
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.016391 | 0.25375 | 0.26286 | 0.27166 | 0.28019 | 0.28846 | 0.5819 | 27
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 5.5 | -0.8693 | 1.2033 | 1.2649 | 1.3236 | 1.3799 | 1.434 | 2.5076 | 14
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 20.9 | -0.96152 | 3.7391 | 4.0611 | 4.3595 | 4.6386 | 4.9019 | 5.8833 | 14
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.15 | 0.96649 | 0.16169 | 0.16845 | 0.17495 | 0.18121 | 0.18727 | 0.3501 | 11
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 11 | -0.50488 | 1.724 | 1.8555 | 1.9783 | 2.0939 | 2.2035 | 3.095 | 6
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 33 | 0.1644 | 4.764 | 5.0867 | 5.3902 | 5.6775 | 5.951 | 8.0122 | 21
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 2.75 | 0.98638 | 0.48243 | 0.51382 | 0.54339 | 0.57143 | 0.59817 | 0.9836 | 28
Yass | Marilba | 66/11 | 3 | 1 |  | 1.1 | 0.99244 | 0.54887 | 0.5833 | 0.6158 | 0.64667 | 0.67613 | 0.92545 | 14
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | -0.98108 | 4.0067 | 4.3246 | 4.6206 | 4.8988 | 5.162 | 6.1681 | 26
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 14.3 | -0.95242 | 4.9117 | 5.2364 | 5.5422 | 5.832 | 6.108 | 6.7919 | 13
Temora | Anona | 66/22 | 3 |  |  | 0 | -0.12201 | 0.33589 | 0.35519 | 0.37349 | 0.39094 | 0.40764 | 0.81 | 3
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 2.75 | -0.85749 | 0.27374 | 0.29393 | 0.31283 | 0.33064 | 0.34754 | 0.4511 | 36
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.3 | -0.97855 | 0.30609 | 0.3293 | 0.35098 | 0.37139 | 0.39074 | 0.6039 | 47
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | -0.99796 | 0.11928 | 0.12014 | 0.121 | 0.12185 | 0.1227 | 0.1564 | 11
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 11 | -0.97308 | 2.7598 | 2.9565 | 3.1409 | 3.3151 | 3.4805 | 4.7146 | 21
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 11 | 0.69905 | 2.41 | 2.5446 | 2.6723 | 2.7943 | 2.9111 | 4.2703 | 26
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.3 | 0.99788 | 0.12323 | 0.13111 | 0.13854 | 0.1456 | 0.15233 | 0.25365 | 11
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 33 | 0.96511 | 0.1706 | 0.17096 | 0.17132 | 0.17168 | 0.17204 | 0.27455 | 13
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/10 | 6.75/10 |  | 11 | -0.98402 | 3.0307 | 3.3316 | 3.6075 | 3.8637 | 4.104 | 3.5028 | 29
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 8.8 | -0.86924 | 1.5563 | 1.6645 | 1.766 | 1.862 | 1.9533 | 3.0297 | 29
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.3 | 0.80531 | 0.2439 | 0.255 | 0.26564 | 0.27587 | 0.28574 | 0.5303 | 9
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 15.4 | 0.97927 | 1.3569 | 1.4717 | 1.5782 | 1.6779 | 1.772 | 1.8593 | 11
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | -0.75974 | 0.14176 | 0.15222 | 0.16202 | 0.17125 | 0.18001 | 0.1817 | 5
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 16.5 | 0.27472 | 1.7142 | 1.8264 | 1.9322 | 2.0325 | 2.128 | 3.2049 | 13
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | -0.9961 | 29.9786 | 29.9786 | 29.9786 | 29.9786 | 29.9786 | 0 | 290
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.91358 | 0.17016 | 0.179 | 0.18742 | 0.19548 | 0.20323 | 0.3704 | 22
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 7.59 | 0.91914 | 0.20993 | 0.22401 | 0.23725 | 0.24979 | 0.26172 | 0.4615 | 22
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.1 | 0.9 | 0.29012 | 0.30344 | 0.3162 | 0.32846 | 0.34028 | 0.6279 | 10
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 33 | 0.69253 | 5.2978 | 5.8443 | 6.3439 | 6.8069 | 7.2404 | 8.025 | 18
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 14.63 | -0.99995 | 5.1223 | 5.6144 | 6.0668 | 6.4877 | 6.8828 | 7.3278 | 25
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 33 | 0.91767 | 1.7037 | 1.8079 | 1.9065 | 2.0002 | 2.0897 | 3.6557 | 13
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 5.5 | -0.95963 | 0.75302 | 0.78815 | 0.82178 | 0.85409 | 0.88521 | 1.6428 | 20
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 27.5 | -0.96393 | 6.0179 | 6.5597 | 7.06 | 7.5271 | 7.9669 | 9.1291 | 23
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 5.5 | -0.62733 | 0.88391 | 0.92379 | 0.96202 | 0.99879 | 1.0343 | 2.0535 | 32
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 22 | 0.96835 | 0.94644 | 1.0167 | 1.0825 | 1.1445 | 1.2033 | 1.7558 | 23
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 17.6 | 0.61394 | 1.4341 | 1.5303 | 1.6207 | 1.7064 | 1.788 | 2.7325 | 15
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 7.7 | -0.972 | 1.4233 | 1.4838 | 1.5418 | 1.5978 | 1.6519 | 2.9537 | 16
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 7.7 | -0.82748 | 1.1231 | 1.1797 | 1.2336 | 1.2854 | 1.3351 | 2.3464 | 12
Morven | Morven | 132/66 | 30 |  |  | 0 | 0 | 2.4586 | 2.5704 | 2.6776 | 2.7807 | 2.88 | 0
Albury | Corowa | 132/22 | 30 | 27/30 |  | 33 | -0.93041 | 68.6334 | 69.0581 | 69.4645 | 69.8548 | 70.2307 | 7.9009 | 367
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 48.4 | 0.98525 | 7.2519 | 7.8421 | 8.3909 | 8.9059 | 9.3928 | 11.8796 | 9
Albury | Mulwala | 132/22 | 30 | 30 |  | 33 | -0.75496 | 5.9872 | 6.4233 | 6.8316 | 7.2169 | 7.5826 | 5.2066 | 14
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 77 | -0.97335 | 20.7376 | 22.6214 | 24.3599 | 25.9823 | 27.5092 | 33.5575 | 31
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 33 | 0 | 3.778 | 3.9602 | 4.1344 | 4.3016 | 4.4625 | 8.0445 | 34
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 11 | -0.37139 | 0.72131 | 0.74918 | 0.77605 | 0.80202 | 0.82718 | 1.8037 | 28
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 11 | 0.73189 | 1.1846 | 1.2257 | 1.2655 | 1.3041 | 1.3416 | 2.8911 | 22
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 33 | 0.93633 | 5.5031 | 5.902 | 6.2755 | 6.6281 | 6.9628 | 9.5823 | 57
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 5.5 | 0.99991 | 0.83583 | 0.87014 | 0.90315 | 0.93499 | 0.96579 | 2.0477 | 8
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 33 | -0.12404 | 3.8247 | 4.0921 | 4.3431 | 4.5804 | 4.806 | 6.3241 | 24
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 5.5 | -0.34507 | 0.35244 | 0.36042 | 0.36823 | 0.37588 | 0.38338 | 0.9199 | 8
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 27.5 | 0.74266 | 0.27437 | 0.27842 | 0.28241 | 0.28635 | 0.29023 | 0.6451 | 154
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 8.25 | 0.49614 | 0.35755 | 0.37087 | 0.38372 | 0.39616 | 0.40822 | 0.6977 | 9
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 13.75 | 0.25909 | 0.71528 | 0.76574 | 0.81308 | 0.8578 | 0.90031 | 1.0742 | 18
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 2.75 | 0.61725 | 0.11118 | 0.11977 | 0.12778 | 0.13532 | 0.14247 | 0.1024 | 1
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.60616 | 0.33901 | 0.33903 | 0.33906 | 0.33909 | 0.33912 | 0.5057 | 80
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.65 | 0.87314 | 0.099047 | 0.10477 | 0.1102 | 0.11538 | 0.12033 | 0.1909 | 24
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 33 | 0.98796 | 0.41246 | 0.41892 | 0.42529 | 0.43155 | 0.43773 | 0.993 | 22
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 11 | -0.95073 | 1.5815 | 1.6833 | 1.7793 | 1.8704 | 1.9572 | 2.6437 | 17
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 17.6 | 0.50998 | 2.3797 | 2.5335 | 2.6785 | 2.8161 | 2.9472 | 3.0082 | 13
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.1 | 0.50143 | 0.14782 | 0.15945 | 0.17028 | 0.18047 | 0.19011 | 0.256 | 4
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 13.75 | -0.99904 | 3.2801 | 3.5497 | 3.8003 | 4.0354 | 4.2574 | 4.8158 | 8
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 55 | -0.17134 | 5.2862 | 5.5893 | 5.8767 | 6.1506 | 6.4129 | 8.2317 | 4
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 27.5 | 0.99577 | 0.89391 | 0.91776 | 0.94101 | 0.96369 | 0.98586 | 1.8229 | 7
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | -0.96011 | 0.36744 | 0.3805 | 0.39312 | 0.40535 | 0.41722 | 0.5927 | 2
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | -0.40082 | 4.2931 | 4.5596 | 4.8114 | 5.0506 | 5.279 | 5.614 | 4
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 2.75 | 0.68603 | 0.39213 | 0.42156 | 0.44907 | 0.47499 | 0.49957 | 0.4552 | 12
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.87872 | 0.26109 | 0.28656 | 0.30994 | 0.33167 | 0.35207 | 0.297 | 11
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 10.45 | 0.78476 | 0.95288 | 0.99508 | 1.0356 | 1.0745 | 1.1121 | 1.6291 | 4
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.58106 | 0.099952 | 0.10927 | 0.11785 | 0.12584 | 0.13336 | 0.1534 | 19
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.69663 | 4.3397 | 4.6128 | 4.8705 | 5.1153 | 5.3489 | 6.8846 | 6
Yanco | Murrami | 33/11 | 5 | 5 |  | 5.5 | 0.25378 | 0.17633 | 0.1794 | 0.18242 | 0.18539 | 0.18832 | 0.3937 | 6
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.82382 | 1.9618 | 2.0661 | 2.1655 | 2.2605 | 2.3516 | 4.1105 | 20
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 6.875 | 0.7152 | 0.4093 | 0.43027 | 0.45027 | 0.46942 | 0.48781 | 0.8144 | 18
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.16758 | 0.77413 | 0.82865 | 0.8798 | 0.92814 | 0.97408 | 1.3394 | 4
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.89385 | 0.38643 | 0.41591 | 0.44343 | 0.46934 | 0.4939 | 0.5928 | 8
Buronga | Powercor Robinvale 22kV Euston Distribution Supply | [5 empty] | 0.97239 | 1.043 | 1.0653 | 1.0871 | 1.1086 | 1.1296 | 1.7272 | 19
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply | [5 empty] | 0.709 | 0.87396 | 0.88612 | 0.89812 | 0.90996 | 0.92165 | 1.0693 | 6
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 33 | 0.66595 | 2.653 | 2.8592 | 3.0514 | 3.2323 | 3.4035 | 4.4294 | 24
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 33 | -0.57179 | 2.7805 | 2.9251 | 3.0595 | 3.1855 | 3.3045 | 3.3488 | 33
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.8222 | 0.27737 | 0.28644 | 0.29522 | 0.30375 | 0.31205 | 0.48 | 4
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Lines Export
Supply Area | Feeder # | Feeder Voltage kV | Feeder Origin | Feeder Destination
[5 empty] | Line Rating | Line Forecast MVA
[5 empty] | Summer MVA | 2024 | 2025 | 2026 | 2027 | 2028
Casino | 96L | 132 | Transgrid Casino 132kV 96L Tee | Casino ZS | 140 | 9.4005 | 10.0464 | 10.6532 | 11.2272 | 11.7733
Casino | 6501 | 66 | Casino ZS | Rappville Tee | 16 | 0.28029 | 0.29653 | 0.31193 | 0.3266 | 0.34064
Casino | 8401 | 33 | Casino ZS | Mallanganee ZS | 4 | 0.85542 | 0.90643 | 0.95469 | 1.0006 | 1.0445
Casino | 8402 | 33 | Mallanganee ZS | Bonalbo ZS | 4 | 0.62047 | 0.65813 | 0.69371 | 0.72754 | 0.75984
Casino | 8403 | 33 | Bonalbo ZS | Urbenville ZS | 4 | 0.29439 | 0.31495 | 0.33425 | 0.35249 | 0.36984
Coffs Harbour | 96C/2(D) | 132 | TransGrid 96C Armidale Coffs Harbour Dorrigo Tee | Dorrigo ZS | 122 | 1.1101 | 1.1788 | 1.2437 | 1.3054 | 1.3643
Coffs Harbour | 702 | 66 | Boambee South 132/66kV STS | Sawtell ZS | 61 | 4.6784 | 5.1272 | 5.5397 | 5.9236 | 6.284
Coffs Harbour | 705 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 7.21 | 7.8274 | 8.3995 | 8.9351 | 9.4403
Coffs Harbour | 706 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 8.2114 | 8.9145 | 9.5661 | 10.1761 | 10.7515
Coffs Harbour | 7501 | 66 | Nana Glen ZS | Woolgoolga ZS | 29 | 2.6894 | 2.9197 | 3.1332 | 3.3329 | 3.5214
Coffs Harbour | 7502 | 66 | Nana Glen ZS | Ulong Tee | 9 | 0.32234 | 0.35749 | 0.38948 | 0.41903 | 0.44664
Coffs Harbour | 7502/1 | 66 | Ulong Tee | Ulong ZS | 9 | 0.32234 | 0.35749 | 0.38948 | 0.41903 | 0.44664
Coffs Harbour | 7503 | 66 | Ulong Tee | Dorrigo ZS | 9 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | 7509 | 66 | Moonee ZS | Woolgoolga ZS | 30 | 8.0546 | 8.7459 | 9.3865 | 9.986 | 10.5516
Coffs Harbour | 7510 | 66 | North Coffs ZS | Moonee ZS | 61 | 3.4905 | 3.7894 | 4.0664 | 4.3257 | 4.5703
Coffs Harbour | 703:NGN | 66 | TransGrid Coffs Harbour 132/66 kV STS | Nana Glen ZS | 62 | 4.4061 | 4.7834 | 5.133 | 5.4603 | 5.7691
Coffs Harbour | 711:CHN | 66 | TransGrid Coffs Harbour 132/66 kV STS | North Coffs ZS | 62 | 8.8694 | 9.6289 | 10.3327 | 10.9916 | 11.6131
Coffs Harbour | 87C | 66 | North Coffs ZS | South Coffs ZS | 68 | 5.5505 | 6.0258 | 6.4663 | 6.8786 | 7.2676
Grafton | 825 | 66 | TransGrid Koolkhan 132/66kV STS | Koolkhan ZS | 62 | 9.4816 | 10.1282 | 10.7359 | 11.311 | 11.8583
Grafton | 826 | 66 | TransGrid Koolkhan 132/66kV STS | Grafton North ZS | 61 | 7.7364 | 8.264 | 8.7598 | 9.2291 | 9.6756
Grafton | 6503 | 66 | Grafton North ZS | South Grafton ZS | 24 | 5.0534 | 5.398 | 5.7219 | 6.0284 | 6.3201
Grafton | 6504 | 66 | Five Mile Sw Stn | South Grafton ZS | 61 | 2.1881 | 2.3373 | 2.4775 | 2.6102 | 2.7365
Grafton | 6505 | 66 | Koolkhan SS | Grafton ZS | 52 | 8.4137 | 8.9874 | 9.5267 | 10.037 | 10.5226
Grafton | 6506 | 66 | Shannon Creek ZS | Nymboida ZS | 14 | 0.13024 | 0.13912 | 0.14747 | 0.15537 | 0.16289
Grafton | 6508 | 66 | Maclean ZS | Yamba ZS | 28 | 6.2256 | 6.7077 | 7.1573 | 7.5803 | 7.9809
Grafton | 6509 | 66 | Shannon Creek ZS | Five Mile Sw Stn | 14 | 0.59912 | 0.63997 | 0.67837 | 0.71471 | 0.74929
Grafton | 6510 | 66 | Grafton North ZS | Five Mile Sw Stn | 28 | 2.7351 | 2.9216 | 3.0969 | 3.2628 | 3.4207
Grafton | 896:MLN | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 21 | 4.5064 | 4.8137 | 5.1025 | 5.3759 | 5.6359
Grafton | 8G1 | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 68 | 5.7828 | 6.1771 | 6.5477 | 6.8985 | 7.2323
Grafton | 6402 | 33 | Maclean ZS | Yamba Tee | 8 | 0.23444 | 0.25042 | 0.26545 | 0.27967 | 0.2932
Grafton | 6403 | 33 | Yamba Tee | Redcliff ZS | 3 | 0.23444 | 0.25042 | 0.26545 | 0.27967 | 0.2932
Grafton | 6404 | 33 | Yamba Tee | Yamba ZS | 10 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7Y1 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7Y2 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7V1 | 33 | Ausgrid Salt Ash ZS | Tee with 7Y1 | 7 | 0 | 0 | 0 | 0 | 0
Herons Creek | 866:KEW | 66 | Herons Creek 132/66kV STS | Kew ZS | 16 | 6.2742 | 6.7206 | 7.1391 | 7.5344 | 7.91
Herons Creek | 871 | 66 | Kew ZS | Laurieton ZS | 36 | 4.2873 | 4.6032 | 4.8988 | 5.1776 | 5.442
Herons Creek | 862/1 | 66 | Kew ZS | Johns River ZS | 16 | 0.2961 | 0.30961 | 0.32255 | 0.335 | 0.34699
Herons Creek | 862/2 | 66 | TransGrid Taree 132/66/33kV STS | Johns River ZS | 16 | 0 | 0 | 0 | 0 | 0
Kempsey | 7R1 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 30 | 3.1533 | 3.4152 | 3.6584 | 3.8865 | 4.1018
Kempsey | 7R2/1 | 33 | TransGrid Kempsey 132/33kV STS | North St Tee | 26 | 3.6498 | 3.9529 | 4.2344 | 4.4984 | 4.7476
Kempsey | 7R2/2 | 33 | North St Tee | Smithtown ZS | 19 | 1.8249 | 1.9765 | 2.1172 | 2.2492 | 2.3738
Kempsey | 7R2/3 | 33 | North St Tee | North St ZS | 10 | 1.798 | 1.9474 | 2.0861 | 2.2161 | 2.3389
Kempsey | 7R3 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 26 | 3.1667 | 3.4298 | 3.674 | 3.903 | 4.1193
Kempsey | 7R4 | 33 | TransGrid Kempsey 132/33kV STS | Munga ZS | 3 | 0.58105 | 0.61942 | 0.65556 | 0.6898 | 0.72242
Kempsey | 7R5 | 33 | TransGrid Kempsey 132/33kV STS | North St ZS | 19 | 2.7642 | 2.9938 | 3.207 | 3.4069 | 3.5956
Kempsey | 7R6/1 | 33 | Prince St ZS | South West Rocks Tee | 15 | 2.3079 | 2.4996 | 2.6777 | 2.8446 | 3.0022
Kempsey | 7R6/2 | 33 | South West Rocks Tee | South West Rocks ZS | 19 | 1.1674 | 1.2644 | 1.3544 | 1.4388 | 1.5185
Kempsey | 7R6/3 | 33 | South West Rocks Tee | Smithtown ZS | 19 | 1.0869 | 1.1772 | 1.261 | 1.3396 | 1.4138
Kempsey | 7R7 | 33 | Prince St ZS | Crescent Head ZS | 5 | 0.79904 | 0.86455 | 0.92544 | 0.98257 | 1.0365
Kempsey | 7R8 | 33 | Smithtown ZS | South West Rocks ZS | 30 | 1.3821 | 1.4969 | 1.6035 | 1.7034 | 1.7978
Lismore | 9U8 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 183 | 24.3895 | 25.4318 | 26.4097 | 27.3338 | 28.2122
Lismore | 9U9 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 22.5704 | 23.535 | 24.4399 | 25.2951 | 26.108
Lismore | 9W1 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 20.8861 | 21.7786 | 22.616 | 23.4074 | 24.1596
Lismore | 9G2 | 132 | Ballina ZS | Lennox Head ZS | 124 | 5.39 | 5.6203 | 5.8364 | 6.0406 | 6.2347
Lismore | 9G3 | 132 | Lennox Head ZS | Suffolk Park ZS | 124 | 7.2091 | 7.5171 | 7.8062 | 8.0793 | 8.339
Lismore | 9G4 | 132 | Suffolk Park ZS | Ewingsdale ZS | 124 | 10.0388 | 10.4678 | 10.8703 | 11.2507 | 11.6122
Lismore | 9G5 | 132 | Ewingsdale ZS | Mullumbimby ZS | 122 | 17.5174 | 18.2659 | 18.9683 | 19.632 | 20.2629
Lismore | 9U6 | 132 | Lismore 132/66kV STS | Mullumbimby ZS | 107 | 11.0494 | 11.5216 | 11.9646 | 12.3833 | 12.7812
Lismore | 9U7 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 12.4643 | 12.9969 | 13.4967 | 13.9689 | 14.4178
Lismore | 9U7/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 9.5672 | 9.976 | 10.3596 | 10.7221 | 11.0667
Lismore | 892 | 66 | Lismore 132/66kV STS | Woodburn ZS | 11 | 3.7303 | 3.9917 | 4.2369 | 4.4687 | 4.689
Lismore | 893 | 66 | Lismore 132/66kV STS | Casino ZS | 34 | 0 | 0 | 0 | 0 | 0
Lismore | 894:LME | 66 | Lismore 132/66kV STS | Kyogle ZS | 11 | 2.9838 | 3.1675 | 3.341 | 3.506 | 3.6636
Lismore | 0897:LME | 66 | Lismore 132/66kV STS | Alstonville ZS | 62 | 8.5566 | 8.9222 | 9.2653 | 9.5895 | 9.8976
Lismore | 8502 | 66 | Lismore East ZS | Alstonville ZS | 62 | 4.5141 | 4.707 | 4.888 | 5.059 | 5.2216
Lismore | 8503 | 66 | Ballina ZS | Alstonville ZS | 62 | 3.9751 | 4.145 | 4.3043 | 4.455 | 4.5981
Lismore | 8507 | 66 | Alstonville ZS | Ballina ZS | 61 | 4.5815 | 4.7772 | 4.9609 | 5.1345 | 5.2995
Lismore | 8510 | 66 | Lismore Sw Stn | East Lismore ZS | 61 | 10.3083 | 10.7488 | 11.1621 | 11.5527 | 11.9239
Lismore | 8511 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 9.0282 | 9.414 | 9.776 | 10.118 | 10.4432
Lismore | 8512 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 2.9772 | 3.1985 | 3.4054 | 3.6004 | 3.7854
Lismore | 8513 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 2.9772 | 3.1985 | 3.4054 | 3.6004 | 3.7854
Lismore | 8514 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 2.3598 | 2.5051 | 2.6423 | 2.7728 | 2.8974
Lismore | 8515 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 2.262 | 2.4071 | 2.5443 | 2.6747 | 2.7992
Lismore | 8516 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 8.9608 | 9.3437 | 9.703 | 10.0425 | 10.3653
Nambucca Heads | 751 | 66 | TransGrid Nambucca 132/66 kV STS | Nambucca ZS | 15 | 4.1992 | 4.5431 | 4.8627 | 5.1626 | 5.446
Port Macquarie | 70Y | 33 | Rocks Ferry ZS | Telegraph Point ZS | 8 | 0.83005 | 0.89293 | 0.95166 | 1.007 | 1.0594
Port Macquarie | 701 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 22 | 5.51 | 5.9948 | 6.4432 | 6.8623 | 7.2573
Port Macquarie | 703:BPM | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 4.5665 | 4.9683 | 5.3399 | 5.6873 | 6.0146
Port Macquarie | 707 | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 5.1704 | 5.6252 | 6.046 | 6.4393 | 6.8099
Port Macquarie | 708 | 33 | TransGrid Port Macquarie 132/33kV STS | Owen Street ZS | 26 | 6.0006 | 6.5286 | 7.0169 | 7.4734 | 7.9035
Port Macquarie | 710 | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 31 | 6.529 | 7.1034 | 7.6347 | 8.1314 | 8.5994
Port Macquarie | 711:CPM | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 20 | 6.4913 | 7.0623 | 7.5906 | 8.0844 | 8.5497
Port Macquarie | 712 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 12 | 3.6608 | 3.9828 | 4.2807 | 4.5592 | 4.8216
Port Macquarie | 715 | 33 | Clearwater ZS | Owen Street ZS | 31 | 2.7173 | 2.9563 | 3.1775 | 3.3842 | 3.5789
Port Macquarie | 719/1 | 33 | Clearwater ZS | Lake Cathie ZS | 20 | 4.6922 | 5.1088 | 5.4939 | 5.8537 | 6.1927
Port Macquarie | 719/2 | 33 | Lake Cathie ZS | Laurieton ZS | 12 | 0 | 0 | 0 | 0 | 0
Port Macquarie | 765 | 33 | Rocks Ferry ZS | Koree ZS | 9 | 2.4531 | 2.6689 | 2.8685 | 3.0551 | 3.231
Port Macquarie | 784 | 33 | Koree ZS | Byabarra ZS | 9 | 0.64158 | 0.69802 | 0.75023 | 0.79904 | 0.84503
Stroud | 9C9/3 | 33 | Stroud 132/33kV STS | Dungog ZS | 27 | 2.2989 | 2.4593 | 2.6098 | 2.7521 | 2.8873
Stroud | 9C9/2 | 33 | Dungog ZS | Martins Creek ZS | 21 | 1.8867 | 2.0116 | 2.1292 | 2.2406 | 2.3467
Stroud | STR4B3/1 | 33 | Stroud 132/33kV STS | Booral ZS | 7 | 1.5752 | 1.6858 | 1.7895 | 1.8875 | 1.9806
Stroud | STR4B3/2 | 33 | Booral ZS | Bulahdelah ZS | 7 | 1.13 | 1.2093 | 1.2837 | 1.354 | 1.4209
Stroud | STR4B4 | 33 | Stroud 132/33kV STS | Dungog ZS | 4 | 0.79577 | 0.85129 | 0.90339 | 0.95264 | 0.99947
Stroud | STR4B5/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 2.2372 | 2.3943 | 2.5416 | 2.6807 | 2.813
Stroud | STR4B5/2 | 33 | Wards River Sw Stn | Stratford Tee | 19 | 1.2863 | 1.3693 | 1.4468 | 1.5197 | 1.5888
Stroud | STR4B5/2a | 33 | Stratford Tee | Stratford Coal ZS | 7 | 0 | 0 | 0 | 0 | 0
Stroud | STR4B5/3 | 33 | Stratford Tee | Gloucester ZS | 19 | 1.0706 | 1.1546 | 1.2329 | 1.3065 | 1.3761
Stroud | STR4B6/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 2.5797 | 2.7607 | 2.9306 | 3.091 | 3.2436
Stroud | STR4B6/2 | 33 | Wards River Sw Stn | Gloucester ZS | 17 | 2.0783 | 2.2413 | 2.3932 | 2.5361 | 2.6713
Stroud | STR4B7 | 33 | Stroud 132/33kV STS | Dungog ZS | 7 | 1.1937 | 1.2769 | 1.3551 | 1.429 | 1.4992
Stroud | STR4B8 | 33 | Stroud 132/33kV STS | Bulahdelah ZS | 7 | 1.4268 | 1.527 | 1.6209 | 1.7096 | 1.794
Stroud | 3801 | 33 | Bulahdelah ZS | Pacific Palms ZS | 7 | 1.5071 | 1.6242 | 1.7335 | 1.8362 | 1.9335
Stroud | 3803 | 33 | Bulahdelah ZS | Bungwahl Sw Stn | 7 | 0 | 0 | 0 | 0 | 0
Stroud | BLH4B4 | 33 | Bulahdelah ZS | Hawks Nest 132/33kV STS | 7 | 0.079902 | 0.085509 | 0.09077 | 0.09574 | 0.10046
Stroud | 7J1 | 33 | Ausgrid Recloser 33175 (Patterson) | Martins Creek Tee | 8 | 0 | 0 | 0 | 0 | 0
Stroud | 7J1/2 | 33 | Martins Creek Tee | Martins Creek ZS | 4 | 0.72479 | 0.77703 | 0.82597 | 0.87217 | 0.91605
Stroud | 7J1/3 | 33 | Martins Creek Tee | Gresford ZS | 4 | 0.72479 | 0.77703 | 0.82597 | 0.87217 | 0.91605
Taree | 861 | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 4.4016 | 4.7883 | 5.1461 | 5.4805 | 5.7957
Taree | 863:WTE | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 4.5596 | 4.9602 | 5.3308 | 5.6772 | 6.0037
Taree | 867 | 66 | TransGrid Taree 132/66/33kV STS | Hallidays Point ZS | 34 | 6.1847 | 6.7282 | 7.2309 | 7.7008 | 8.1437
Taree | 867/1 | 66 | Hallidays Point Tee | Tuncurry ZS | 39 | 6.1847 | 6.7282 | 7.2309 | 7.7008 | 8.1437
Taree | 868/1 | 66 | TransGrid Taree 132/66/33kV STS | Bohnock Tee | 36 | 7.2456 | 7.8823 | 8.4712 | 9.0218 | 9.5406
Taree | 868/2 | 66 | Bohnock Tee | Bohnock ZS | 16 | 3.8024 | 4.1503 | 4.4713 | 4.7707 | 5.0524
Taree | 868/3 | 66 | Bohnock Tee | Hallidays Point ZS | 38 | 5.3044 | 5.7705 | 6.2017 | 6.6047 | 6.9846
Taree | 872 | 66 | Tuncurry ZS | Forster ZS | 30 | 3.1149 | 3.3886 | 3.6418 | 3.8785 | 4.1016
Taree | 86C | 66 | Tuncurry ZS | Forster ZS | 42 | 2.7312 | 2.9712 | 3.1932 | 3.4007 | 3.5963
Taree | 86R | 66 | Hallidays Point ZS | Tuncurry ZS | 38 | 5.1916 | 5.6477 | 6.0697 | 6.4642 | 6.836
Taree | 7G2/1 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Tee | 22 | 1.6799 | 1.8085 | 1.9286 | 2.0416 | 2.1487
Taree | 7G2/2 | 33 | Kanangra Tee | Coopernook ZS | 7 | 1.4366 | 1.5465 | 1.6492 | 1.7459 | 1.8375
Taree | 7G2/3 | 33 | Coopernook ZS | Harrington ZS | 8 | 2.7407 | 2.9694 | 3.1818 | 3.3808 | 3.5687
Taree | 7G4 | 33 | Bootawa ZS | Wingham ZS | 18 | 0.66725 | 0.71834 | 0.76603 | 0.81093 | 0.85346
Taree | 7G5 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Dr ZS | 17 | 2.4728 | 2.6621 | 2.8388 | 3.0052 | 3.1628
Taree | 7G1 | 33 | TransGrid Taree 132/66/33kV STS | Bootawa ZS | 17 | 1.8055 | 1.9438 | 2.0728 | 2.1943 | 2.3094
Taree | 7G3 | 33 | TransGrid Taree 132/66/33kV STS | Wingham ZS | 18 | 1.8997 | 2.0452 | 2.1809 | 2.3088 | 2.4299
Terranora | 757 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 141.4214 | 141.4214 | 141.4214 | 141.4214 | 141.4214
Terranora | 758 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 142.8356 | 142.8356 | 142.8356 | 142.8356 | 142.8356
Terranora | 9501 | 66 | Terranora 110/66kV STS | Cudgen ZS | 59 | 7.2183 | 7.7088 | 8.1698 | 8.6062 | 9.0215
Terranora | 9502 | 66 | Terranora 110/66kV STS | Murwillumbah ZS | 61 | 5.0528 | 5.3887 | 5.7048 | 6.0044 | 6.2896
Terranora | 9503 | 66 | Terranora 110/66kV STS | Banora Pt ZS | 59 | 13.4582 | 14.362 | 15.2122 | 16.0173 | 16.7838
Terranora | 9504 | 66 | Terranora 110/66kV STS | Condong Sw Stn | 61 | 4.5475 | 4.8498 | 5.1344 | 5.4039 | 5.6607
Terranora | 9505 | 66 | Cudgen ZS | Banora Point ZS | 53 | 0.55533 | 0.59252 | 0.62751 | 0.66065 | 0.6922
Terranora | 9508 | 66 | Terranora 110/66kV STS | Tweed Heads ZS | 41 | 2.7685 | 2.9651 | 3.1494 | 3.3235 | 3.4889
Terranora | 9510 | 66 | Banora Point ZS | Tweed Heads South ZS | 43 | 8.6674 | 9.2424 | 9.7836 | 10.2964 | 10.7849
Terranora | 9514 | 66 | Condong Sw Stn | Murwillumbah ZS | 61 | 8.5898 | 9.1608 | 9.6982 | 10.2074 | 10.6924
Terranora | 9516 | 66 | Tweed Head South ZS | Tweed Heads ZS | 43 | 0.65917 | 0.70597 | 0.74985 | 0.7913 | 0.83069
Terranora | 9406 | 33 | Cudgen ZS | Casuarina Sw Stn | 17 | 8.718 | 9.3132 | 9.8727 | 10.402 | 10.9057
Terranora | 9407 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 0 | 0 | 0 | 0 | 0
Terranora | 9409 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 8.718 | 9.3132 | 9.8727 | 10.402 | 10.9057
Armidale | 661/1 | 66 | TransGrid Armidale 330/132/66kV STS | Hillgrove Tee | 20 | 0.3755 | 0.40389 | 0.4304 | 0.45538 | 0.47905
Armidale | 661/2 | 66 | Hillgrove Tee | Hillgrove ZS | 16 | 0.16093 | 0.17309 | 0.18446 | 0.19516 | 0.20531
Armidale | 661/3 | 66 | Hillgrove Tee | Oaky ZS | 20 | 0.22798 | 0.24522 | 0.26132 | 0.27648 | 0.29085
Armidale | 662/1 | 66 | TransGrid Armidale 330/132/66kV STS | Uralla Tee | 12 | 2.5824 | 2.7598 | 2.9259 | 3.0826 | 3.2314
Armidale | 662/2 | 66 | Uralla Tee | Uralla ZS | 9 | 1.6842 | 1.8153 | 1.9375 | 2.0525 | 2.1614
Armidale | 662/4 | 66 | Uralla Tee | Walcha South ZS | 9 | 0.89825 | 0.94457 | 0.98839 | 1.0301 | 1.07
Armidale | 664 | 66 | TransGrid Armidale 330/132/66kV STS | Galloway St ZS | 28 | 6.1958 | 6.6641 | 7.1016 | 7.5137 | 7.9044
Armidale | 665 | 66 | TransGrid Armidale 330/132/66kV STS | Madgwick Dr ZS | 21 | 3.983 | 4.2841 | 4.5653 | 4.8303 | 5.0814
Armidale | 66C | 66 | Miller St ZS | Madgwick Dr ZS | 21 | 0.79124 | 0.85105 | 0.90692 | 0.95955 | 1.0094
Armidale | 66F | 66 | Galloway St ZS | Miller St ZS | 15 | 2.8431 | 3.058 | 3.2588 | 3.4479 | 3.6271
Bathurst | 81H | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 62 | 3.1684 | 3.4526 | 3.7151 | 3.9602 | 4.191
Bathurst | 81G | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 64 | 4.5263 | 4.9322 | 5.3072 | 5.6574 | 5.9871
Bathurst | 81F | 66 | TransGrid Panorama 132/66kV STS | Russell St ZS | 64 | 8.4498 | 9.2322 | 9.9533 | 10.6256 | 11.2577
Bathurst | 81J | 66 | Raglan ZS | Russell St ZS | 64 | 1.6154 | 1.765 | 1.9028 | 2.0314 | 2.1522
Bathurst | 81L | 66 | TransGrid Panorama 132/66kV STS | Raglan ZS | 64 | 5.219 | 5.7023 | 6.1476 | 6.5629 | 6.9533
Bathurst | 81C | 66 | TransGrid Panorama 132/66kV STS | Blayney ZS | 19 | 3.6538 | 3.9578 | 4.2399 | 4.5042 | 4.7537
Bathurst | 66:MAN | 66 | Blayney ZS | Mandurama ZS | 9 | 0.82463 | 0.87796 | 0.92823 | 0.97592 | 1.0214
Beryl | 94M/4 | 132 | TransGrid 94M Mudgee Tee | Mudgee ZS | 128 | 8.1449 | 8.7783 | 9.369 | 9.9245 | 10.4506
Beryl | 851 | 66 | TransGrid Beryl 132/66kV STS | Gulgong ZS | 28 | 1.1327 | 1.2303 | 1.3207 | 1.4053 | 1.4851
Beryl | 851 | 66 | Gulgong ZS | Mudgee ZS | 28 | 0 | 0 | 0 | 0 | 0
Beryl | 852 | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 15 | 0 | 0 | 0 | 0 | 0
Beryl | 86J | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 61 | 4.1249 | 4.3432 | 4.551 | 4.7497 | 4.9404
Beryl | 85A | 66 | Dunedoo ZS | Coonabarabran ZS | 11 | 3.1329 | 3.2414 | 3.3452 | 3.4448 | 3.5408
Beryl | 80L | 66 | Ulan Sw Stn | Ulan Town ZS | 15 | 0.82639 | 0.87429 | 0.9197 | 0.96298 | 1.0044
Beryl | 80R | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 64 | 0 | 0 | 0 | 0 | 0
Beryl | 80U | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 61 | 0 | 0 | 0 | 0 | 0
Beryl | 80T | 66 | Ulan Sw Stn | Moolarben No1 Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Beryl | 80W | 66 | Moolarben No1 Mine ZS | Moolarben No2 Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Beryl | 80X | 66 | Moolarben No2 Mine ZS | Wilpinjong Mine ZS | 61 | 0 | 0 | 0 | 0 | 0
Broken Hill | X4 | 220 | TransGrid Broken Hill 220/22kV STS | Perilya Mine | 213 | 0 | 0 | 0 | 0 | 0
Broken Hill | 5B1:PPL | 66 | Pinnacles Place ZS | Mt Gipps ZS | 19 | 0 | 0 | 0 | 0 | 0
Broken Hill | 5B1:MTG | 66 | Mt Gipps ZS | Sunset Strip ZS | 19 | 0.32873 | 0.34154 | 0.35362 | 0.3651 | 0.37607
Broken Hill | 5B1:SUN | 66 | Sunset Strip ZS | Menindee ZS | 6 | 0.50073 | 0.54133 | 0.5791 | 0.61454 | 0.64805
Dubbo | 94J/3 | 132 | 94J Tee | Dubbo South ZS | 106 | 60.8413 | 60.8413 | 60.8413 | 60.8413 | 60.8413
Dubbo | 943/2 | 132 | Dubbo South ZS | Narromine South Sw Stn | 106 | 43.2543 | 43.2543 | 43.2543 | 43.2543 | 43.2543
Dubbo | 94W/1 | 132 | Dubbo 132/66kV STS | Nevertire Tee | 128 | 143.9735 | 143.9189 | 143.867 | 143.8175 | 143.7701
Dubbo | 94W/2 | 132 | Nevertire Tee | Nevertire ZS | 124 | 1.3955 | 1.4733 | 1.5473 | 1.6178 | 1.6854
Dubbo | 94W/3 | 132 | Nevertire Tee | Nevertire Sw Stn | 128 | 144.9569 | 144.9569 | 144.9569 | 144.9569 | 144.9569
Dubbo | 9GX | 132 | Nevertire Sw Stn | Nyngan 132/66kV STS | 128 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GP | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 9.5314 | 9.7194 | 9.8979 | 10.0681 | 10.2312
Dubbo | 9GR | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GT | 132 | Dubbo West ZS | Narromine South Sw Stn | 140 | 9.5314 | 9.7194 | 9.8979 | 10.0681 | 10.2312
Dubbo | 9GU | 132 | Narromine South Sw Stn | Nyngan 132/66kV STS | 106 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GW | 132 | Dubbo 132/66kV STS | Dubbo West ZS | 140 | 47.0569 | 47.0569 | 47.0569 | 47.0569 | 47.0569
Dubbo | 812 | 66 | Yarrandale ZS | Gilgandra ZS | 15 | 0 | 0 | 0 | 0 | 0
Dubbo | 815 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 24 | 1.519 | 1.6241 | 1.7228 | 1.8162 | 1.905
Dubbo | 816 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 24 | 1.519 | 1.6241 | 1.7228 | 1.8162 | 1.905
Dubbo | 813:EUL | 66 | Eulomogo ZS | Geurie Tee | 12 | 0.41999 | 0.44706 | 0.47259 | 0.4968 | 0.51988
Dubbo | 813/1:GUE | 66 | Geurie Tee | Geurie ZS | 16 | 0.41999 | 0.44706 | 0.47259 | 0.4968 | 0.51988
Dubbo | 814/1 | 66 | Gilgandra ZS | Gulargambone ZS | 11 | 2.0373 | 2.1571 | 2.2703 | 2.3778 | 2.4805
Dubbo | 814/2 | 66 | Gulargambone ZS | Coonamble ZS | 11 | 1.5158 | 1.6107 | 1.7003 | 1.7855 | 1.8668
Dubbo | 81M | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 3.8413 | 4.1108 | 4.3637 | 4.6027 | 4.8298
Dubbo | 81P | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 61 | 2.2603 | 2.3946 | 2.5215 | 2.642 | 2.7572
Dubbo | 81R | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 3.8413 | 4.1108 | 4.3637 | 4.6027 | 4.8298
Dubbo | 81X | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 28 | 2.7626 | 2.9267 | 3.0818 | 3.2292 | 3.3699
Dubbo | 81T | 66 | Yarrandale ZS | Gilgandra ZS | 43 | 4.0921 | 4.3319 | 4.5585 | 4.7739 | 4.9796
Forbes | 858 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 3.5446 | 3.7932 | 4.0265 | 4.247 | 4.4566
Forbes | 859 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 0 | 0 | 0 | 0 | 0
Forbes | 893/5 | 66 | TransGrid Forbes 132/66kV STS | Payten's Bridge ZS | 12 | 0.52098 | 0.55193 | 0.58123 | 0.60912 | 0.63579
Forbes | 894:CDN | 66 | Condobolin ZS | Lake Cargelligo ZS | 15 | 1.1091 | 1.1491 | 1.1877 | 1.2251 | 1.2614
Forbes | 896:WJL | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 20 | 25.4558 | 25.4558 | 25.4558 | 25.4558 | 25.4558
Forbes | 897:CDN | 66 | West Jemalong ZS | Condobolin ZS | 20 | 0 | 0 | 0 | 0 | 0
Forbes | 89H | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 43 | 42.4264 | 42.4264 | 42.4264 | 42.4264 | 42.4264
Glen Innes | 886 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 70 | 4.7328 | 4.8768 | 5.0131 | 5.1427 | 5.2666
Glen Innes | 887 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 19 | 5.6338 | 5.8052 | 5.9674 | 6.1217 | 6.2692
Glen Innes | 6NY | 66 | Glen Innes ZS | Guyra ZS | 11 | 1.6155 | 1.7158 | 1.8105 | 1.9004 | 1.9864
Glen Innes | 6NE | 66 | Glen Innes ZS | Emmaville ZS | 17 | 0.95277 | 0.98176 | 1.0092 | 1.0353 | 1.0602
Glen Innes | 6AE/A | 66 | Pindari ZS | Ashford ZS | 17 | 0 | 0 | 0 | 0 | 0
Glen Innes | 6AE/E | 66 | Emmaville ZS | Pindari ZS | 17 | 0.3314 | 0.34148 | 0.35102 | 0.3601 | 0.36878
Gunnedah | 877 | 66 | TransGrid Gunnedah 132/66kV STS | Keepit Dam ZS | 10 | 0.28284 | 0.28284 | 0.28284 | 0.28284 | 0.28284
Gunnedah | 878/1 | 66 | Gunnedah ZS | Emerald Hill Sw Stn | 24 | 17.4032 | 17.4237 | 17.4434 | 17.4623 | 17.4806
Gunnedah | 878/5 | 66 | Emerald Hill Sw Stn | Boggabri ZS | 24 | 0.60435 | 0.63272 | 0.65987 | 0.68595 | 0.71107
Gunnedah | 88K | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 11.2448 | 11.4937 | 11.7263 | 11.9457 | 12.154
Gunnedah | 88L | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 11.2448 | 11.4937 | 11.7263 | 11.9457 | 12.154
Inverell | 734 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 15.3074 | 15.569 | 15.8181 | 16.0563 | 16.2849
Inverell | 735 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 15.5543 | 15.8201 | 16.0732 | 16.3152 | 16.5476
Inverell | 6AB | 66 | Borthwick St ZS | Ashford ZS | 17 | 5.586 | 5.6814 | 5.7723 | 5.8592 | 5.9427
Inverell | 6AF/A | 66 | Ashford ZS | Wallangra ZS | 11 | 0.77154 | 0.78473 | 0.79728 | 0.80929 | 0.82081
Inverell | 6AF/F | 66 | Wallangra ZS | Coolatai Sw Stn | 11 | 0.64809 | 0.65917 | 0.66972 | 0.6798 | 0.68948
Inverell | 6AX | 66 | Ashford ZS | Texas ZS | 9 | 4.6601 | 4.7397 | 4.8156 | 4.8881 | 4.9577
Inverell | 6BC | 66 | Borthwick St ZS | Copeton ZS | 21 | 0.70982 | 0.72195 | 0.7335 | 0.74454 | 0.75515
Inverell | 6BD | 66 | Borthwick St ZS | Bundarra ZS | 14 | 0.8024 | 0.81612 | 0.82917 | 0.84166 | 0.85365
Inverell | 6BW | 66 | Borthwick St ZS | Warialda ZS | 15 | 6.1415 | 6.2464 | 6.3464 | 6.4419 | 6.5337
Inverell | 6FH | 66 | Coolatai Sw Stn | Yallaroi ZS | 20 | 1.9443 | 1.9775 | 2.0091 | 2.0394 | 2.0684
Inverell | 6FW | 66 | Warialda ZS | Coolatai Sw Stn | 11 | 1.4814 | 1.5067 | 1.5308 | 1.5538 | 1.576
Inverell | 6HG | 66 | Yallaroi ZS | Goondiwindi ZS | 20 | 0 | 0 | 0 | 0 | 0
Inverell | 6WK | 66 | Warialda ZS | Bingara ZS | 11 | 2.3763 | 2.417 | 2.4556 | 2.4926 | 2.5281
Molong | 8C1 | 66 | TransGrid Molong 132/66kV STS | Cumnock / Orange West Tee | 61 | 0.44026 | 0.45875 | 0.47653 | 0.49366 | 0.51022
Molong | 8C1/3 | 66 | Cumnock / Orange West Tee | Cumnock ZS | 9 | 0.44026 | 0.45875 | 0.47653 | 0.49366 | 0.51022
Molong | 8C1/4 | 66 | Cumnock / Orange West Tee | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0
Moree | 876 | 66 | TransGrid Moree 132/66kV STS | Moree Solar Farm | 70 | 56.7807 | 56.8231 | 56.8282 | 56.733 | 56.8257
Moree | 87J | 66 | Moree Solar Farm | Bellata ZS | 25 | 0.15241 | 0.15429 | 0.15614 | 0.15797 | 0.15978
Moree | 721 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 25.8987 | 26.0171 | 26.1303 | 26.239 | 26.3437
Moree | 722 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 27.315 | 27.4399 | 27.5593 | 27.6739 | 27.7843
Moree | 881/1 | 66 | TransGrid Moree 132/66kV STS | Ashley Tee | 15 | 0.76674 | 0.78673 | 0.80594 | 0.82445 | 0.84234
Moree | 881/2 | 66 | Ashley Tee | Ashley ZS | 10 | 0.16793 | 0.17039 | 0.17281 | 0.17519 | 0.17755
Moree | 6PU | 66 | Ashley Tee | Mungindi ZS | 10 | 0.37227 | 0.3905 | 0.40792 | 0.42463 | 0.4407
Moree | 723:WTR/1 | 66 | TransGrid Moree 132/66kV STS | Wathagar ZS | 12 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Moree | 723:WTR/2 | 66 | Wathagar ZS | Wenna ZS | 15 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Narrabri | 879 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 18 | 0.57065 | 0.60137 | 0.63053 | 0.65835 | 0.68501
Narrabri | 882 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 64 | 1.1096 | 1.1693 | 1.226 | 1.2801 | 1.332
Narrabri | 885 | 66 | Burren Junction ZS | Merrywinebone ZS | 15 | 0.25659 | 0.27603 | 0.29419 | 0.31129 | 0.3275
Narrabri | 833:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 1.9292 | 2.0181 | 2.1033 | 2.1852 | 2.2641
Narrabri | 834:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 1.9292 | 2.0181 | 2.1033 | 2.1852 | 2.2641
Narrabri | 861/1 | 66 | TransGrid Narrabri 132/66kV STS | Wilga Park ZS | 64 | 30.326 | 30.264 | 30.2112 | 30.1663 | 30.1283
Narrabri | 861/2 | 66 | Wilga Park ZS | Walgett ZS | 64 | 2.8347 | 3.0782 | 3.3032 | 3.5134 | 3.7114
Narrabri | 88F | 66 | Narrabri Coal Tee | Boggabri ZS | 24 | 0 | 0 | 0 | 0 | 0
Narrabri | 878/3 | 66 | TransGrid Narrabri 132/66kV STS | Narrabri Coal Tee | 61 | 26.4458 | 26.4458 | 26.4458 | 26.4458 | 26.4458
Narrabri | 88C | 66 | Narrabri Coal Tee | Narrabri Coal | 61 | 26.163 | 26.163 | 26.163 | 26.163 | 26.163
Narrabri | 880/1 | 66 | Wee Waa ZS | Burren Junction ZS | 13 | 0.43877 | 0.46253 | 0.48495 | 0.50626 | 0.52662
Narrabri | 880/2 | 66 | Burren Junction ZS | Walgett ZS | 13 | 0 | 0 | 0 | 0 | 0
Narrabri | 890:BRE | 66 | Walgett ZS | Brewarrina ZS | 15 | 0.34083 | 0.36521 | 0.38805 | 0.40962 | 0.43012
Narrabri | 895:LGR | 66 | Walgett ZS | Lightning Ridge ZS | 15 | 1.1611 | 1.2865 | 1.4006 | 1.5062 | 1.6048
Nyngan | 9UT | 132 | Nyngan 132/66kV STS | Nyngan Solar Farm | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 9UW | 132 | Nyngan Solar Farm | Scrubby Valley Sw Stn | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 946/2 | 132 | Scrubby Valley Sw Stn | Cobar CSA ZS | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 946/3 | 132 | Scrubby Valley Sw Stn | Cobar Peak ZS | 102 | 0 | 0 | 0 | 0 | 0
Nyngan | 94R | 132 | Cobar CSA ZS | Cobar Elura ZS | 128 | 0 | 0 | 0 | 0 | 0
Nyngan | 811 | 66 | Nyngan 132/66kV STS | Cobar Town ZS | 10 | 3.4354 | 3.5905 | 3.7366 | 3.8749 | 4.0068
Nyngan | 854 | 66 | Nyngan 132/66kV STS | Nyngan Town ZS | 15 | 1.632 | 1.7054 | 1.7758 | 1.8435 | 1.9088
Nyngan | 820/1:NYN | 66 | Nyngan Town ZS | Nevertire Tee | 15 | 0 | 0 | 0 | 0 | 0
Nyngan | 820:NVE | 66 | Nyngan 132/66kV STS | Nevertire ZS | 11 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/1 | 66 | Nyngan 132/66kV STS | Girilambone Tee | 28 | 1.0274 | 1.0533 | 1.0783 | 1.1025 | 1.126
Nyngan | 855/1a | 66 | Girilambone Tee | Girilambone ZS | 24 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/2 | 66 | Girilambone Tee | Byrock Tee | 28 | 1.2843 | 1.3166 | 1.3478 | 1.3781 | 1.4075
Nyngan | 855/3 | 66 | Byrock Tee | Bourke ZS | 28 | 0.92827 | 0.96053 | 0.99167 | 1.0218 | 1.051
Nyngan | 855/3a | 66 | Byrock Tee | Byrock ZS | 15 | 0.020482 | 0.021438 | 0.022353 | 0.023233 | 0.02408
Nyngan | 855/4 | 66 | Girilambone ZS | Tritton Mine ZS | 24 | 0 | 0 | 0 | 0 | 0
Oberon | 94C | 132 | TransGrid Wallerawang 330/132/66kV STS | Oberon 132 ZS | 128 | 0 | 0 | 0 | 0 | 0
Oberon | 856 | 66 | TransGrid Wallerawang 330/132/66kV STS | Oberon Town ZS | 28 | 1.8992 | 2.0279 | 2.1485 | 2.2624 | 2.3706
Oberon | 81B | 33 | Oberon Town ZS | Burraga ZS | 8 | 0 | 0 | 0 | 0 | 0
Orange | 94G | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 0 | 0 | 0 | 0 | 0
Orange | 9MC | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 0 | 0 | 0 | 0 | 0
Orange | 807 | 66 | TransGrid Orange 132/66kV STS | Orange West & South Tee | 61 | 7.0705 | 7.6924 | 8.2677 | 8.8055 | 9.3123
Orange | 807/2 | 66 | Orange West & South Tee | Orange South ZS | 63 | 0 | 0 | 0 | 0 | 0
Orange | 807/3 | 66 | Orange West & South Tee | Orange West ZS | 62 | 7.0705 | 7.6924 | 8.2677 | 8.8055 | 9.3123
Orange | 818/1 | 66 | TransGrid Orange 132/66kV STS | Blayney ZS | 11 | 0 | 0 | 0 | 0 | 0
Orange | 8C2 | 66 | TransGrid Orange 132/66kV STS | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0
Orange | 8F1 | 66 | TransGrid Orange 132/66kV STS | Orange South ZS | 63 | 8.1421 | 8.9598 | 9.7089 | 10.4043 | 11.056
Orange | 8M1 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 11 | 6.8169 | 7.3794 | 7.902 | 8.3922 | 8.8552
Orange | 8M2 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 21 | 0 | 0 | 0 | 0 | 0
Parkes | 300 | 132 | TransGrid Parkes 132/66kV STS | North Parkes Mine ZS | 87 | 0 | 0 | 0 | 0 | 0
Parkes | 898 | 66 | TransGrid Parkes 132/66kV STS | Trundle ZS | 11 | 6.7882 | 6.7882 | 6.7882 | 6.7882 | 6.7882
Parkes | 899 | 66 | Parkes Town ZS | Peak Hill ZS | 13 | 4.0809 | 4.1182 | 4.1535 | 4.1869 | 4.2189
Parkes | 89G | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 68 | 5.6998 | 5.9297 | 6.1463 | 6.3517 | 6.5475
Parkes | 89L | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 38 | 5.1298 | 5.3367 | 5.5317 | 5.7166 | 5.8927
Parkes | 89M | 66 | Peak Hill ZS | Tomingley Mine ZS | 17 | 0 | 0 | 0 | 0 | 0
Tamworth | 801 | 66 | Transgrid Tamworth 132/66kV STS | Oxley Vale ZS | 63 | 4.9119 | 5.3186 | 5.6963 | 6.0505 | 6.385
Tamworth | 803 | 66 | Transgrid Tamworth 132/66kV STS | South Tamworth ZS | 70 | 8.7987 | 9.5082 | 10.1683 | 10.7881 | 11.3742
Tamworth | 804 | 66 | Transgrid Tamworth 132/66kV STS | Nundle ZS | 8 | 0.45199 | 0.47134 | 0.48992 | 0.50782 | 0.52512
Tamworth | 806 | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 38 | 2.4768 | 2.6498 | 2.8119 | 2.965 | 3.1104
Tamworth | 873 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 2.9207 | 3.142 | 3.3488 | 3.5435 | 3.7281
Tamworth | 874 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 3.0399 | 3.2703 | 3.4855 | 3.6882 | 3.8803
Tamworth | 803/2 | 66 | South Tamworth ZS | Oxley Vale ZS | 63 | 1.6373 | 1.7729 | 1.8988 | 2.0168 | 2.1283
Tamworth | 806/1 | 66 | Goddard Lane ZS | Attunga ZS | 18 | 2.7925 | 2.9614 | 3.1212 | 3.2731 | 3.4182
Tamworth | 806/1 | 66 | Attunga ZS | Manilla ZS | 18 | 1.9127 | 2.0368 | 2.1538 | 2.2647 | 2.3704
Tamworth | 806/2 | 66 | Manilla ZS | Upper Manilla ZS | 18 | 0.72084 | 0.769 | 0.81431 | 0.85722 | 0.89808
Tamworth | 806/4 | 66 | Upper Manilla ZS | Barraba ZS | 15 | 0.76181 | 0.81338 | 0.86186 | 0.90776 | 0.95145
Tamworth | 80C | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 61 | 2.1964 | 2.3498 | 2.4936 | 2.6293 | 2.7583
Tamworth | 813:CLA | 66 | Transgrid Tamworth 132/66kV STS | Currububula ZS | 28 | 2.3231 | 2.4638 | 2.5967 | 2.723 | 2.8435
Tamworth | 813/1:QDI | 66 | Currububula ZS | Werris Creek ZS | 28 | 2.0977 | 2.2318 | 2.3583 | 2.4784 | 2.5929
Tamworth | 813/2:QDI | 66 | Werris Creek ZS | Quirindi ZS | 28 | 1.5362 | 1.6337 | 1.7258 | 1.8131 | 1.8965
Tamworth | 870/1:KTL | 66 | Transgrid Tamworth 132/66kV STS | Kootingal Tee | 14 | 2.4708 | 2.6376 | 2.7945 | 2.9431 | 3.0845
Tamworth | 870/2:KTL | 66 | Kootingal Tee | Kootingal ZS | 12 | 2.196 | 2.3464 | 2.4878 | 2.6216 | 2.7488
Tamworth | 870/3:KTL | 66 | Kootingal Tee | Bendemeer ZS | 13 | 0.27479 | 0.2912 | 0.30673 | 0.32151 | 0.33564
Tamworth | 798 | 33 | Quirindi ZS | Murrurundi ZS | 4 | 0.898 | 0.96417 | 1.0261 | 1.0845 | 1.1398
Tamworth | 799/1 | 33 | Quirindi ZS | Caroona Tee | 6 | 0.45227 | 0.46021 | 0.46785 | 0.47524 | 0.4824
Tamworth | 799/2 | 33 | Caroona Tee | Caroona ZS | 4 | 0.019655 | 0.020548 | 0.021404 | 0.022226 | 0.02302
Tamworth | 799/3 | 33 | Caroona Tee | Spring Ridge ZS | 3 | 0.056565 | 0.058517 | 0.060406 | 0.062238 | 0.064017
Tamworth | 799/4 | 33 | Spring Ridge ZS | Colly Blue ZS | 3 | 0.12943 | 0.13541 | 0.14114 | 0.14665 | 0.15195
Wellington | 945/3 | 132 | TransGrid Line 945 Wellington 132kV Tee | Wellington 132kV ZS | 124 | 2.442 | 2.6667 | 2.874 | 3.0672 | 3.249
Wellington | 947/1 | 132 | TransGrid Line 947 Burrendong Tee | Burrendong Hydro | 36 | 8.8471 | 8.9786 | 9.0331 | 9.1136 | 9.1665
Wellington | 94F | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 123.3462 | 123.3462 | 123.3462 | 123.3462 | 123.3462
Wellington | 94J | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 114.3151 | 114.3151 | 114.3151 | 114.3151 | 114.3151
Wellington | 805 | 66 | Wellington 132kV ZS | Mumbil ZS | 11 | 0.38483 | 0.42531 | 0.46226 | 0.49647 | 0.52847
Wellington | 813:WGN | 66 | Wellington 132kV ZS | Geurie Tee | 12 | 0 | 0 | 0 | 0 | 0
Albury | 997/1 | 132 | Union Rd ZS | Corowa ZS | 128 | 29.8482 | 30.1926 | 30.5185 | 30.8287 | 31.1253
Albury | 997/2 | 132 | Corowa ZS | Mulwala ZS | 128 | 2.3949 | 2.5693 | 2.7326 | 2.8868 | 3.033
Albury | 99E | 132 | Union Rd ZS | Jelbart ZS | 148 | 3.626 | 3.9211 | 4.1955 | 4.453 | 4.6964
Albury | 99G | 132 | Union Rd ZS | Jelbart ZS | 148 | 3.626 | 3.9211 | 4.1955 | 4.453 | 4.6964
Bega | 84G | 66 | Bega 132/66kV STS | Eden South ZS | 61 | 1.8208 | 1.9527 | 2.0761 | 2.1926 | 2.3031
Bega | 84H | 66 | Eden South ZS | Edrom ZS | 38 | 0 | 0 | 0 | 0 | 0
Bega | 84M | 66 | Bega 132/66kV STS | Maher St ZS | 61 | 2.4517 | 2.6062 | 2.7511 | 2.8881 | 3.0183
Bega | 89A | 66 | Bega 132/66 | Pambula ZS | 38 | 4.8044 | 5.2127 | 5.5912 | 5.9457 | 6.2803
Bega | 84P | 66 | Bega 132/66kV STS | Maher St ZS | 38 | 2.4517 | 2.6062 | 2.7511 | 2.8881 | 3.0183
Bega | 89F | 66 | Pambula ZS | Eden South ZS | 16 | 0.60058 | 0.64096 | 0.67895 | 0.71491 | 0.74915
Bega | 7802/1 | 33 | Maher St ZS | Brogo ZS | 12 | 0 | 0 | 0 | 0 | 0
Bega | 7802/2 | 33 | Brogo ZS | Cobargo ZS | 10 | 2.5714 | 2.7902 | 2.9929 | 3.1827 | 3.3618
Bega | 84R | 33 | Maher St ZS | Quira ZS | 6 | 0 | 0 | 0 | 0 | 0
Bega | 7814 | 33 | Cobargo ZS | Bermagui ZS | 5 | 1.6441 | 1.7937 | 1.9317 | 2.0605 | 2.1817
Buronga | 87G | 66 | Dareton ZS | Ellerslie ZS | 67 | 0.24964 | 0.25779 | 0.2657 | 0.27337 | 0.28084
Buronga | 87H/1 | 66 | Ellerslie ZS | Ginkgo Snapper Tee | 45 | 0 | 0 | 0 | 0 | 0
Buronga | 87H/2 | 66 | Ginkgo Snapper Tee | Ginkgo ZS | 20 | 0 | 0 | 0 | 0 | 0
Buronga | 87H/3 | 66 | Ginkgo Snapper Tee | Snapper ZS | 12 | 0 | 0 | 0 | 0 | 0
Buronga | 83U | 66 | Powercor Mildura ZS (NSW Border) | Buronga ZS | 22 | 4.3876 | 4.7438 | 5.0752 | 5.3862 | 5.6802
Buronga | 83W | 66 | Buronga ZS | Dareton ZS | 22 | 0 | 0 | 0 | 0 | 0
Buronga | Merbein - Dareton Line | 66 | Powercor Mildura ZS (NSW Border) | Dareton ZS | 49 | 0.27959 | 0.28873 | 0.29758 | 0.30618 | 0.31454
Coleambally | CLY1526 | 33 | Coleambally 132/33kV STS | Coleambally Tee | 10 | 0.3933 | 0.40795 | 0.4221 | 0.43578 | 0.44905
Coleambally | CLY1526 | 33 | Coleambally Tee | Coleambally ZS | 10 | 0.35755 | 0.37087 | 0.38372 | 0.39616 | 0.40822
Coleambally | CLY1526 | 33 | Coleambally Tee | Egansford ZS | 8 | 0.1223 | 0.13175 | 0.14056 | 0.14886 | 0.15671
Coleambally | CLY1530 | 33 | Coleambally 132/33kV STS | Ringwood Rd ZS | 8 | 0.96995 | 1.0164 | 1.06 | 1.1011 | 1.1403
Coleambally | CLY1530 | 33 | Ringwood Rd ZS | Darlington Point ZS | 8 | 0.71528 | 0.76574 | 0.81308 | 0.8578 | 0.90031
Cooma | 974 | 132 | TransGrid Cooma 132/66kV STS | Bega 132/66kV STS | 128 | 56.4783 | 57.0182 | 57.521 | 57.9934 | 58.4404
Cooma | 97R | 132 | TransGrid Cooma 132/66kV STS | Steeple Flat 132/66kV STS | 140 | 34.1142 | 33.535 | 32.8258 | 32.4982 | 31.8103
Cooma | 82D | 66 | TransGrid Cooma 132/66kV STS | Jindabyne East ZS | 20 | 2.7303 | 2.9644 | 3.1802 | 3.3814 | 3.5706
Cooma | 84J | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 70 | 1.6619 | 1.7647 | 1.8619 | 1.9542 | 2.0423
Cooma | 84L | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 64 | 1.6619 | 1.7647 | 1.8619 | 1.9542 | 2.0423
Cooma | 82J/1 | 66 | Snowy Adit 132/66/11kV ZS | Snowy Lookout Sw Stn | 12 | 0 | 0 | 0 | 0 | 0
Cooma | 82J/2 | 66 | Jindabyne ZS | Snowy Lookout Sw Stn | 12 | 0.14142 | 0.14142 | 0.14142 | 0.14142 | 0.14142
Cooma | 82R | 66 | Jindabyne East ZS | Jindabyne ZS | 20 | 0.93549 | 1.019 | 1.0962 | 1.1683 | 1.2362
Cooma | 888/1 | 66 | TransGrid Cooma 132/66kV STS | Rhine Falls Sw Stn | 16 | 0.76279 | 0.78989 | 0.8154 | 0.83957 | 0.86262
Cooma | 888/3 | 66 | Rhine Falls Sw Stn | Adaminaby ZS | 16 | 0.51119 | 0.54004 | 0.56709 | 0.59264 | 0.61693
Cooma | 888/4 | 66 | Rhine Falls Sw Stn | Eucumbene Tee | 15 | 0.14142 | 0.14142 | 0.14142 | 0.14142 | 0.14142
Cooma | 888/6 | 66 | Eucumbene Tee | Eucumbene ZS | 15 | 0 | 0 | 0 | 0 | 0
Cooma | 888/7 | 66 | Eucumbene Tee | Snowy Adit 132/66/11kV ZS | 20 | 0 | 0 | 0 | 0 | 0
Cooma | 849/1 | 33 | Adaminaby ZS | Providence Portal ZS | 7 | 0 | 0 | 0 | 0 | 0
Cowra | 865 | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 2.6717 | 2.8938 | 3.1 | 3.2934 | 3.476
Cowra | 863:CWD | 66 | TransGrid Cowra 132/66kV STS | Canowindra ZS | 9 | 2.0103 | 2.1944 | 2.3641 | 2.5225 | 2.6715
Cowra | 866:COW | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 2.6717 | 2.8938 | 3.1 | 3.2934 | 3.476
Cowra | 891/1 | 66 | TransGrid Cowra 132/66kV STS | Wyangala Dam Tee | 20 | 31.4672 | 31.4509 | 31.4353 | 31.4203 | 31.4059
Cowra | 891/2 | 66 | Wyangala Dam Tee | Wyangala Dam | 19 | 31.8198 | 31.8198 | 31.8198 | 31.8198 | 31.8198
Cowra | 891/5 | 66 | Monteagle Tee | Monteagle ZS | 13 | 0.25375 | 0.26286 | 0.27166 | 0.28019 | 0.28846
Cowra | 891/6 | 66 | Monteagle Tee | Young ZS | 19 | 0 | 0 | 0 | 0 | 0
Cowra | 891/7 | 66 | Bendick Murrell Tee | Bendick Murrell ZS | 19 | 0.80198 | 0.84205 | 0.8803 | 0.91696 | 0.9522
Cowra | 891:BMU | 66 | Wyangala Dam Tee | Bendick Murrell Tee | 19 | 1.0029 | 1.0497 | 1.0944 | 1.1373 | 1.1786
Cowra | 891:BMU | 66 | Bendick Murrell Tee | Monteagle Tee | 19 | 0.25375 | 0.26286 | 0.27166 | 0.28019 | 0.28846
Cowra | 893/1 | 66 | TransGrid Cowra 132/66kV STS | Grenfell Tee | 12 | 2.1125 | 2.2873 | 2.4497 | 2.602 | 2.7458
Cowra | 893/4 | 66 | Grenfell Tee | Payten's Bridge ZS | 12 | 0 | 0 | 0 | 0 | 0
Cowra | 893/6 | 66 | Grenfell Tee | Grenfell ZS | 12 | 2.1125 | 2.2873 | 2.4497 | 2.602 | 2.7458
Darlington Point | 99N | 132 | TransGrid Darlington Point 330/132kV STS | Hillston ZS | 128 | 51.8189 | 51.9575 | 52.0892 | 52.2149 | 52.3353
Darlington Point | 99R | 132 | TransGrid Darlington Point 330/132kV STS | Hay 132 ZS | 128 | 2.01 | 2.0152 | 2.0203 | 2.0253 | 2.0303
Darlington Point | HAT 22 | 33 | Hay 132 ZS | Hay ZS | 8 | 1.2982 | 1.3802 | 1.4575 | 1.5308 | 1.6008
Darlington Point | HAT 32 | 33 | Hay 132 ZS | Hay ZS | 8 | 0.32455 | 0.34504 | 0.36437 | 0.38271 | 0.4002
Darlington Point | HAT 42 | 33 | Hay 132 ZS | Carrathool ZS | 7 | 0.38777 | 0.39802 | 0.4079 | 0.41746 | 0.42674
Darlington Point | HIL1117 | 33 | Hillston ZS | Ivanhoe ZS | 8 | 1.0997 | 1.1728 | 1.2417 | 1.3069 | 1.369
Deniliquin | 844 | 66 | TransGrid Deniliquin 132/66kV STS | Barham ZS | 11 | 1.3174 | 1.3955 | 1.4694 | 1.5398 | 1.6071
Deniliquin | 845 | 66 | TransGrid Deniliquin 132/66kV STS | Deniliquin ZS | 38 | 5.0106 | 5.3076 | 5.5888 | 5.8565 | 6.1125
Deniliquin | 822/1 | 66 | TransGrid Deniliquin 132/66kV STS | Murgha ZS | 11 | 1.7227 | 1.8249 | 1.9215 | 2.0136 | 2.1016
Deniliquin | 822/2 | 66 | Murgha ZS | Moulamein ZS | 11 | 1.4413 | 1.5267 | 1.6076 | 1.6846 | 1.7582
Deniliquin | 84Y | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 66 | 1.9367 | 2.0515 | 2.1602 | 2.2636 | 2.3626
Deniliquin | MM61 | 66 | Moulamein ZS | Koraleigh ZS | 15 | 0.95708 | 1.0138 | 1.0675 | 1.1187 | 1.1676
Deniliquin | No.6 Moama | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 34 | 1.3512 | 1.4313 | 1.5071 | 1.5793 | 1.6483
Finley | 9R4 | 132 | TransGrid Finley 132/66kV STS | Mulwala ZS | 140 | 0 | 0 | 0 | 0 | 0
Finley | 84A | 66 | TransGrid Finley 132/66kV STS | Jerilderie ZS | 15 | 0.72131 | 0.74918 | 0.77605 | 0.80202 | 0.82718
Finley | 84B | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 1.3223 | 1.3861 | 1.4471 | 1.5056 | 1.5619
Finley | 84C | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 2.4557 | 2.5742 | 2.6874 | 2.796 | 2.9006
Goulburn | 972 | 132 | TransGrid Marulan 330/132kV STS | Goulburn 132/66/33kV STS | 180 | 110.0434 | 109.8199 | 109.7699 | 110.135 | 110.0643
Goulburn | 9UR | 132 | TransGrid Marulan 330/132kV STS | Taralga Wind Farm | 140 | 110.0434 | 109.8199 | 109.7699 | 110.135 | 110.0643
Goulburn | 843 | 66 | Clinton St ZS | Goulburn North ZS | 46 | 1.6193 | 1.7565 | 1.8837 | 2.0028 | 2.1152
Goulburn | 82K/2 | 66 | Woodlawn ZS | Bungendore ZS | 28 | 0 | 0 | 0 | 0 | 0
Goulburn | 840:GOU | 66 | Goulburn 132/66/33kV STS | Goulburn North ZS | 61 | 4.3666 | 4.7007 | 5.0125 | 5.306 | 5.5842
Goulburn | 841:GBN | 66 | Goulburn North ZS | Crookwell ZS | 9 | 1.8101 | 1.9138 | 2.0122 | 2.106 | 2.1958
Goulburn | 850:GOU | 66 | Goulburn 132/66/33kV STS | Woodlawn ZS | 28 | 7.2669 | 7.3346 | 7.3972 | 7.4557 | 7.5108
Goulburn | 86M/1 | 66 | Goulburn 132/66/33kV STS | Marulan North Tee | 25 | 1.4183 | 1.5379 | 1.6488 | 1.7527 | 1.8508
Goulburn | 86M/2 | 66 | Marulan North Tee | Marulan South ZS | 25 | 0 | 0 | 0 | 0 | 0
Goulburn | 86L | 66 | Marulan North Tee | Marulan North ZS | 12 | 1.5759 | 1.7088 | 1.832 | 1.9474 | 2.0564
Goulburn | 870:GOU | 66 | Goulburn 132/66/33kV STS | Clinton St ZS | 34 | 8.5495 | 9.236 | 9.8747 | 10.4745 | 11.0417
Goulburn | GOU12 | 33 | Goulburn 132/66/33kV STS | Brisbane Grove ZS | 7 | 1.1923 | 1.2797 | 1.3615 | 1.4386 | 1.5118
Griffith | 79C/1 | 33 | TransGrid Griffith 132/33kV STS | Widgelli / Willbriggie Tee | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79C/2 | 33 | Widgelli / Willbriggie Tee | Widgelli ZS | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79C/3 | 33 | Widgelli / Willbriggie Tee | Willbriggie Tee | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79C/4 | 33 | Willbriggie Tee | Willbriggie ZS | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79C/5 | 33 | Willbriggie Tee | 79C / 79P Tee | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79F | 33 | TransGrid Griffith 132/33kV STS | Yenda ZS | 22 | 0 | 0 | 0 | 0 | 0
Griffith | 79G | 33 | Beelbangera ZS | Griffith ZS | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79J | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 0 | 0 | 0 | 0 | 0
Griffith | 79L | 33 | TransGrid Griffith 132/33kV STS | Beelbangera ZS | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79M | 33 | TransGrid Griffith 132/33kV STS | Hanwood ZS | 22 | 0.89391 | 0.91776 | 0.94101 | 0.96369 | 0.98586
Griffith | 79P | 33 | TransGrid Griffith 132/33kV STS | Warrawidgee Tee | 22 | 0 | 0 | 0 | 0 | 0
Griffith | 79W | 33 | Warrawidgee Tee | Warrawidgee ZS | 6 | 0 | 0 | 0 | 0 | 0
Griffith | 79W | 33 | Warrawidgee Tee | Nericon Tee | 21 | 0 | 0 | 0 | 0 | 0
Griffith | 79W | 33 | Nericon Tee | Nericon ZS | 6 | 0 | 0 | 0 | 0 | 0
Griffith | 79R | 33 | TransGrid Griffith 132/33kV STS | Tharbogang ZS | 31 | 4.2931 | 4.5596 | 4.8114 | 5.0506 | 5.279
Griffith | 79U | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 5.2862 | 5.5893 | 5.8767 | 6.1506 | 6.4129
Harden - Murrumburrah | 836 | 66 | TransGrid Murrumburrah 132/66kV STS | Cootamundra ZS | 12 | 3.7391 | 4.0611 | 4.3595 | 4.6386 | 4.9019
Harden - Murrumburrah | 837 | 66 | TransGrid Murrumburrah 132/66kV STS | Jugiong ZS | 12 | 0.16169 | 0.16845 | 0.17495 | 0.18121 | 0.18727
Harden - Murrumburrah | 847 | 66 | TransGrid Murrumburrah 132/66kV STS | Boorowa ZS | 10 | 3.7763 | 3.8288 | 3.879 | 3.9273 | 3.9739
Harden - Murrumburrah | 823/3 | 66 | Bogalara Sw Stn | Marilba ZS | 12 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 830/1:PCR | 66 | Bogalara Sw Stn | Parsons Creek ZS | 11 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 838/3 | 66 | Jugiong ZS | Bogalara Sw Stn | 12 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 83A | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 1.724 | 1.8555 | 1.9783 | 2.0939 | 2.2035
Harden - Murrumburrah | 83D | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 890:YOU | 66 | TransGrid Murrumburrah 132/66kV STS | Young ZS | 24 | 4.764 | 5.0867 | 5.3902 | 5.6775 | 5.951
Moruya North | 98H | 132 | Endeavour Energy Evans Lane Sw Stn | Moruya North 132/33kV STS | 180 | 0 | 0 | 0 | 0 | 0
Moruya North | 98M | 132 | Endeavour Energy Evans Lane Sw Stn | Batemans Bay ZS | 50 | 0 | 0 | 0 | 0 | 0
Moruya North | 98T | 132 | Batemans Bay ZS | Moruya North 132/33kV STS | 61 | 0 | 0 | 0 | 0 | 0
Moruya North | 7703 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 30 | 0 | 0 | 0 | 0 | 0
Moruya North | 7704 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 26 | 0 | 0 | 0 | 0 | 0
Moruya North | 7706 | 33 | Moruya North 132/33kV STS | Mossy Point ZS | 25 | 0 | 0 | 0 | 0 | 0
Moruya North | 7712 | 33 | Bodalla Tee | Bodalla ZS | 10 | 0 | 0 | 0 | 0 | 0
Moruya North | 7713 | 33 | Bodalla Tee | Narooma ZS | 21 | 0 | 0 | 0 | 0 | 0
Moruya North | 7817 | 33 | Narooma Tee | Cobargo ZS | 10 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/1 | 33 | Moruya Town ZS | Tuross Tee | 17 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/2 | 33 | Tuross Tee | Tuross ZS | 7 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/3 | 33 | Tuross Tee | Bodalla Tee | 21 | 0 | 0 | 0 | 0 | 0
Moruya North | 7715/1 | 33 | Moruya Town ZS | Narooma Tee | 30 | 0 | 0 | 0 | 0 | 0
Moruya North | 7715/2 | 33 | Narooma Tee | Narooma ZS | 10 | 0 | 0 | 0 | 0 | 0
Morven | 996/1 | 132 | TransGrid 132kV Line 996 Tee | Morven 132/66kV STS | 45 | 2.4586 | 2.5704 | 2.6776 | 2.7807 | 2.88
Morven | 83M/3 | 66 | Morven 132/66kV STS | Culcairn ZS | 15 | 1.4233 | 1.4838 | 1.5418 | 1.5978 | 1.6519
Morven | 83M/4 | 66 | Morven 132/66kV STS | Holbrook ZS | 15 | 1.1231 | 1.1797 | 1.2336 | 1.2854 | 1.3351
Munyang | 56 | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.12149 | 0.13752 | 0.15187 | 0.16497 | 0.17711
Munyang | 57A | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.052528 | 0.059095 | 0.065003 | 0.070416 | 0.075442
Munyang | 57B | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.035019 | 0.039397 | 0.043335 | 0.046944 | 0.050295
Munyang | No.1 Perisher | 33 | TransGrid Munyang 132/33kV STS | Smiggin Sw Stn | 38 | 0.12149 | 0.13752 | 0.15187 | 0.16497 | 0.17711
Munyang | No.2 Perisher | 33 | TransGrid Munyang 132/33kV STS | Blue Cow Tee | 38 | 0.087547 | 0.098492 | 0.10834 | 0.11736 | 0.12574
Munyang | No.2 Perisher | 33 | Blue Cow Tee | Smiggin Sw Stn | 38 | 0.087547 | 0.098492 | 0.10834 | 0.11736 | 0.12574
Munyang | 60/2 | 33 | Bullocks Portal ZS | Bullocks Flat ZS | 19 | 0.1063 | 0.12033 | 0.13289 | 0.14435 | 0.15497
Munyang | 58 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.70711 | 0.70711 | 0.70711 | 0.70711 | 0.70711
Munyang | 59 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.039853 | 0.045178 | 0.049939 | 0.054284 | 0.058305
Munyang | Bullocks Portal Line | 33 | Perisher ZS | Bullocks Portal ZS | 20 | 0.12149 | 0.13752 | 0.15187 | 0.16497 | 0.17711
Queanbeyan | 97Y | 132 | TransGrid Williamsdale 330/132kV STS | Googong Town ZS | 91 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 975 | 132 | TransGrid Queanbeyan 132/66kV STS | Googong Town ZS | 41 | 7.9558 | 8.8011 | 9.572 | 10.2853 | 10.9522
Queanbeyan | 82A | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 6.6798 | 7.3084 | 7.887 | 8.4259 | 8.9325
Queanbeyan | 82B | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 5.0099 | 5.4813 | 5.9152 | 6.3195 | 6.6993
Queanbeyan | 82F | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 49 | 5.0225 | 5.4666 | 5.8772 | 6.2609 | 6.6224
Queanbeyan | 82G | 66 | TransGrid Queanbeyan 132/66kV STS | Captains Flat ZS | 12 | 2.0439 | 2.1784 | 2.3038 | 2.4217 | 2.5335
Queanbeyan | 82K/1 | 66 | TransGrid Queanbeyan 132/66kV STS | Sutton / Bungendore Tee | 28 | 6.7519 | 7.232 | 7.6803 | 8.1025 | 8.5026
Queanbeyan | 82K/1 | 66 | Sutton / Bungendore Tee | Bungendore ZS | 28 | 4.5715 | 4.9114 | 5.2279 | 5.5252 | 5.8065
Queanbeyan | 82K/3 | 66 | Sutton / Bungendore Tee | Sutton ZS | 28 | 2.1807 | 2.3209 | 2.4527 | 2.5775 | 2.6963
Queanbeyan | 82M | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 20 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 830:QSH | 66 | Queanbeyan South ZS | Googong Dam ZS | 15 | 0.70113 | 0.70113 | 0.70113 | 0.70113 | 0.70113
Steeple Flat | 97C | 132 | Steeple Flat 132/66kV STS | Boco Rock Wind Farm | 140 | 114.44 | 114.5202 | 114.4159 | 114.6725 | 114.5171
Steeple Flat | 97R | 132 | Steeple Flat 132/66kV STS | Bega 132/66kV STS | 140 | 57.9877 | 58.5421 | 59.0583 | 59.5434 | 60.0023
Steeple Flat | 810/3 | 66 | Steeple Flat 132/66kV STS | Brown Mountain Hydro | 70 | 4.6983 | 4.6984 | 4.7096 | 4.7176 | 4.7053
Steeple Flat | 810/4 | 66 | Steeple Flat 132/66kV STS | Bombala ZS | 21 | 0.74711 | 0.80978 | 0.86794 | 0.92244 | 0.97389
Steeple Flat | S839 | 66 | Brown Mountain Hydro | Quira ZS | 70 | 0.53247 | 0.58226 | 0.62811 | 0.67084 | 0.711
Temora | 901 | 132 | Temora 132/66 STS | Wyalong Switching Station | 108 | 0 | 0 | 0 | 0 | 0
Temora | 9JW | 132 | Wyalong Switching Station | West Wyalong Switching Station | 108 | 0 | 0 | 0 | 0 | 0
Temora | 9JX | 132 | West Wyalong Switching Station | Lake Cowal | 108 | 0 | 0 | 0 | 0 | 0
Temora | 4 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 0 | 0 | 0 | 0 | 0
Temora | 5 | 66 | Temora 132/66 STS | Ariah Park Tee | 21 | 0 | 0 | 0 | 0 | 0
Temora | 6 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 2.7598 | 2.9565 | 3.1409 | 3.3151 | 3.4805
Temora | 20-60 | 66 | Ariah Park Tee | West Wyalong ZS | 21 | 0 | 0 | 0 | 0 | 0
Temora | 60-70 | 66 | West Wyalong ZS | Anona ZS | 7 | 0.33589 | 0.35519 | 0.37349 | 0.39094 | 0.40764
Temora | 80-140 | 66 | Ariah Park Tee | Ariah Park ZS | 15 | 0 | 0 | 0 | 0 | 0
Temora | 80-140 | 66 | Ariah Park ZS | Ardlethan ZS | 11 | 0.27374 | 0.29393 | 0.31283 | 0.33064 | 0.34754
Temora | 835/J | 66 | Junee Reefs ZS | Junee ZS | 12 | 0 | 0 | 0 | 0 | 0
Temora | 835/T | 66 | Temora 132/66 STS | Junee Reefs ZS | 12 | 0.11928 | 0.12014 | 0.121 | 0.12185 | 0.1227
Tumut | 827 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 3.207 | 3.4274 | 3.6345 | 3.8304 | 4.0168
Tumut | 828 | 66 | TransGrid Tumut 132/66kV STS | Gundagai South ZS | 11 | 1.7451 | 1.8543 | 1.9571 | 2.0546 | 2.1475
Tumut | 829 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 0 | 0 | 0 | 0 | 0
Tumut | 831 | 66 | Gundagai South ZS | Nangus ZS | 11 | 0.44359 | 0.4726 | 0.49947 | 0.52463 | 0.54836
Tumut | 848 | 66 | Adelong Tee | Adelong ZS | 12 | 0.65634 | 0.69341 | 0.72859 | 0.76215 | 0.79429
Tumut | 830/2:GUN | 66 | Gundagai South ZS | Parsons Creek ZS | 11 | 0.16425 | 0.16441 | 0.16456 | 0.16472 | 0.16487
Tumut | 848/1 | 66 | Adelong Tee | Batlow ZS | 21 | 2.0504 | 2.1587 | 2.2616 | 2.3599 | 2.4543
Tumut | 848/2 | 66 | Batlow ZS | Tumbarumba ZS | 22 | 1.4906 | 1.56 | 1.6265 | 1.6903 | 1.7519
Tumut | 848/3 | 66 | TransGrid Tumut 132/66kV STS | Adelong Tee | 21 | 2.5755 | 2.7134 | 2.8445 | 2.9697 | 3.0897
Tumut | 850:TAL | 66 | TransGrid Tumut 132/66kV STS | Talbingo ZS | 18 | 19.6576 | 19.6576 | 19.6576 | 19.6576 | 19.6576
Wagga (Copland St) | 83L | 66 | Hammond Ave ZS | Bomen ZS | 54 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Uranquinty ZS | 28 | 2.1871 | 2.3184 | 2.4425 | 2.5605 | 2.6732
Wagga (Copland St) | 840/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bulgary ZS | 15 | 0.88391 | 0.92379 | 0.96202 | 0.99879 | 1.0343
Wagga (Copland St) | 840/2 | 66 | Bulgary ZS | Lockhart ZS | 15 | 0.88391 | 0.92379 | 0.96202 | 0.99879 | 1.0343
Wagga (Copland St) | 840/3 | 66 | Lockhart Tee | Kywong ZS | 16 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M/1 | 66 | Uranquinty ZS | Henty ZS | 15 | 0.75302 | 0.78815 | 0.82178 | 0.85409 | 0.88521
Wagga (Copland St) | 83M/2 | 66 | Henty ZS | Culcairn ZS | 15 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8W9 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Ashmont ZS | 34 | 5.6198 | 6.1749 | 6.6837 | 7.1562 | 7.5993
Wagga (Copland St) | 8WF/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bourkelands ZS | 34 | 5.1223 | 5.6144 | 6.0668 | 6.4877 | 6.8828
Wagga (Copland St) | 8WM | 66 | Hammond Ave ZS | Morrow St ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WO | 66 | Ashmont ZS | Bourkelands ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WP | 66 | Morrow St ZS | Cartwrights Hill ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WR | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 0.88592 | 0.94013 | 0.99137 | 1.0401 | 1.0866
Wagga (Copland St) | 8WT | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 0.83481 | 0.88589 | 0.93418 | 0.98009 | 1.024
Wagga (Copland St) | 8WG | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Kooringal ZS | 34 | 6.0179 | 6.5597 | 7.06 | 7.5271 | 7.9669
Wagga (Copland St) | 8WF/2 | 66 | Bourkelands ZS | Kooringal ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga North | 99U | 132 | TransGrid Wagga North 132/66kV STS | Sebastopol Sw Stn | 128 | 106.066 | 106.066 | 106.066 | 106.066 | 106.066
Wagga North | 9J6 | 132 | Sebastopol Sw Stn | Temora 132/66 STS | 128 | 0 | 0 | 0 | 0 | 0
Wagga North | 9J5/1 | 132 | TransGrid Wagga North 132/66kV STS | Junee 132/66/11kV ZS | 140 | 0 | 0 | 0 | 0 | 0
Wagga North | 9J5/2 | 132 | Junee 132/66/11kV ZS | Temora 132/66 STS | 140 | 14.9893 | 14.9893 | 14.9893 | 14.9893 | 14.9893
Wagga North | 30-90 | 66 | Junee ZS | Coolamon ZS | 6 | 1.8804 | 1.9872 | 2.0877 | 2.1827 | 2.2731
Wagga North | 834:JUN | 66 | Junee ZS | Bethungra ZS | 11 | 0.51877 | 0.52522 | 0.53134 | 0.53718 | 0.54277
Wagga North | 83C | 66 | TransGrid Wagga North 132/66kV STS | Oura ZS | 24 | 0.32567 | 0.33909 | 0.35176 | 0.3638 | 0.37529
Wagga North | 83C | 66 | Oura ZS | Forest Hill ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga North | 83G | 66 | TransGrid Wagga North 132/66kV STS | Bomen ZS | 34 | 2.8811 | 3.1523 | 3.4009 | 3.6318 | 3.8484
Wagga North | 83J | 66 | Bomen ZS | Cartwrights Hill ZS | 34 | 3.2369 | 3.5372 | 3.8127 | 4.0686 | 4.3086
Wagga North | 850:BET | 66 | Bethungra ZS | Cootamundra ZS | 12 | 0 | 0 | 0 | 0 | 0
Wagga North | CHI2527 | 33 | Cartwrights Hill ZS | Euberta ZS | 4 | 0.43851 | 0.45995 | 0.48027 | 0.49963 | 0.51817
Wagga North | CHI2527 | 33 | Euberta ZS | Ganmurra ZS | 4 | 0.19817 | 0.20831 | 0.21783 | 0.22683 | 0.23538
Wagga North | Mates Gully | 33 | Oura ZS | Mates Gully ZS | 3 | 0.56913 | 0.59096 | 0.61185 | 0.63191 | 0.65123
Wagga North | Mates Gully | 33 | Mates Gully ZS | Tarcutta ZS | 4 | 0.29012 | 0.30344 | 0.3162 | 0.32846 | 0.34028
Wagga North | 8WJ | 66 | TransGrid Wagga North 132/66kV STS | Forest Hill ZS | 34 | 1.5697 | 1.6836 | 1.7894 | 1.8885 | 1.9821
Yanco | 840/4 | 66 | Narrandra ZS | Kywong ZS | 16 | 0.099952 | 0.10927 | 0.11785 | 0.12584 | 0.13336
Yanco | 841:YNC | 66 | TransGrid Yanco 132/33/66kV STS | Narrandera ZS | 15 | 1.9793 | 2.0884 | 2.192 | 2.2909 | 2.3856
Yanco | 7L3 | 33 | TransGrid Yanco 132/33/66kV STS | Cudgel ZS | 8 | 7.7782 | 7.7782 | 7.7782 | 7.7782 | 7.7782
Yanco | 7L6 | 33 | TransGrid Yanco 132/33/66kV STS | Whitton / Murrami Tee | 15 | 1.8746 | 1.895 | 1.9146 | 1.9335 | 1.9518
Yanco | 7L6 | 33 | Whitton / Murrami Tee | Whitton ZS | 8 | 0.4093 | 0.43027 | 0.45027 | 0.46942 | 0.48781
Yanco | 7L6 | 33 | Whitton / Murrami Tee | Murrami ZS | 8 | 0.17633 | 0.1794 | 0.18242 | 0.18539 | 0.18832
Yanco | 7L5 | 33 | TransGrid Yanco 132/33/66kV STS | Yanco ZS | 8 | 2.8572 | 3.0428 | 3.2176 | 3.3835 | 3.5415
Yanco | 7L5 | 33 | Yanco ZS | Leeton ZS | 6 | 2.0831 | 2.2141 | 2.3378 | 2.4553 | 2.5675
Yanco | 7L4 | 33 | TransGrid Yanco 132/33/66kV STS | Leeton ZS | 31 | 2.2567 | 2.3986 | 2.5327 | 2.6599 | 2.7814
Yass | 971(1) | 132 | TransGrid Yass 330/132/66kV STS | Cullerin Range Wind Farm | 106 | 77.9841 | 77.8365 | 78.0423 | 78.0869 | 78.0199
Yass | 971(2) | 132 | Cullerin Range Wind Farm | Gunning Wind Farm | 140 | 48.3866 | 48.3398 | 48.4895 | 48.5367 | 48.4585
Yass | 971(3) | 132 | Cullerin Range Wind Farm | Goulburn 132/66/33kV STS | 106 | 0 | 0 | 0 | 0 | 0
Yass | 976/2 (M) | 132 | TransGrid 132kV Line 976/2(Y) / Murrumbateman Tee | Murrumbateman ZS | 42 | 4.0067 | 4.3246 | 4.6206 | 4.8988 | 5.162
Yass | 824 | 66 | TransGrid Yass 330/132/66kV STS | Yass ZS | 12 | 5.4605 | 5.8197 | 6.158 | 6.4787 | 6.7842
Yass | 823/5 | 66 | Yass ZS | Marilba ZS | 12 | 0.54887 | 0.5833 | 0.6158 | 0.64667 | 0.67613

## BSP Export
Connection Point | Forecast PF | Summer Forecast (MVA)
|  | 23/24 | 24/25 | 25/26 | 26/27 | 27/28
Albury (Corowa) | -0.93041 | 34.3167 | 34.5291 | 34.7323 | 34.9274 | 35.1153
Albury (Mulwala) | -0.75496 | 2.9936 | 3.2116 | 3.4158 | 3.6084 | 3.7913
Albury (Union Rd + Jelbart) | 0.99967 | 28.9079 | 30.9684 | 32.891 | 34.7007 | 36.4154
Armidale | -0.99142 | 13.4108 | 14.4245 | 15.3715 | 16.2635 | 17.109
Balranald | 0.709 | 0.43698 | 0.44306 | 0.44906 | 0.45498 | 0.46083
Beryl | 0.99872 | 92.5163 | 92.8829 | 93.2293 | 93.5585 | 93.873
Boambee South | -0.94868 | 9.5916 | 10.4188 | 11.1849 | 11.9018 | 12.578
Broken Hill 22kV | -0.95792 | 24.9301 | 26.0737 | 27.1368 | 28.1344 | 29.0772
Casino | -0.94616 | 10.0006 | 10.6876 | 11.3331 | 11.9438 | 12.5247
Coffs Harbour | -0.20102 | 28.6111 | 31.061 | 33.3314 | 35.4567 | 37.4616
Coleambally | 0.68621 | 1.6906 | 1.7528 | 1.813 | 1.8712 | 1.9276
Cooma 132kV | 0.50944 | 125.7869 | 126.9893 | 128.1091 | 129.1613 | 130.1568
Cooma 66kV | 0.4953 | 4.6371 | 4.8622 | 5.0749 | 5.277 | 5.47
Cowra | -0.3874 | 30.2718 | 31.1005 | 31.8718 | 32.5961 | 33.2811
Darlington Point | 1 | 89.3429 | 89.5819 | 89.8089 | 90.0256 | 90.2332
Deniliquin | 0.90913 | 11.2598 | 11.9271 | 12.5591 | 13.1607 | 13.736
Dorrigo | 0.325 | 1.1101 | 1.1788 | 1.2437 | 1.3054 | 1.3643
Dunoon | -0.94009 | 3.4196 | 3.6611 | 3.8877 | 4.1018 | 4.3052
Evans Lane | 1 | 0 | 0 | 0 | 0 | 0
Finley 132kV | 1 | 0 | 0 | 0 | 0 | 0
Finley 66kV | -0.7009 | 2.6056 | 2.64 | 2.673 | 2.7046 | 2.7351
Forbes | 0.454 | 56.5781 | 56.9597 | 57.3224 | 57.6686 | 58.0005
Glen Innes | -0.94514 | 10.3562 | 10.6713 | 10.9695 | 11.2532 | 11.5243
Griffith | -0.7094 | 41.5622 | 42.4967 | 43.3805 | 44.221 | 45.024
Gunnedah 66kV | 0.98218 | 13.238 | 13.8019 | 14.3262 | 14.8182 | 15.2834
Hawks Nest | 1 | 0 | 0 | 0 | 0 | 0
Herons Ck | -0.97262 | 6.2742 | 6.7206 | 7.1391 | 7.5344 | 7.91
Inverell | -0.87588 | 30.8616 | 31.389 | 31.8912 | 32.3715 | 32.8325
Kempsey 33kV | 0.85823 | 13.4183 | 14.5328 | 15.5678 | 16.5381 | 17.4546
Koolkhan | -0.6838 | 26.0485 | 27.8248 | 29.4943 | 31.0743 | 32.5777
Lismore 132kV | -0.8562 | 59.0276 | 61.305 | 63.4425 | 65.4631 | 67.3842
Macksville | -0.99823 | 5.3447 | 5.7939 | 6.2107 | 6.6013 | 6.97
Manildra | -0.96737 | 44.4227 | 44.4561 | 44.4883 | 44.5194 | 44.5494
Marulan | 0.992 | 128.4944 | 129.7804 | 130.9809 | 132.1109 | 133.1817
Merbein | 1 | 0.27737 | 0.28644 | 0.29522 | 0.30375 | 0.31205
Mildura | 0.9958 | 4.3876 | 4.7438 | 5.0752 | 5.3862 | 5.6802
Molong | -0.98052 | 31.4024 | 31.5047 | 31.6011 | 31.6926 | 31.7798
Moree | -0.97809 | 67.4444 | 67.7528 | 68.0477 | 68.3307 | 68.6033
Morven | 1 | 2.4586 | 2.5704 | 2.6776 | 2.7807 | 2.88
Mudgee | -0.15797 | 8.1449 | 8.7783 | 9.369 | 9.9245 | 10.4506
Mullumbimby | 1 | 4.9273 | 5.2875 | 5.6248 | 5.9429 | 6.2448
Munyang | 0.83915 | 0.18851 | 0.2137 | 0.23622 | 0.25677 | 0.2758
Murrumbateman | -0.98108 | 4.0067 | 4.3246 | 4.6206 | 4.8988 | 5.162
Murrumburrah | 0.61901 | 11.3615 | 12.1687 | 12.9256 | 13.6405 | 14.3198
Nambucca | -0.78994 | 4.1992 | 4.5431 | 4.8627 | 5.1626 | 5.446
Narrabri | 0.31819 | 25.5651 | 26.011 | 26.4339 | 26.8371 | 27.223
Orange 132kV | 1 | 0 | 0 | 0 | 0 | 0
Orange 66kV | -0.84372 | 25.4022 | 27.733 | 29.8826 | 31.8876 | 33.7737
Panorama | 0.91288 | 29.3201 | 31.409 | 33.3375 | 35.1379 | 36.8327
Parkes 132kV | 1 | 0 | 0 | 0 | 0 | 0
Parkes 66kV | -0.95988 | 66.2974 | 66.7866 | 67.2487 | 67.6876 | 68.1067
Port Macquarie | 0.068622 | 37.7398 | 41.0601 | 44.1313 | 47.0022 | 49.7076
Queanbeyan 132kV | -0.87821 | 7.9558 | 8.8011 | 9.572 | 10.2853 | 10.9522
Queanbeyan 66kV | -0.31143 | 24.3865 | 26.4654 | 28.3908 | 30.1923 | 31.8912
Raleigh | -0.88775 | 5.1751 | 5.5652 | 5.9297 | 6.2731 | 6.5986
Robinvale | 0.97239 | 1.043 | 1.0653 | 1.0871 | 1.1086 | 1.1296
Snowy Adit | 1 | 0 | 0 | 0 | 0 | 0
Stroud | -0.55776 | 11.4145 | 12.2156 | 12.9671 | 13.6772 | 14.352
Tamworth | 0.99997 | 30.1559 | 32.4055 | 34.5087 | 36.491 | 38.3709
Taree 33kV | 0.034937 | 7.85 | 8.4511 | 9.0122 | 9.5403 | 10.0407
Taree 66kV | 0.9641 | 22.5721 | 24.5554 | 26.39 | 28.1052 | 29.7215
Tenterfield | -0.99118 | 2.0398 | 2.1608 | 2.2753 | 2.3844 | 2.4887
Terranora | 1 | 75.9189 | 79.4256 | 82.7213 | 85.84 | 88.8074
Tumut | 0.33858 | 15.3297 | 15.8113 | 16.2666 | 16.6994 | 17.1128
Upper Tumut | 0 | 0 | 0 | 0 | 0 | 0
Wagga 66kV | 0.98471 | 21.2693 | 23.1012 | 24.7981 | 26.3862 | 27.8839
Wagga North 132kV | -0.91427 | 220.8956 | 221.4851 | 222.0411 | 222.5687 | 223.0719
Wagga North 66kV | 0.99932 | 5.4611 | 5.9733 | 6.445 | 6.8844 | 7.2974
Waggamba | 1 | 0 | 0 | 0 | 0 | 0
Wallerawang 132kV | 1 | 0 | 0 | 0 | 0 | 0
Wallerawang 66kV | 0.77567 | 1.7966 | 1.9254 | 2.0462 | 2.1602 | 2.2685
Wellington 132kV | -0.8921 | 237.6612 | 237.6612 | 237.6612 | 237.6612 | 237.6612
Yanco | 0.19401 | 17.0617 | 17.5223 | 17.9578 | 18.372 | 18.7677
Yass 132kV | -0.97194 | 74.946 | 74.946 | 74.946 | 74.946 | 74.946
Yass 66kV | -0.9529 | 5.9098 | 6.2943 | 6.6566 | 7.0001 | 7.3276

## System Limitations
Feeder - Terranora - BPT3B3 Fingal
Feeder - Terranora - MWN3B2 Norco
Feeder - Terranora - MWN3B8 Uki
Feeder - Lismore - LHD3B5 Lennox West
Feeder - Lismore - WBN3B4 Broadwater
Feeder - Lismore - SLI3B23 Carrington St Nth
Feeder - Grafton - MLN3B5 Woodford Dale-Leigh
Feeder - Grafton - SGN3B1 Armidale Rd
Feeder - Kempsey - SWR3B6 Stuarts Pt
Feeder - Port Macquarie - BPM3B4 Hastings River Dr
Feeder - Port Macquarie - OPM3B1 Granite St
Feeder - Taree - BNK24787 Old Bar No.2
Feeder - Taree - HGN3B1 Crowdy Head
Feeder - Stroud - BLH3B2 Crawford/Girvan/Booral
Feeder - Hawks Nest - TEA3B4 Tea Gardens
Feeder - Armidale - GLS3B7 City Central
Feeder - Armidale - HGE3B1 Grafton Rd
Feeder - Glen Innes - GYA8K1 Wandsworth
Feeder - Inverell - BTS8B8 Delungra
Feeder - Tamworth - BBA3B4 Barraba
Feeder - Tamworth - STH3B11 Robert St
Feeder - Tamworth - STH3B6 Country Ln
Feeder - Dubbo - DBW3B5 Rural West
Feeder - Dubbo - EUL32 Dubbo Nth/East Town
Feeder - Dubbo - EUL62 Dubbo Sth/East Town
Feeder - Dubbo - GID22 Rural Nth/Sth/West
Feeder - Dubbo - GID42 Town No.2
Feeder - Orange - ORS3B2 Jeager Ave
Feeder - Orange - ORS3B7 Anson St Sth
Feeder - Orange - ORS3B8 Edward St
Feeder - Bathurst - BNY3B4 Millthorpe
Feeder - Bathurst - BTH3B3 Brilliant St
Feeder - Bathurst - RAG3B3 Raglan Industrial
Feeder - Parkes - PKT3B3 Telescope
Feeder - Parkes - PKT3B9 Parkes Town No.3
Feeder - Parkes - TDL8B1 Bogan Gate
Feeder - Parkes - TDL8B2 Tullamore/Tottenham
Feeder - Forbes - WJL3B2 Warroo
Feeder - Forbes - WJL3B3 West Plain
Feeder - Moruya North - MYT3B6 Moruya Nth
Feeder - Cooma - JYE3B2 Kalkite
Feeder - Bega - MAH3B3 Glebe
Feeder - Goulburn - CST5362 Sth Goulburn/Collector
Feeder - Goulburn - GBN3B4 Towrang
Feeder - Cowra - CWD13 Cargo
Feeder - Wagga (Copland St) - ASM3B4 Fernleigh Rd West
Feeder - Wagga (Copland St) - HAM3B7 Tarcutta St
Feeder - Albury - ALU8B10 Ettamogah
Feeder - Finley - FIN8B1 Tocumwal
Feeder - Coleambally - CLY1523 Coleambally 132 - Darlington Point (Bore Pumpers)
Feeder - Griffith - GFH3B2 Wakaden St
Feeder - Griffith - THA2225 Hillston Rd
Feeder - Yanco - LEE3B7 Corbie Hill
Subtransmission Line - Griffith - 79W Goolgowi
Substation - Lismore - Suffolk Park
Substation - Moree - Moree
Substation - Wagga North - Bomen

## Comments
A 30MW biomass generator is located at Condong and is connected to the Terranora 110/66kV sub-transmission substation at 66kV via feeders 9504, 9514 and 9502.
A 30MW biomass generator is located at Broadwater and is connected to the Lismore 132/66kV sub-transmission substation at 66kV via feeder 0892.
The Nymboida hydro generation has reached end of life so has been decommissioned.
The 5MW hydro generation at Oaky is presently decommissioned after failure of the dam wall.
A 5MW solar generator is connected to Galloway St zone substation on the 11kV network.
A 5.5MW hydro generator is located at Pindari Dam and is connected to the Transgrid Glen Innes 132/66kV sub-transmission substation at 66kV via feeders 6AE, 6NE, 886 and 887.
A 23MW hydro generator is located at Copeton Dam and is connected to the Transgrid Inverell 132/66kV sub-transmission substation at 66kV via feeders 6BC, 734 and 735.
A 56MW solar generator is located at Moree Solar Farm and is connected to Transgrid’s Moree 132/66kV sub-transmission substation at 66kV via feeder 876.
A 5MW solar generator is located at Wenna on the 22kV network.
A 5MW solar generator is located at Wathagar on the 22kV network.
A 10MW and 6MW gas generator located at Wilga Park is connected to the Transgrid Narrabri 132/66kV sub-transmission substation at 66kV via feeder 861.
A 7MW hydro generator is located at Lake Keepit and is connected to the Transgrid Gunnedah 132/66kV sub-transmission substation at 66kV via feeder 877.
A 9.2MW solar generator is located at Narromine on the 22kV network, and a 14.5MW solar generator is connected at Dubbo South on the 11kV network.
A 105MW solar generator is located at Nevertire and is connected to the Dubbo 132/66kV sub-transmission substation at 132kV via the feeder 94W.
A 5MW solar generator is located at Nyngan Town on the 22kV network.
A 102MW solar generator is located at Nyngan Solar Farm and is connected to the Nyngan 132/66kV sub-transmission substation at 132kV via the feeder 9UT.
A 53MW solar generator is located at Broken Hill and is connected to the Transgrid Broken Hill 220/22kV sub-transmission substation at 22kV.
There have been changes to the water pump network with a new water supply now coming from Wentworth. It is unclear what the long-term configuration will be for the existing water pump infrastructure and whether it will affect peak loads.
A 46.7MW solar generator is located at Manildra on the 11kV network.
A 10MW wind generator is located at Blayney wind farm and is connected to the Transgrid Panorama 132/66kV sub-transmission substation at 66kV via feeders 66:MAN and 81C.
A 4.99MW solar generator is located at Peak Hill on the 11kV network, and a 4.99MW solar generator is located at Trundle on the 22kV network.
A 50MW solar generator is located at West Jemalong and is connected to the Transgrid Forbes 132/66kV sub-transmission substation at 66kV via the feeder 89R.
A 3MW solar thermal generator is located at Lake Cargelligo on the 22kV network, and a 1.1MW solar thermal generator is located at West Jemalong on the 11kV network.
A 5MW hydro generator is located at Brown Mountain Hydro and is connected to Steeple Flat 132/66kV sub-transmission substation at 66kV via feeder 810.
A 114MW wind generator is located at Boco Rock wind farm and is connected to the Steeple Flat 132/66kV sub-transmission substation which is connected to Transgrid’s Cooma 132/66kV sub-transmission substation at 132kV via the feeder 97R.
A 1MW hydro generator is located at Jindabyne Dam and is connected to the Jindabyne zone substation 11kV busbar via feeder JIN22.
Lines 849/2 and 849/3 sustained bushfire damage so are not currently in service. More information is contained in 4.3 Urgent and Unforeseen Investments.
A 15MW hydro generator is located at Jounama Dam and is connected to the Transgrid Tumut 132/66kV sub-transmission substation at 66kV via feeder 850:TAL.
A 7MW biomass generator is located at Woodlawn Bioreactor and is connected to the Woodlawn 66/11kV zone substation at 11kV via feeder WOO8642.
A 5MW wind generator is located at Crookwell wind farm and is connected to the Goulburn 132/66kV sub-transmission substation at 66kV via feeders 841:GBN and 840:GOU.
A 107MW wind generator is located at Taralga wind farm and is connected to the Transgrid Marulan 330/132kV sub-transmission substation at 132kV via feeder 9UR.
A 22.5MW hydro generator is located at Wyangala Dam and is connected to the Transgrid Cowra 132/66kV sub-transmission substation at 66kV via feeder 891.
A 30MW wind generator is located at Cullerin Range wind farm and is connected to the Transgrid Yass 330/132/66kV sub-transmission substation at 132kV via feeder 971.
A 47MW wind generator is located at Gunning wind farm and is also connected to the Transgrid Yass 330/132/66kV sub-transmission substation at 132kV via feeder 971.
There are multiple load transfer points in the Yass area to other zone substations that can be utilised with the loss of a single Yass transformer.
A 90MW solar generator is located at Sebastopol and is connected to the Transgrid Wagga North 132/66kV sub-transmission substation at 132kV via feeder 99U.
A 90MW solar generator is located at West Wyalong and is connected to the Temora 132/66kV sub-transmission substation at 132kV via feeder 9JW.
A 53MW solar generator is located at Wyalong and is connected to the Temora 132/66kV sub-transmission substation at 132kV via feeder 901.
A 30MW solar generator is located at Junee on the 11kV network.
A 30MW solar thermal generator is located at Corowa on the 22kV network.
A 5MW solar generator is located at Mulwala on the 22kV network.
A 2.5MW hydro generator is located at The Drop and is connected to the Finley 66/22kV zone substation at 22kV via feeder FIN42.
An 85MW solar generator is located at Hillston and is connected to the Hillston 132/66kV sub-transmission substation at 132kV via feeder 9JY.
A 5MW solar generator is located near Egansford and is connected to the Coleambally 132/33kV sub-transmission substation at 33kV via feeder CLY4B4.
Two 5MW solar generators are located near Leeton and are connected to the Yanco 132/33kV sub-transmission substation at 33kV via feeder 7L2.
A 3.3MW solar generator is located at Dareton on the 22kV network.