## AER_NOM_annual_data
asset_name | asset_code | exclude_from_capacity_layers | network | network_element | use_5yr_forecast | voltage_highside | voltage_lowside | investment_description | reliability_criteria | latitude | longitude | latitude_end | longitude_end | res_cust_affected_no | res_cust_affected_percent | primary_driver | augmentation_invest | replacement_invest | connections_invest | other_invest | total_invest | cost_accuracy_plus | cost_accuracy_minus | annual_deferral | deferrable_invest | opex | project_timing | commitment_timing | summer_critical | winter_critical | spring_critical | autumn_critical | summer_nameplate_cap_mva | summer_secure_cap_mva | summer_acc_cap_yr_minus2_mva | summer_acc_cap_yr_minus1_mva | summer_acc_cap_yr0_mva | summer_acc_cap_yr1_mva | summer_acc_cap_yr2_mva | summer_acc_cap_yr3_mva | summer_acc_cap_yr4_mva | summer_acc_cap_yr5_mva | summer_acc_cap_yr6_mva | summer_acc_cap_yr7_mva | summer_acc_cap_yr8_mva | summer_acc_cap_yr9_mva | summer_acc_cap_yr10_mva | summer_load_yr1_poe50_mva | summer_load_yr2_poe50_mva | summer_load_yr3_poe50_mva | summer_load_yr4_poe50_mva | summer_load_yr5_poe50_mva | summer_load_yr6_poe50_mva | summer_load_yr7_poe50_mva | summer_load_yr8_poe50_mva | summer_load_yr9_poe50_mva | summer_load_yr10_poe50_mva | summer_load_yr1_poe10_mva | summer_load_yr2_poe10_mva | summer_load_yr3_poe10_mva | summer_load_yr4_poe10_mva | summer_load_yr5_poe10_mva | summer_load_yr6_poe10_mva | summer_load_yr7_poe10_mva | summer_load_yr8_poe10_mva | summer_load_yr9_poe10_mva | summer_load_yr10_poe10_mva | winter_nameplate_cap_mva | winter_secure_cap_mva | winter_acc_cap_yr_minus2_mva | winter_acc_cap_yr_minus1_mva | winter_acc_cap_yr0_mva | winter_acc_cap_yr1_mva | winter_acc_cap_yr2_mva | winter_acc_cap_yr3_mva | winter_acc_cap_yr4_mva | winter_acc_cap_yr5_mva | winter_acc_cap_yr6_mva | winter_acc_cap_yr7_mva | winter_acc_cap_yr8_mva | winter_acc_cap_yr9_mva | winter_acc_cap_yr10_mva | winter_load_yr1_poe50_mva | winter_load_yr2_poe50_mva | winter_load_yr3_poe50_mva | winter_load_yr4_poe50_mva | winter_load_yr5_poe50_mva | winter_load_yr6_poe50_mva | winter_load_yr7_poe50_mva | winter_load_yr8_poe50_mva | winter_load_yr9_poe50_mva | winter_load_yr10_poe50_mva | winter_load_yr1_poe10_mva | winter_load_yr2_poe10_mva | winter_load_yr3_poe10_mva | winter_load_yr4_poe10_mva | winter_load_yr5_poe10_mva | winter_load_yr6_poe10_mva | winter_load_yr7_poe10_mva | winter_load_yr8_poe10_mva | winter_load_yr9_poe10_mva | winter_load_yr10_poe10_mva | mapped_poe | load_at_risk_yr1_mw | load_at_risk_yr2_mw | load_at_risk_yr3_mw | load_at_risk_yr4_mw | load_at_risk_yr5_mw | EUSE_MWh_yr1 | EUSE_MWh_yr2 | EUSE_MWh_yr3 | EUSE_MWh_yr4 | EUSE_MWh_yr5 | EUSE_MWh_yr6 | EUSE_MWh_yr7 | EUSE_MWh_yr8 | EUSE_MWh_yr9 | EUSE_MWh_yr10 | hrs_exceedance_yr1 | hrs_exceedance_yr2 | hrs_exceedance_yr3 | hrs_exceedance_yr4 | hrs_exceedance_yr5 | hrs_exceedance_yr6 | hrs_exceedance_yr7 | hrs_exceedance_yr8 | hrs_exceedance_yr9 | hrs_exceedance_yr10 | EUSE_value_yr1 | EUSE_value_yr2 | EUSE_value_yr3 | EUSE_value_yr4 | EUSE_value_yr5 | EUSE_value_yr6 | EUSE_value_yr7 | EUSE_value_yr8 | EUSE_value_yr9 | EUSE_value_yr10 | summer_support_constraintyr_mw | summer_support_constraintyr_mva | summer_support_yr1_mva | summer_support_yr2_mva | summer_support_yr3_mva | summer_support_yr4_mva | summer_support_yr5_mva | summer_support_yr6_mva | summer_support_yr7_mva | summer_support_yr8_mva | summer_support_yr9_mva | summer_support_yr10_mva | winter_support_constraintyr_mw | winter_support_constraintyr_mva | winter_support_yr1_mva | winter_support_yr2_mva | winter_support_yr3_mva | winter_support_yr4_mva | winter_support_yr5_mva | winter_support_yr6_mva | winter_support_yr7_mva | winter_support_yr8_mva | winter_support_yr9_mva | winter_support_yr10_mva | power_factor | reactive_support_details | load_transfer_capability_mva | emergency_generation_mva | emergency_generation_mw | historic_emergency_generation_flag | connected_region1 | connected_region1_EF | connected_region2 | connected_region2_EF | connected_region3 | connected_region3_EF | connected_region4 | connected_region4_EF | connected_region5 | connected_region5_EF | connected_region6 | connected_region6_EF | connected_region7 | connected_region7_EF | connected_region8 | connected_region8_EF | connected_region9 | connected_region9_EF | connected_region10 | connected_region10_EF | connected_region11 | connected_region11_EF | connected_region12 | connected_region12_EF | connected_region13 | connected_region13_EF | connected_region14 | connected_region14_EF | connected_region15 | connected_region15_EF | connected_region16 | connected_region16_EF | connected_region17 | connected_region17_EF | connected_region18 | connected_region18_EF | connected_region19 | connected_region19_EF | connected_region20 | connected_region20_EF | connected_region21 | connected_region21_EF | connected_region22 | connected_region22_EF | connected_region23 | connected_region23_EF | connected_region24 | connected_region24_EF | connected_region25 | connected_region25_EF | connected_region26 | connected_region26_EF | connected_region27 | connected_region27_EF | connected_region28 | connected_region28_EF | connected_region29 | connected_region29_EF | connected_region30 | connected_region30_EF | template_version_v3.1
| ORS3B2 Jeager Ave |  |  | DF |  | 11 |  | Project will install a switching station in Churchill Avenue adjacent to Electrolux so that the unutilised ORS3B3 Feeder can be used to back up ORS3B8 Edward Street and ORS3B5 Lords Place for network reliability |  | -33.2963 | 149.1027 | -33.2963 | 149.1027 | 736 | 1 | Reliability | 251707 |  |  |  | 251707 | 0.1 | 0.1 | 18405 |  | 5034 | 06/2025 | [7 empty] | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | [15 empty] | 3.02 | 3.06 | 3.09 | 3.12 | 3.15 | [7 empty] | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | [15 empty] | 3.02 | 3.06 | 3.09 | 3.12 | 3.15 | [6 empty] | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | 2.28 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 3.7 | 0 |  | No
| ORS3B3 Email (Electrolux) |  |  | DF |  | 11 |  | Orange Install 3 way switching station |  | -33.3037 | 149.0978 | -33.3037 | 149.0978 | 988 | 1 | Reliability | 203709 |  |  |  | 203709 | 0.1 | 0.1 | 14896 |  | 4074 | 06/2024 | [7 empty] | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | [15 empty] | 0 | 0 | 0 | 0 | 0 | [7 empty] | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | [15 empty] | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| ORS3B5 Lords Place |  |  | DF |  | 11 |  | Millthorpe-BurtonsLn&WilsonsLn-HVReconductoring-Refurb |  | -33.4459 | 149.1022 | -33.4859 | 149.0682 | 1120 | 0.16 | Asset Condition |  | 276936 |  |  | 276936 | 0.1 | 0.1 | 20250 |  | 5539 | 07/2024 | [7 empty] | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | [15 empty] | 3.21 | 3.24 | 3.28 | 3.31 | 3.35 | [7 empty] | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | [15 empty] | 3.21 | 3.24 | 3.28 | 3.31 | 3.35 | [6 empty] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 1.33 | 0 |  | No
| BNY3B4 Millthorpe |  |  | DF |  | 11 |  | Bathurst supply constraints BTH3B7 Llyods Rd Feeder |  | -33.4419 | 149.5689 | -33.4612 | 149.5716 | 141 | 0.8 | Capacity | 251258 |  |  |  | 251258 | 0.1 | 0.1 | 18373 |  | 5025 | 06/2025 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [6 empty] | 2.74 | 2.7 | 2.7 | 2.7 | 2.7 | 2.74 | 2.7 | 2.7 | 2.7 | 2.7 | [26 empty] | 1.6 | [11 empty] | 1.6 | [10 empty] | 0.95 |  | 0.48 | 0 |  | No
| BTH3B8 Lagoon/Trunkey |  |  | DF |  | 11 |  | Bathurst voltage constraints Raglan 3B3 |  | -33.4264 | 149.72 | -33.4278 | 149.7535 | 267 | 0.26 | Voltage | 200504 |  |  |  | 200504 | 0.1 | 0.1 | 14661 |  | 4010 | 06/2024 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.5 | [11 empty] | 0.5 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| BNY3B4 Millthorpe |  |  | DF |  | 22 |  | Berrigan, Tocumwal FIN8B1 upgrade regulator 62-V602 to 300A & install additional recloser north of Fullers Rd Finley . |  | -35.7078 | 145.5776 | -35.8785 | 145.6596 | 1927 | 1 | Capacity | 598481 |  |  |  | 598481 | 0.1 | 0.1 | 43762 |  | 11970 | 06/2025 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 2.91 | 2.94 | 2.96 | 2.98 | 3.01 | [6 empty] | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| RAG3B6 Limekilns |  |  | DF |  | 22 |  | Albury, Catherine Cres, sub 61-50317 replace failed HV ring main switch & damaged HV cable, def Rec |  | -36.0414 | 146.9651 | -36.0419 | 146.9626 | 941 | 1 | Asset Condition |  | 316713 |  |  | 316713 | 0.1 | 0.1 | 23159 |  | 6334 | 06/2024 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 3.06 | 3.08 | 3.09 | 3.1 | 3.12 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 3.06 | 3.08 | 3.09 | 3.1 | 3.12 | [6 empty] | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| SWT42 Simplot |  |  | DF |  | 22 |  | Install a new 22kV line along Dandaloo Rd. |  | -32.375 | 147.4872 | -32.2606 | 147.6244 | 856 | 0.6 | Reliability | 1784443 |  |  |  | 1784443 | 0.1 | 0.1 | 130482 |  | 35689 | 06/2025 | [7 empty] | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | [15 empty] | 5.82 | 5.9 | 5.96 | 6.04 | 6.15 | [7 empty] | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | [15 empty] | 5.82 | 5.9 | 5.96 | 6.04 | 6.15 | [6 empty] | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.991 |  | 0.5 | 0 |  | No
| BTH3B7 Lloyds Rd |  |  | DF |  | 11 |  | Parkes Porter St Replace failed LV cables |  | -33.1453 | 148.178 | -33.1465 | 148178685 | 2054 | 0.01 | Asset Condition |  | 564270 |  |  | 564270 | 0.1 | 0.1 | 41261 |  | 11285 | 06/2025 | [7 empty] | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | [15 empty] | 3.87 | 3.87 | 3.87 | 3.86 | 3.86 | [7 empty] | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | [15 empty] | 3.87 | 3.87 | 3.87 | 3.86 | 3.86 | [6 empty] | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| BTH3B6 City Central |  |  | DF |  | 11 |  | Reedy Swamp Reedy Swamp Rd Replace 6km in poor condition 7/0.064 SC/GZ. |  | -36.679 | 149.8724 | -36.7015 | 149.8838 | 1549 | 0.03 | Asset Condition |  | 284493 |  |  | 284493 | 0.1 | 0.1 | 20803 |  | 5690 | 06/2024 | [7 empty] | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | [15 empty] | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | [7 empty] | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | [15 empty] | 1.99 | 1.99 | 1.99 | 1.99 | 1.99 | [6 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| FIN8B1 Tocumwal |  |  | DF |  | 22 |  | Bogan Gate Henry Parkes Way Replace failing HDBC conductor. |  | -33.1098 | 147.761 | -33.1141 | 147.6888 | 203 | 0.09 | Asset Condition |  | 283687 |  |  | 283687 | 0.1 | 0.1 | 20744 |  | 5674 | 06/2025 | [7 empty] | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | [15 empty] | 5.36 | 5.38 | 5.38 | 5.39 | 5.39 | [7 empty] | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | [15 empty] | 5.36 | 5.38 | 5.38 | 5.39 | 5.39 | [6 empty] | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | 5.14 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| MWA8B4 North St and Rural |  |  | DF |  | 22 |  | Tullamore Switching Station Upgrade Feeder Protection on 11kV Network |  | -32.6528 | 147.5816 | -32.654 | 147.5808 | 856 | 1 | Reliability |  | 219269 |  |  | 219269 | 0.1 | 0.1 | 16033 |  | 4385 | 06/2025 | [7 empty] | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | [15 empty] | 2 | 2 | 2 | 2 | 2.02 | [7 empty] | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | [15 empty] | 2 | 2 | 2 | 2 | 2.02 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.991 |  | 0 | 0 |  | No
| CRA42 Corurgan |  |  | DF |  | 11 |  | Goonumbla Wards Ln Replace faulty conductor |  | -32.9715 | 148.1658 | -32.9828 | 148.222 | 945 | 0.01 | Asset Condition |  | 214002 |  |  | 214002 | 0.1 | 0.1 | 15648 |  | 4280 | 06/2025 | [7 empty] | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | [15 empty] | 3.19 | 3.2 | 3.2 | 3.2 | 3.22 | [7 empty] | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | [15 empty] | 3.19 | 3.2 | 3.2 | 3.2 | 3.22 | [6 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| HOL1890 Wantagong/Woomargama |  |  | DF |  | 11 |  | Moruya Phyllis Price Dr Replace 31-V1471 with Coopers Regs |  | -35.877 | 150.1178 | -35.877 | 150.1178 | 1233 | 0.03 | Asset Condition |  | 205697 |  |  | 205697 | 0.1 | 0.1 | 15041 |  | 4114 | 06/2025 | [7 empty] | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | [15 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.86 | [7 empty] | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | [15 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.86 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 2 | 0 |  | No
| BOM8B2 Nimmitabel |  |  | DF |  | 11 |  | New 11kV feeder as a dedicated supply to Berridale township, freeing up existing feeder as a dedicated supply for Kalkite |  | -36.39 | 148.6719 | -36.3637 | 148.7282 | 1159 | 1 | Capacity | 712398 |  |  |  | 712398 | 0.2 | 0.2 | 52092 |  | 14248 | 06/2025 | [7 empty] | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | [15 empty] | 0.28 | 0.29 | 0.29 | 0.29 | 0.29 | [7 empty] | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | [15 empty] | 0.28 | 0.29 | 0.29 | 0.29 | 0.29 | [6 empty] | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | 0.25 | 0.26 | 0.26 | 0.26 | 0.26 | [26 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  | 0.45 | 0 |  | No
| JYE3B2 Kalkite |  |  | DF |  | 11 |  | Replace failing Quince conductor with Raisin |  | -34.8278 | 149.5594 | -34.8794 | 149.5278 | 2390 | 0.01 | Asset Condition |  | 321532 |  |  | 321532 | 0.1 | 0.1 | 23511 |  | 6430 | 06/2024 | [7 empty] | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | [15 empty] | 2.76 | 2.82 | 2.87 | 2.93 | 3 | [7 empty] | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | [15 empty] | 2.76 | 2.82 | 2.87 | 2.93 | 3 | [6 empty] | 2 | 2.5 | 3 | 3.5 | 3.5 | 2 | 2.5 | 3 | 3.5 | 3.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| ADE22 Rural West |  |  | DF |  | 22 |  | Replace failing Quince conductor and install 2 reclosers to improve reliability |  | -34.7295 | 149.8226 | -34.6929 | 149.852 | 656 | 0.14 | Asset Condition |  | 290087 |  |  | 290087 | 0.1 | 0.1 | 21212 |  | 5801 | 11/2024 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.47 | 0.47 | 0.47 | 0.47 | 0.48 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.47 | 0.47 | 0.47 | 0.47 | 0.48 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| MTG4B1 Tibooburra Backbone Line |  |  | DF |  | 11 |  | Reconductor from 2454 084 to reclosers 70-R80 and 70-R382 with Flourine. |  | -33.399 | 148.6091 | -33.3575 | 148.6091 | 706 | 0.12 | Voltage | 370000 | 170000 |  |  | 540000 | 0.1 | 0.1 | 39486 |  | 10800 | 06/2025 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.34 | 1.36 | 1.38 | 1.4 | 1.4 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.34 | 1.36 | 1.38 | 1.4 | 1.4 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0.05 | [11 empty] | 0.05 | [10 empty] | 1 |  | 0.1 | 0 |  | No
| TDL8B2 Tullamore/Tottenham |  |  | DF |  | 22 |  | Relocate Step up transformer and 22 to 11kV conversion |  | -33.3808 | 147.6616 | -33.5472 | 147.656 | 179 | 1 | Reliability | 373774 |  |  |  | 373774 | 0.1 | 0.1 | 27331 |  | 7475 | 06/2025 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [6 empty] | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| YAS6242 Yass Town Sth |  |  | DF |  | 11 |  | Replacement of 7/064HDCU mainline conductor |  | -33.3625 | 147.6728 | -33.3211 | 147.5892 | 101 | 1 | Asset Condition |  | 336973 |  |  | 336973 | 0.1 | 0.1 | 24640 |  | 6739 | 07/2023 | [7 empty] | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | [15 empty] | 4.43 | 4.46 | 4.49 | 4.52 | 4.57 | [7 empty] | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | [15 empty] | 4.43 | 4.46 | 4.49 | 4.52 | 4.57 | [6 empty] | 0.06 | 0.1 | 0.06 | 0.06 | 0.06 | 0.06 | 0.1 | 0.06 | 0.06 | 0.06 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| WGN72 Yeoval |  |  | DF |  | 33 |  | Upgrade Darlington Pt Farms CLY1523 Bore Pumpers 33kV tie ( Griffith Network) OH Conductors |  | -34.6199 | 145.9018 | -34.5486 | 145.9097 | 55 | 0.56 | Capacity | 619083 |  |  |  | 619083 | 0.1 | 0.1 | 45269 |  | 12381 | 06/2025 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [6 empty] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| TDL8B2 Tullamore/Tottenham |  |  | DF |  | 11 |  | Griffith Whites Rd Reconductor 4km |  | -34.2642 | 146.0005 | -34.2497 | 145.9731 | 261 | 0.25 | Asset Condition |  | 339002 |  |  | 339002 | 0.1 | -0.1 | 24789 |  | 6780 | 06/2025 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 2.09 | 2.07 | 2.08 | 2.1 | 2.14 | [6 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| PKT3B9 Parkes Town No.3 |  |  | DF |  | 11 |  | Griffith KoobaBetts 96-797 LV Encroachment(West) |  | -34.2791 | 146.0436 | -34.2791 | 146.043 | 1027 | 0.01 | Safety | 216749 |  |  |  | 216749 | 0.1 | 0.1 | 15849 |  | 4334 | 06/2025 | [7 empty] | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | [15 empty] | 5.01 | 5.05 | 5.09 | 5.11 | 5.11 | [7 empty] | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | [15 empty] | 5.01 | 5.05 | 5.09 | 5.11 | 5.11 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| WJL3B3 West Plain |  |  | DF |  | 22 |  | Leeton Corbie Hill Payten Rd Reconductor cu 4.5km |  | -34.5577 | 146.4586 | -34.5942 | 146.4719 | 799 | 0.15 | Voltage | 211210 |  |  |  | 211210 | 0.1 | 0.1 | 15444 |  | 4224 | 06/2025 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.78 | 0.78 | 0.78 | 0.78 | 0.77 | [7 empty] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | [15 empty] | 0.78 | 0.78 | 0.78 | 0.78 | 0.77 | [6 empty] | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| CMK4005 West |  |  | DF |  | 11 |  | Relocate Padmount Sub - Wagga Depot Hammond Ave |  | -35.12 | 147.384 | -35.12 | 147.384 | 296 | 1 | Asset Condition |  | 341000 |  |  | 341000 | 0.1 | 0.1 | 24935 |  | 6823 | 06/2025 | [7 empty] | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | [15 empty] | 0.42 | 0.42 | 0.43 | 0.43 | 0.43 | [7 empty] | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | [15 empty] | 0.42 | 0.42 | 0.43 | 0.43 | 0.43 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| THA2223 West End |  |  | DF |  | 11 |  | LV UG Replacement CONSAC - 71-3456, Adams St Ashmont - Wagga |  | -35.1232 | 147.3215 | -35.1232 | 147.3215 | 1258 | 1 | Asset Condition |  | 247000 |  |  | 247000 | 0.1 | 0.1 | 18061 |  | 4951 | 06/2024 | [7 empty] | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | [15 empty] | 3.41 | 3.43 | 3.44 | 3.45 | 3.45 | [7 empty] | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | [15 empty] | 3.41 | 3.43 | 3.44 | 3.45 | 3.45 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| GFH3B2 Wakaden St |  |  | DF |  | 11 |  | Orange cable replacements Orange South Zone Feeders 10000924 |  | -33.2982 | 149.096 | -33.2984 | 149.0918 | 2412 | 1 | Asset Condition |  | 765314 |  |  | 765314 | 0.1 | 0.1 | 55961 |  | 15306 | 06/2025 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| GFH3B6 Illilliwa |  |  | DF |  | 11 |  | Tamworth, New Winton Rd, Old 66kV structures operating at 11kV |  | -31.093 | 150.845 | -31.0876 | 150.8215 | 33 | 1 | Asset Condition |  | 408829 |  |  | 408829 | 0.1 | 0.1 | 29894 |  | 8177 | 06/2024 | [7 empty] | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | [15 empty] | 4.14 | 4.12 | 4.14 | 4.12 | 4.09 | [7 empty] | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | [15 empty] | 4.14 | 4.12 | 4.14 | 4.12 | 4.09 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| BEE1347 Collina No.1 |  |  | DF |  | 11 |  | Barraba Woodsreef 614614 Asbestos |  | -30.3987 | 150.7282 | -30.3987 | 150.73 | 810 | 0.026 | Safety |  | 306352 |  |  | 306352 | 0.1 | 0.1 | 22401 |  | 6127 | 06/2025 | [7 empty] | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | [15 empty] | 3.86 | 3.94 | 4.04 | 4.11 | 4.17 | [7 empty] | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | 5.95 | [15 empty] | 3.86 | 3.94 | 4.04 | 4.11 | 4.17 | [6 empty] | 3.66 | 3.75 | 3.84 | 3.91 | 3.96 | 3.66 | 3.75 | 3.84 | 3.91 | 3.96 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| GFH3B2 Wakaden St |  |  | DF |  | 11 |  | Tamworth Links Ave 18-15760 LV Consac End of Life |  | -31.1088 | 150.9077 | -31.1088 | 150.9077 | 1493 | 0.023 | Asset Condition |  | 249411 |  |  | 249411 | 0.1 | 0.1 | 18237 |  | 4988 | 06/2024 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [7 empty] | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | 3.76 | [15 empty] | 2.43 | 2.42 | 2.43 | 2.42 | 2.4 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| KOO3B1 Plumpton Rd |  |  | DF |  | 22 |  | Inverell MT Russel Rd 30201248 to 30201460 Asset Condition |  | -29.6904 | 150.9419 | -29.6725 | 150.9013 | 706 | 0.092 | Asset Condition | 248616 |  |  |  | 248616 | 0.1 | 0.1 | 18179 |  | 4972 | 06/2025 | [7 empty] | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | [15 empty] | 4.22 | 4.27 | 4.35 | 4.39 | 4.4 | [7 empty] | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | 2.03 | [15 empty] | 4.22 | 4.27 | 4.35 | 4.39 | 4.4 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| ASM3B9 Ashmont Sth |  |  | DF |  | 22 |  | Inverell Gum Flat 30200535 to 30200616 Asset Condition |  | -29.7798 | 150.9836 | -29.7798 | 150.9836 | 706 | 0.147 | Asset Condition |  | 245446 |  |  | 245446 | 0.1 | 0.1 | 17948 |  | 4909 | 06/2025 | [7 empty] | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | [15 empty] | 2.67 | 2.66 | 2.68 | 2.7 | 2.73 | [7 empty] | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | 3.04 | [15 empty] | 2.67 | 2.66 | 2.68 | 2.7 | 2.73 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| HAM3B7 Tarcutta St |  |  | DF |  | 11 |  | UG - Create 11 kV link Spinifex Ave Tea Gardens 88-82432, 1600 m |  | -32.6512 | 152.1487 | -32.6608 | 152.1375 | 1295 | 0.309 | Reliability | 809947 |  |  |  | 809947 | 0.1 | 0.1 | 59225 |  | 16199 | 06/2025 | [7 empty] | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | [15 empty] | 1.63 | 1.66 | 1.69 | 1.72 | 1.75 | [7 empty] | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | 4.17 | [15 empty] | 1.63 | 1.66 | 1.69 | 1.72 | 1.75 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| TAL1414 Talbingo Town |  |  | DF |  | 11 |  | Old Bar Wyden St 29751 Cable Replacement Growth Thermal |  | -31.9734 | 152.5793 | -31.9678 | 152.5804 | 1132 | 0.443 | Capacity | 350272 |  |  |  | 350272 | 0.1 | 0.1 | 25613 |  | 7005 | 06/2025 | [7 empty] | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | [15 empty] | 0.57 | 0.59 | 0.61 | 0.62 | 0.64 | [7 empty] | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | [15 empty] | 0.57 | 0.59 | 0.61 | 0.62 | 0.64 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 0.7 | [11 empty] | 0.7 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| ORS3B7 Anson St Sth |  |  | DF |  | 11 |  | Markwell Newells Creek HV Augmentation Encroachment |  | -32.2909 | 152.1754 | -32.2933 | 152.1749 | 177 | 0.661 | Safety |  | 343998 |  |  | 343998 | 0.1 | 0.1 | 25154 |  | 6880 | 06/2025 | [7 empty] | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | [15 empty] | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | [7 empty] | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | 7.94 | [15 empty] | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | [6 empty] | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | 4.96 | 5.01 | 5.07 | 5.12 | 5.18 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| RAG3B5 OConnell |  |  | DF |  | 11 |  | Harrington Bungulla Place CONSAC replacement EOL |  | -31.8725 | 152.6816 | -31.8712 | 152.6803 | 1033 | 0.042 | Asset Condition |  | 325367 |  |  | 325367 | 0.1 | 0.1 | 23792 |  | 6507 | 06/2025 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.53 | 1.54 | 1.55 | 1.56 | 1.56 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.53 | 1.54 | 1.55 | 1.56 | 1.56 | [6 empty] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| DNO132 Dunedoo No.1 |  |  | DF |  | 11 |  | Armidale Rologas Flats Sub 16-1466 End of Life |  | -30.5144 | 151.6688 | -30.5144 | 151.6688 | 774 | 0.068 | Asset Condition |  | 525742 |  |  | 525742 | 0.1 | 0.1 | 38443 |  | 10515 | 06/2024 | [7 empty] | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | [15 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | [15 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| ETH3B7 TCC/Calala |  |  | DF |  | 11 |  | Armidale, Rokvale North, 16-R12142, HV Reconductor. |  | -30.3088 | 152.0261 | -30.324 | 152.107 | 207 | 0.087 | Reliability |  | 429480 |  |  | 429480 | 0.1 | 0.1 | 31405 |  | 8590 | 06/2025 | [7 empty] | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | [15 empty] | 6.4 | 6.4 | 6.5 | 6.4 | 6.4 | [7 empty] | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | [15 empty] | 6.4 | 6.4 | 6.5 | 6.4 | 6.4 | [6 empty] | 4.8 | 4.85 | 4.9 | 4.95 | 4.99 | 4.8 | 4.85 | 4.9 | 4.95 | 4.99 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| GDH8B15 Sth Gunnedah |  |  | DF |  | 11 |  | Lismore Winterton and Alexandra Pde OH - Reconduct HV |  | -28.802 | 153.2757 | -28.7891 | 153.2892 | 930 | 1 | Asset Condition |  | 322226 |  |  | 322226 | 0.1 | 0.1 | 23562 |  | 6445 | 06/2025 | [7 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [15 empty] | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | [7 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [15 empty] | 0.6 | 0.62 | 0.64 | 0.66 | 0.68 | [6 empty] | 0.59 | 0.61 | 0.63 | 0.65 | 0.67 | 0.59 | 0.61 | 0.63 | 0.65 | 0.67 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WCK516 Dewhurst/Gordon |  |  | DF |  | 22 |  | Guyra, Tenterden Rd, HV Reco, Riliability, EOL |  | -30.1195 | 151.5102 | -33.3037 | 149.0978 | 156 | 0.385 | Reliability |  | 285925 |  |  | 285925 | 0.1 | 0.1 | 20907 |  | 5719 | 06/2025 | [7 empty] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | [15 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [7 empty] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | [15 empty] | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | [6 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| BBA3B4 Barraba |  |  | DF |  | 11 |  | Murwillumbah Buchanan St create HV interconnector MWN3B2/9 |  | -28.3389 | 153.4191 | -28.3373 | 153.4094 | 1101 | 1 | Capacity | 386455 |  |  |  | 386455 | 0.1 | 0.1 | 28258 |  | 7729 | 06/2025 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [15 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [15 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [6 empty] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | [26 empty] | 3 | [11 empty] | 3 | [10 empty] | 0.9 |  | 3 | 0 |  | No
| ATA3B1 Attunga |  |  | DF |  | 11 |  | Tweed Heads South Alf Rush Memorial Dr Sub 54-212 EOL Chamber sub replacement |  | -28.2089 | 153.5592 | -28.2089 | 153.5592 | 1968 | 0.001 | Asset Condition |  | 349243 |  |  | 349243 | 0.1 | 0.1 | 25537 |  | 6985 | 06/2025 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [6 empty] | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| BGA2K13 Horton Valley |  |  | DF |  | 11 |  | Kunghur Kyogle Rd 6.4km 11kV Reconductor Reliability |  | -28.4909 | 153.2177 | -28.4654 | 153.2657 | 2132 | 0.077 | Asset Condition |  | 301257 |  |  | 301257 | 0.1 | 0.1 | 22029 |  | 6025 | 06/2025 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 0.37 | 0.37 | 0.37 | 0.38 | 0.38 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 0.37 | 0.37 | 0.37 | 0.38 | 0.38 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| MRE8B4 Western Rural |  |  | DF |  | 11 |  | Lawrence River Crossing Pole 74700 End Of Life |  | -29.4916 | 153.1172 | -29.4916 | 153.1172 | 857 | 0.9 | Safety |  | 261415 |  |  | 261415 | 0.1 | 0.1 | 19115 |  | 5228 | 06/2025 | [7 empty] | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | [15 empty] | 4.02 | 4.13 | 5.7 | 6.29 | 5.57 | [7 empty] | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | [15 empty] | 4.02 | 4.13 | 5.7 | 6.29 | 5.57 | [6 empty] | 3.9 | 4 | 5.6 | 6.2 | 5.5 | 3.9 | 4 | 5.6 | 6.2 | 5.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WTR8B2 Poison Gate |  |  | DF |  | 11 |  | Gilgandra Main Street Under Awning Fascia LV Mains |  | -31.7122 | 148.6682 | -31.7106 | 148.6698 | 770 | 0.013 | Safety |  | 716024 |  |  | 716024 | 0.1 | 0.1 | 52357 |  | 14320 | 06/2024 | [7 empty] | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | [15 empty] | 3.54 | 3.52 | 3.53 | 3.53 | 3.53 | [7 empty] | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | [15 empty] | 3.54 | 3.52 | 3.53 | 3.53 | 3.53 | [6 empty] | 3.38 | 3.36 | 3.37 | 3.37 | 3.36 | 3.38 | 3.36 | 3.37 | 3.37 | 3.36 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0.2 | 0 |  | No
| BNK24787 Old Bar No.2 |  |  | DF |  | 11 |  | Dubbo Eulomogo ZS CB32 CB82 Replace HV UG Cable |  | -32.2512 | 148.6482 | -32.2512 | 148.6482 | 1490 | 1 | Asset Condition |  | 523415 |  |  | 523415 | 0.1 | 0.1 | 38273 |  | 10468 | 06/2024 | [7 empty] | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | [15 empty] | 2.09 | 2.14 | 2.19 | 2.23 | 2.27 | [7 empty] | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | [15 empty] | 2.09 | 2.14 | 2.19 | 2.23 | 2.27 | [6 empty] | 2.09 | 2.14 | 2.18 | 2.22 | 2.26 | 2.09 | 2.14 | 2.18 | 2.22 | 2.26 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| BLH3B3 Bulahdelah Nth/Markwell/Newells Ck |  |  | DF |  | 11 |  | Dubbo Windsor Pde CE261523 End of Life |  | -32.256 | 148.6423 | -32.2579 | 148.6389 | 1170 | 0.065 | Asset Condition |  | 257090 |  |  | 257090 | 0.1 | 0.1 | 18799 |  | 5142 | 06/2024 | [7 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [15 empty] | 1.66 | 1.67 | 1.69 | 1.71 | 1.73 | [7 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [15 empty] | 1.66 | 1.67 | 1.69 | 1.71 | 1.73 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| HGN3B1 Crowdy Head |  |  | DF |  | 11 |  | Dubbo Airport U/G 185mm Thermal Constraint 598m |  | -32.2261 | 148.5682 | -32.2223 | 148.5637 | 384 | 0.13 | Capacity | 249806 |  |  |  | 249806 | 0.1 | 0.1 | 18266 |  | 4996 | 06/2025 | [7 empty] | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | [15 empty] | 0.81 | 0.83 | 0.86 | 0.88 | 0.9 | [7 empty] | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | [15 empty] | 0.81 | 0.83 | 0.86 | 0.88 | 0.9 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WTE3B7 Spence St |  |  | DF |  | 11 |  | Gilgandra GID22-1 22 kV OH Conductor End of Life |  | -31.7263 | 148.6552 | -31.7263 | 148.6552 | 609 | 1 | Asset Condition |  | 235374 |  |  | 235374 | 0.1 | 0.1 | 17211 |  | 4707 | 06/2025 | [7 empty] | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | [15 empty] | 3.38 | 3.35 | 3.35 | 3.34 | 3.34 | [7 empty] | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34 | [15 empty] | 3.38 | 3.35 | 3.35 | 3.34 | 3.34 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| TEA3B4 Tea Gardens |  |  | DF |  | 11 |  | 11kV Feeder backup Pacific Highway, Halfway Creek, Voltage |  | -29.9514 | 153.1183 | -29.9642 | 153.1322 | 1226 | 0.8 | Reliability | 667008 |  |  |  | 667008 | 0.1 | 0.1 | 48773 |  | 13340 | 06/2025 | [7 empty] | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | [15 empty] | 2.72 | 2.74 | 2.75 | 2.75 | 2.74 | [7 empty] | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | [15 empty] | 2.72 | 2.74 | 2.75 | 2.75 | 2.74 | [6 empty] | 2.72 | 2.73 | 2.74 | 2.74 | 2.73 | 2.72 | 2.73 | 2.74 | 2.74 | 2.73 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 1 | 0 |  | No
| GLS3B2 Rockvale |  |  | DF |  | 11 |  | OH-11kV - Establish new river crossing -270m- Broadwater |  | -28.9965 | 153.443 | -28.9965 | 153.4434 | 376 | 0.133 | Voltage |  |  | 594675 |  | 594675 | 0.1 | 0.1 | 43484 |  | 11894 | 06/2024 | [7 empty] | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | [15 empty] | 1.77 | 1.8 | 1.82 | 1.84 | 1.86 | [7 empty] | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | [15 empty] | 1.77 | 1.8 | 1.82 | 1.84 | 1.86 | [6 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| WLS3B1 Walcha East |  |  | DF |  | 11 |  | UG-11kV - replace 95mm cable - 360m - Hutley Dve, Lennox Hd |  | -28.8022 | 153.5857 | -28.8012 | 153.5885 | 673 | 1 | Capacity | 296482 |  |  |  | 296482 | 0.1 | 0.1 | 21679 |  | 5930 | 06/2025 | [7 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | [15 empty] | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | [7 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | [15 empty] | 1.23 | 1.24 | 1.25 | 1.26 | 1.27 | [6 empty] | 0.01 | 0 | 0.2 | 0.21 | 0.2 | 0.01 | 0 | 0.2 | 0.21 | 0.2 | [26 empty] | 0.5 | [11 empty] | 0.5 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| HGE3B1 Grafton Rd |  |  | DF |  | 11 |  | Port Macquarie Central Rd & Acacia Ave Conductor Rating |  | -31.4538 | 152.8819 | -31.4547 | 152.8802 | 1069 | 0.047 | Capacity | 642466 |  |  |  | 642466 | 0.1 | 0.1 | 46979 |  | 12849 | 06/2024 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.27 | 0.27 | 0.28 | 0.28 | 0.28 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.27 | 0.27 | 0.28 | 0.28 | 0.28 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.1 | [11 empty] | 0.1 | [10 empty] | 0.9 |  | 0.1 | 0 |  | No
| GLS3B7 City Central |  |  | DF |  | 11 |  | HV UG DEFRECT replace HV cable 400m McLaren Drv nr sub 2-41451 Port Macquarie |  | -31.4489 | 152.9086 | -31.4496 | 152.9136 | 1370 | 0.182 | Asset Condition |  | 282896 |  |  | 282896 | 0.1 | 0.1 | 20686 |  | 5658 | 06/2024 | [7 empty] | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | [15 empty] | 2.07 | 2.11 | 2.13 | 2.15 | 2.18 | [7 empty] | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | [15 empty] | 2.07 | 2.11 | 2.13 | 2.15 | 2.18 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| MLN3B4 Townsend |  |  | DF |  | 11 |  | Port Macquarie Highfields Cct Conductor Rating |  | -31.4538 | 152.8819 | -31.4547 | 152.8802 | 1069 | 0.05 | Capacity | 226711 |  |  |  | 226711 | 0.1 | 0.1 | 16578 |  | 4534 | 06/2024 | [7 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [15 empty] | 2.47 | 2.48 | 2.49 | 2.47 | 2.42 | [7 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [15 empty] | 2.47 | 2.48 | 2.49 | 2.47 | 2.42 | [6 empty] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | [26 empty] | 0.1 | [11 empty] | 0.1 | [10 empty] | 0.9 |  | 0.1 | 0 |  | No
| SGN3B4 Ulmarra |  |  | DF |  | 11 |  | OH_2480m 1ph 11kV 3/2.75SC/GZ Reconduct_Freedom Island |  | -30.8851 | 153.0061 | -30.8671 | 152.9927 | 862 | 0.01 | Asset Condition |  | 219213 |  |  | 219213 | 0.1 | 0.1 | 16029 |  | 4384 | 06/2025 | [7 empty] | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | [15 empty] | 2.1 | 2.09 | 2.09 | 2.09 | 2.08 | [7 empty] | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | 1.64 | [15 empty] | 2.1 | 2.09 | 2.09 | 2.09 | 2.08 | [6 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.9 |  | 0 | 0 |  | No
| MWN3B8 Uki |  |  | DF |  | 11 |  | Kunghur Doon Doon Rd 11kV Reconductor End Of Life |  | -28.4663 | 153.2665 | -28.5033 | 153.2651 | 2136 | 0.06 | Asset Condition |  | 277299 |  |  | 277299 | 0.1 | 0.1 | 22578 |  | 5585 | 06/2026 | [7 empty] | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | [15 empty] | 3.39 | 3.41 | 3.42 | 3.45 | 3.48 | [7 empty] | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | 1.66 | [15 empty] | 3.39 | 3.41 | 3.42 | 3.45 | 3.48 | [6 empty] | 3.25 | 3.27 | 3.29 | 3.31 | 3.34 | 3.25 | 3.27 | 3.29 | 3.31 | 3.34 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| SGN3B1 Armidale Rd |  |  | DF |  | 11 |  | Wells Crossing Parker Rd Establish HV Tie Reliability |  | -29.9081 | 153.023 | -29.9075 | 153.0649 | 1231 | 0.29 | Reliability | 458005 |  |  |  | 458005 | 0.1 | 0.1 | 37292 |  | 9160 | 06/2025 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [6 empty] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| MLN3B5 Woodford Dale-Leigh |  |  | DF |  | 11 |  | Lawrence River Crossing Pole 74700 End Of Life |  | -29.4916 | 153.1172 | -29.4916 | 153.1172 | 863 | 0.72 | Safety |  | 282348 |  |  | 282348 | 0.1 | 0.1 | 22989 |  | 5647 | 06/2026 | [7 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [15 empty] | 1.59 | 1.59 | 1.6 | 1.59 | 1.56 | [7 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [15 empty] | 1.59 | 1.59 | 1.6 | 1.59 | 1.56 | [6 empty] | 1.55 | 1.56 | 1.57 | 1.55 | 1.53 | 1.55 | 1.56 | 1.57 | 1.55 | 1.53 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 1 | 0 |  | No
| MWN3B2 Norco |  |  | DF |  | 11 |  | Murwillumbah Buchanan St create HV interconnector MWN3B2/9 |  | -28.3373 | 153.4094 | -28.3386 | 153.4192 | 1105 | 1 | Capacity | 414506 |  |  |  | 414506 | 0.1 | 0.1 | 33750 |  | 8022 | 06/2025 | [7 empty] | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | [15 empty] | 2.55 | 2.57 | 2.58 | 2.6 | 2.63 | [7 empty] | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | [15 empty] | 2.55 | 2.57 | 2.58 | 2.6 | 2.63 | [6 empty] | 2.45 | 2.47 | 2.48 | 2.5 | 2.52 | 2.45 | 2.47 | 2.48 | 2.5 | 2.52 | [26 empty] | 2 | [11 empty] | 2 | [10 empty] | 0.96 |  | 1 | 0 |  | No
| BPT3B3 Fingal |  |  | DF |  | 11 |  | Tweed Heads South Alf Rush Memorial Dr Sub 54-212 EOL Chamber sub replacement |  | -28.2077 | 153.5606 | -28.2077 | 153.5606 | 1972 | 0.01 | Asset Condition | 370791 |  |  |  | 370791 | 0.1 | 0.1 | 30191 |  | 6908 | 06/2026 | [7 empty] | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | [15 empty] | 4.46 | 4.46 | 4.46 | 4.47 | 4.48 | [7 empty] | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | [15 empty] | 4.46 | 4.46 | 4.46 | 4.47 | 4.48 | [6 empty] | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| BHL42 Railwaytown |  |  | DF |  | 22 |  | Broken Hill, Refurbishment sub 6-16271 Sturt Park Sulphide St |  | -31.9571 | 141.4625 | -31.9571 | 141.4625 | 4472 | 0.04 | Asset Condition |  | 294685 |  |  | 294685 | 0.1 | 0.1 | 23994 |  | 5894 | 06/2025 | [7 empty] | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | [15 empty] | 40.78 | 42.22 | 42.21 | 42.07 | 41.8 | [7 empty] | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | [15 empty] | 40.78 | 42.22 | 42.21 | 42.07 | 41.8 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.981 |  | 0 | 0 |  | No
| WLC4B1 White Cliffs |  |  | DF |  | 33 |  | Wilcannia - Underground Network alterations White Cliffs |  | -30.8531 | 143.097 | -30.8463 | 143.0836 | 262 | 0.44 | Safety |  | 387059 |  |  | 387059 | 0.1 | 0.1 | 31515 |  | 7741 | 06/2025 | [7 empty] | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | [15 empty] | 0.64 | 0.65 | 0.67 | 0.68 | 0.69 | [7 empty] | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | [15 empty] | 0.64 | 0.65 | 0.67 | 0.68 | 0.69 | [6 empty] | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | [26 empty] | 0.15 | [11 empty] | 0.15 | [10 empty] | 0.857 |  | 0 | 0 |  | No
| DBS3B8 Margaret Cres |  |  | DF |  | 11 |  | Replace existing 1000kVA Pad Sub 30-4559 with a 1500 kVA Pad Sub. |  | -32.26 | 148.6233 | -32.26 | 148.6233 | 2287 | 0 | Capacity |  | 258749 |  |  | 258749 | 0.1 | 0.1 | 21068 |  | 5175 | 06/2025 | [7 empty] | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | [15 empty] | 5.27 | 5.33 | 5.39 | 5.45 | 5.49 | [7 empty] | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | [15 empty] | 5.27 | 5.33 | 5.39 | 5.45 | 5.49 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| BKE4B2 M82 Wanaaring |  |  | DF |  | 33 |  | Bourke Wanaaring BKE4B2 M82 Multiple Sites Poor Performing Feeder |  | -29.3547 | 145.0001 | -29.668 | 145.272 | 331 | 0.8 | Reliability |  | 280710 |  |  | 280710 | 0.1 | 0.1 | 22856 |  | 5614 | 06/2025 | [7 empty] | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | [15 empty] | 1.62 | 1.62 | 1.63 | 1.65 | 1.67 | [7 empty] | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | [15 empty] | 1.62 | 1.62 | 1.63 | 1.65 | 1.67 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.54 |  | 0 | 0 |  | No
| DBW3B5 Rural West |  |  | DF |  | 11 |  | Dubbo Airport U/G 185mm Thermal Constraint 598m |  | -32.2261 | 148.5682 | -32.2222 | 148.5636 | 388 | 1 | Capacity |  | 261645 |  |  | 261645 | 0.1 | 0.1 | 21304 |  | 5233 | 06/2026 | [7 empty] | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | [15 empty] | 2.7 | 2.74 | 2.76 | 2.78 | 2.81 | [7 empty] | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | 1.42 | [15 empty] | 2.7 | 2.74 | 2.76 | 2.78 | 2.81 | [6 empty] | 2.62 | 2.66 | 2.68 | 2.7 | 2.73 | 2.62 | 2.66 | 2.68 | 2.7 | 2.73 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.971 |  | 0 | 0 |  | No
| EUL32 Dubbo Nth/East Town |  |  | DF |  | 11 |  | Replace defective cable emanating from the Eulomogo Zone Substation |  | -32.2517 | 148.6488 | -32.2459 | 148.6487 | 1495 | 1 | Asset Condition |  | 483545 |  |  | 483545 | 0.1 | 0.1 | 39371 |  | 9671 | 06/2025 | [7 empty] | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | [15 empty] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | [7 empty] | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | [15 empty] | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | [6 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| GID22 Rural Nth/Sth/West |  |  | DF |  | 11 |  | Replace 2.9 km of 7/104 HDBC 11 kV conductor with 7/450 AAAC in the vicinity of South Gilgandra. |  | -31.7206 | 148.6554 | -31.7418 | 148.6446 | 610 | 1 | Asset Condition |  | 302320 |  |  | 302320 | 0.1 | 0.1 | 24616 |  | 6046 | 06/2026 | [7 empty] | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | [15 empty] | 2.08 | 2.09 | 2.1 | 2.11 | 2.12 | [7 empty] | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | [15 empty] | 2.08 | 2.09 | 2.1 | 2.11 | 2.12 | [6 empty] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.992 |  | 0 | 0 |  | No
| GID12 Gilgandra Town No.1 |  |  | DF |  | 11 |  | Relocate the existing Low Voltage network that supplies the CBD of the Township of Gilgandra |  | -31.7122 | 148.6682 | -31.7106 | 148.6698 | 705 | 0.108 | Safety | 702128 |  |  |  | 702128 | 0.1 | 0.1 | 57169 |  | 14043 | 06/2025 | [7 empty] | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | [15 empty] | 1.95 | 1.96 | 1.97 | 1.98 | 1.99 | [7 empty] | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | [15 empty] | 1.95 | 1.96 | 1.97 | 1.98 | 1.99 | [6 empty] | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| WBN3B3 Coraki |  |  | DF |  | 11 |  | Marom Creek Cook Rd Conductor 4.6km End Of Life |  | -28.897 | 153.3659 | -28.9266 | 153.334 | 914 | 0.01 | Reliability |  | 273485 |  |  | 273485 | 0.1 | 0.1 | 22268 |  | 5470 | 06/2026 | [7 empty] | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | [15 empty] | 1.76 | 1.77 | 1.78 | 1.78 | 1.8 | [7 empty] | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | [15 empty] | 1.76 | 1.77 | 1.78 | 1.78 | 1.8 | [42 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 1 | 0 |  | No | bar: 0.59 to 0.67
| EWE3B1 Brunswick No.1 |  |  | DF |  | 11 |  | Brunswick Heads LV conductor 3.0km End Of Life |  | -28.5424 | 153.5432 | -28.5419 | 153.5539 | 1174 | 0.6 | Asset Condition |  | 433695 |  |  | 433695 | 0.1 | 0.1 | 35312 |  | 8674 | 06/2026 | [7 empty] | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | [15 empty] | 2.1 | 2.13 | 2.16 | 2.19 | 2.24 | [7 empty] | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | [15 empty] | 2.1 | 2.13 | 2.16 | 2.19 | 2.24 | [42 empty] | 1.5 | [11 empty] | 1.5 | [10 empty] | 0.98 |  | 0 | 0 |  | No | bar: 0.59 to 0.67
| WGN72 Yeoval |  |  | DF |  | 11 |  | Wellington, Upgrade conductor beyond 30-R12394, Protection constraints |  | -32.7362 | 148.7431 | -32.8098 | 148.7905 | 373 | 0.12 | Capacity | 598980 |  |  |  | 598980 | 0.1 | 0.1 | 48770 |  | 11980 | 06/2026 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.75 | 0.76 | 0.77 | 0.78 | 0.78 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.02 | [11 empty] | 0.02 | [10 empty] | 0.95 |  | 0.01 | 0 |  | No
| TXS3X06 Yelarbon |  |  | DF |  | 33 |  | Texas Holdflat Rd DEF REC 9.8km HV Conductor |  | -28.6697 | 150.6858 | -28.7519 | 150.7042 | 346 | 0.07 | Asset Condition |  | 609577 |  |  | 609577 | 0.1 | 0.1 | 49633 |  | 12192 | 06/2026 | [7 empty] | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | [15 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [7 empty] | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | [15 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [6 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| LKC7781 Cathie Sth |  |  | DF |  | 11 |  | Wallum Drv Seascape Lake Cathie thermal overload & reliability |  | -31566 | 152.827 | -31566 | 152.827 | 1148 | 1 | Reliability | 414450 |  |  |  | 414450 | 0.1 | 0.1 | 33745 |  | 7911 | 06/2029 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 2.08 | 2.16 | 2.24 | 2.32 | 2.41 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 2.08 | 2.16 | 2.24 | 2.32 | 2.41 | [6 empty] | 0.9 | 1.1 | 1.3 | 1.4 | 1.6 | 0.9 | 1.1 | 1.3 | 1.4 | 1.6 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.976 |  | 3 | 0 |  | No
| BPM3B3 Oxley |  |  | DF |  | 11 |  | Port Macquarie Central Rd & Acacia Ave Conductor Rating |  | -31.4511 | 152.875 | -31.455 | 152.874 | 1753 | 0.3 | Capacity | 1021663 |  |  |  | 1021663 | 0.1 | 0.1 | 83186 |  | 20575 | 06/2025 | [7 empty] | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | [15 empty] | 4.15 | 4.22 | 4.3 | 4.38 | 4.45 | [7 empty] | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | [15 empty] | 4.15 | 4.22 | 4.3 | 4.38 | 4.45 | [6 empty] | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | 0.6 | 0.7 | 0.8 | 0.8 | 0.8 | [26 empty] | 0.7 | [11 empty] | 0.7 | [10 empty] | 0.996 |  | 0 | 0 |  | No
| OPM3B1 Granite St |  |  | DF |  | 11 |  | Replace HV cable 400m McLaren Drv near sub 2-41451 Port Macquarie |  | -31.449 | 152.913 | -31.489 | 152.908 | 1372 | 0.054 | Asset Condition |  | 328536 |  |  | 328536 | 0.1 | 0.1 | 26750 |  | 5509 | 06/2024 | [7 empty] | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | [15 empty] | 2.32 | 2.33 | 2.33 | 2.33 | 2.33 | [7 empty] | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | [15 empty] | 2.32 | 2.33 | 2.33 | 2.33 | 2.33 | [6 empty] | 0.51 | 0.51 | 0.5 | 0.5 | 0.5 | 0.51 | 0.51 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| SGN3B1 Armidale Rd |  |  | DF |  | 11 |  | 11kV Feeder backup Pacific Highway, Halfway Creek, Voltage |  | -29.9822 | 153.1429 | -29.9538 | 153.1193 | 1231 | 0.1 | Reliability | 722225 |  |  |  | 722225 | 0.1 | 0.1 | 58805 |  | 14445 | 06/2025 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.52 | 2.51 | 2.51 | 2.51 | 2.5 | [6 empty] | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [26 empty] | 0.28 | [11 empty] | 0.28 | [10 empty] | 0.97 |  | 0.5 | 0 |  | No
| GGB112 Gulargambone |  |  | DF |  | 22 |  | Reconductor 7/064 HDBC between GGB112 CB through to 30-G2930 with 7/450 AAAC in vicinity of Gulargambone |  | -31.3253 | 148.4848 | -31.4244 | 148.5254 | 481 | 1 | Asset Condition | 836206 |  |  |  | 836206 | 0.1 | 0.1 | 68086 |  | 16724 | 06/2026 | [7 empty] | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | [15 empty] | 1.31 | 1.31 | 1.32 | 1.32 | 1.32 | [7 empty] | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | [15 empty] | 1.31 | 1.31 | 1.32 | 1.32 | 1.32 | [6 empty] | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| NBI3B1 M14 Spring Ck |  |  | DF |  | 11 |  | Narrabri to Bellata Interconnector supply constraint |  | -30.2384 | 149.8098 | -30.178 | 149.8195 | 81 | 1 | Reliability | 1966866 |  |  |  | 1966866 | 0.1 | 0.1 | 160147 |  | 39337 | 06/2026 | [7 empty] | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | [15 empty] | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | [7 empty] | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | [15 empty] | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.946 |  | 0 | 0 |  | No
| WWA8B4 M8/M21 Spring Plains Rd |  |  | DF |  | 22 |  | WWA8B4 past 75-R602109- Poletop refurb - Poor Performing Feeder |  | -30.1128 | 149.4684 | -29.9673 | 149.4983 | 17 | 0.16 | Reliability | 285987 |  |  |  | 285987 | 0.1 | 0.1 | 23286 |  | 5720 | 06/2026 | [7 empty] | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | [15 empty] | 1.53 | 1.56 | 1.58 | 1.6 | 1.61 | [7 empty] | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | [15 empty] | 1.53 | 1.56 | 1.58 | 1.6 | 1.61 | [6 empty] | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | 1.4 | 1.5 | 1.5 | 1.5 | 1.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| NBI8B10 M16 Mount Dowe |  |  | DF |  | 22 |  | Replace ground mount TX 75-160005 Mt Dowe Kaputar with padsub |  | -30.2858 | 150.1671 | -30.2858 | 150.1671 | 1 | 0.01 | Reliability |  | 252100 |  |  | 252100 | 0.1 | 0.1 | 20527 |  | 5042 | 06/2025 | [7 empty] | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | [15 empty] | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | [7 empty] | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | 3.09 | [15 empty] | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | [6 empty] | 0.68 | 0.67 | 0.67 | 0.67 | 0.67 | 0.68 | 0.67 | 0.67 | 0.67 | 0.67 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| SFP |  |  | ZS |  | 132 | 11 | Single transformer with high forecast growth |  | -28.6727 | 153.5938 | -28.6727 | 153.5938 | 6400 | 1 | Capacity | 2000000 |  |  |  | 2000000 | 0.1 | 0.1 | 146200 |  | 40000 | 06/2027 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | [15 empty] | 12.6 | 12.9 | 13 | 13.3 | 13.5 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | [15 empty] | 13.8 | 14 | 14.2 | 14.4 | 14.6 | [6 empty] | 13.8 | 14 | 14.2 | 14.4 | 14.6 | 9.66 | 9.8 | 9.94 | 10.08 | 10.22 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 4 | 0
| MRE |  |  | ZS |  | 66 | 22 | Transformer capacity overload with high forecast growth |  | -29.4836 | 149.8519 | -29.4836 | 149.8519 | 6288 | 1 | Capacity | 1000000 |  |  |  | 1000000 | 0.1 | 0.1 | 73100 |  | 20000 | 06/2026 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 90 | 90 | 90 | [15 empty] | 25.3 | 25.9 | 26.4 | 27.3 | 36.4 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 90 | 90 | 90 | [15 empty] | 26.2 | 26.5 | 27.1 | 36.1 | 39.5 | [6 empty] | 26.2 | 26.5 | 27.1 | 36.1 | 39.5 | 18.34 | 18.55 | 18.97 | 25.27 | 27.65 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 4 | 0
| BBN |  |  | ZS |  | 66 | 11 | Transformer capacity overload with high forecast growth |  | -35.0742 | 147.4074 | -35.0742 | 147.4074 | 147 | 1 | Capacity | 2900000 |  |  |  | 2900000 | 0.1 | 0.1 | 211990 |  | 58000 | 06/2026 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | [15 empty] | 11.7 | 11.7 | 11.7 | 15.2 | 21.1 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | [15 empty] | 10.7 | 10.7 | 14.2 | 20.2 | 36.3 | [6 empty] | 11.7 | 11.7 | 14.2 | 20.2 | 36.3 | 8.19 | 8.19 | 9.94 | 14.14 | 25.41 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 8 | 0
| 79W Tharbogang - Warrawidgee - Nericon |  |  | DF |  | 33 |  | Voltage and thermal limitations under contingent conditions |  | -34.2355 | 146.0481 | -34.2039 | 146.0482 | 184 | 1 | Capacity | 4000000 |  |  |  | 4000000 | 0.1 | 0.1 | 292400 |  | 80000 | 06/2027 | [7 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | [15 empty] | 11.4 | 11.5 | 11.6 | 11.7 | 11.8 | [7 empty] | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | [15 empty] | 7.8 | 7.9 | 8 | 8.1 | 8.2 | [6 empty] | 11.4 | 11.5 | 11.6 | 11.7 | 11.8 | 7.98 | 8.05 | 8.12 | 8.19 | 8.26 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 2 | 0
Note on A1: Full asset name (or, for TNSPs, 'Project Name' if more relevant). Should include any spatially represented asset type for which you wish to present data. For Zone Sustation asset this will generally match the asset_name in NOM polygon files. Units/format: Free text field
Note on B1: AER Ref: DT004 'shorthand' code or asset ID of Network Asset. Should be consistent with RIN Sustained Interruptions sheet from Category Analysis template. Generally this will match NOM polygon file asset_codes however the entry of the relevant asset_code of mapped region now occurs in connected_region1. (Col FN) Units/format: Free text field but ideally short notation no spaces and be unique.
Note on C1: There may be multiple investments (data lines) that relate to a given mapping region/polygon (such as a transformer replacement, a feeder augmentation and a switchboard rebuild at the same Zone Substation), but only 1 data line can be associated with each polygon's available capacity information. Therefore this cell specifies - where multiple investments are occurring - which lines the NOM should map on "Proposed Investment" and "Annual Deferral Value" maps, but ignore for "Available Capacity" and "Peak Day Available Capacity". Zone Substation data is generally preferred to display, or data for the sub-investment with the greatest opportunity for non-network solutions. Format: enter 'TRUE' to exclude. Otherwise leave blank.
Note on D1: Name of NSP or planning manager (for Vic transmission). Units/format: Text, but must conform exactly (case sensitive) to following list: United Energy, Tasnetworks, Transgrid, Essential Energy, Endeavour, Ausgrid, Evoenergy, Ergon Energy, Energex, SA Power Networks, Electranet, Jemena, Ausnet, Citipower-Powercor, AEMO
Note on E1: AER Ref: DT005 TL: Transmission Line TS: Transmission terminal station TCP: Transmission Connection Point STL: Sub transmission line ZS: Zone Substation ZS (proposed): New Zone Substation proposed to be built DF: (Distribution) feeder Units/format: Defined code above. Must match exactly (case sensitive)
Note on F1: Some assets may not have a 10-yr forecast, and only have a 5-yr forecast available (e.g. feeders). However, the maps produced will be for 10 years. Marking this field TRUE will keep yr5 loads and support requirements static out to yr10, and automatically include a standard caveat explaining this in the investment_description field. Format: enter 'TRUE' to use 5yr forecast only. Otherwise leave blank.
Note on G1: AER Ref: DT009 Highest operational voltage level of the assets involved in the constraints Units/format: kV (integer)
Note on H1: AER Ref: DT009 Operational voltage level of the assets involved in the constraints on the low side of the transformer Units/format: kV (integer)
Note on I1: AER Ref: DT012 Description of the problem or general asset situation and proposed network solution. Units/format: Free text field. Include special data caveats here if relevant.
Note on J1: Indicate the reliability criteria applied to the network asset. For example n, n-1, n-2, n-1 + risk. Unit/Format: Free text.
Note on K1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on L1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on M1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on N1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on O1: AER Ref: DT006 Total number of customers affected
Note on P1: AER Ref: DT006_a Percent of customers affected Format: Percent, entered as a positive decimal between 0 and 1 (e.g. 15% would be entered as 0.15)
Note on Q1: AER Ref: DT001 Constraint primary investment driver Format: Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage; market benefit. Must match list (but no longer case sensitive)
Note on R1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Demand growth related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on S1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Age/condition related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on T1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Connections related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on U1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Related to investments not falling into one of the other categories. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on V1: AER Ref: DT013 Total value of proposed network solution - should be the sum of Cols P to S (all investment types). If zero leave blank. Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on W1: AER Ref: DT014_a Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on X1: AER Ref: DT014_b Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on Y1: AER Ref: DT017 Saving in cost of capital from defering the project. Note that this does not use Value of Customer Reliability as an Input, as originally specified in AER guidance. Units: $/a (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload. NB: This is not the same calculation as represented in the Annual Deferral Value (ADV) map on the Network Opportunity Maps.
Note on Z1: Provide the component of the total proposed investment (Col T) that is considered deferrable with the non-network alternative/ Includes: • Defering augmentation (reducing project demand growth) • Defering new infrastructure riven by revised reliability criteria • Retiring assets (by reducing demand) • Downsizing assets (by reducing demand) • Extending the life of assets (by reducing the load conditions) Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AA1: AER Ref: DT013_a Annual operating costs (including overheads, risk allowance and contingency allowance if included) Units/Formats: $ AUD (real) Note: It may be useful to view your $ figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AB1: AER Ref: DT015 Provide the expected month and year when investment is planned for commissioning. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AC1: Provide the expected month and year when investment decision is locked in and non-network solutions are no longer an option. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AD1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AE1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AF1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AG1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AH1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on AI1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on AJ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AK1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AL1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AM1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AN1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AO1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AP1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AQ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AR1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AW1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AX1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AY1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AZ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BA1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BB1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BC1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BD1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BE1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BF1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BG1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BH1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BI1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BJ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BK1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BL1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BM1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BN1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BO1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BP1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BQ1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on BR1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on BS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BW1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BX1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BY1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BZ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CA1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CB1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CC1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CD1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CE1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CF1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CG1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CH1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CI1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CJ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CK1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CL1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CM1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CN1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CO1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CP1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CQ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CR1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CS1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CT1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CU1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CV1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CW1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CX1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CY1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CZ1: Provide Probability of Exceedance (POE) to be used in the NOM calculations. Should be the forecast upon which investment decision is based. Unit/Format: integer (10 or 50 ONLY)
Note on DA1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DB1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DC1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DD1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DE1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DF1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DG1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DH1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DI1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DJ1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DK1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DL1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DM1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DN1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DO1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DP1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DQ1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DR1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DS1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DT1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DU1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DV1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DW1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DX1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DY1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DZ1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EA1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EB1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EC1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on ED1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EE1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EF1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EG1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EH1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EI1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EJ1: AER Ref: DT016_a Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EK1: AER Ref: DT016_b Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EL1: AER Ref: DT016 Support Required in Summer. Unit/Format: MVA
Note on EM1: Support Required in Summer. Unit/Format: MVA
Note on EN1: Support Required in Summer. Unit/Format: MVA
Note on EO1: Support Required in Summer. Unit/Format: MVA
Note on EP1: Support Required in Summer. Unit/Format: MVA
Note on EQ1: Support Required in Summer. Unit/Format: MVA
Note on ER1: Support Required in Summer. Unit/Format: MVA
Note on ES1: Support Required in Summer. Unit/Format: MVA
Note on ET1: Support Required in Summer. Unit/Format: MVA
Note on EU1: Support Required in Summer. Unit/Format: MVA
Note on EV1: AER Ref: DT016_a Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EW1: AER Ref: DT016_b Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EX1: AER Ref: DT016 Support Required in Winter. Unit/Format: MVA
Note on EY1: Support Required in winter. Unit/Format: MVA
Note on EZ1: Support Required in winter. Unit/Format: MVA
Note on FA1: Support Required in winter. Unit/Format: MVA
Note on FB1: Support Required in winter. Unit/Format: MVA
Note on FC1: Support Required in winter. Unit/Format: MVA
Note on FD1: Support Required in winter. Unit/Format: MVA
Note on FE1: Support Required in winter. Unit/Format: MVA
Note on FF1: Support Required in winter. Unit/Format: MVA
Note on FG1: Support Required in winter. Unit/Format: MVA
Note on FH1: Supports solution for AER Refs: DT007_a, DT008_a, DT017_a, DT021_a Asset specific power factor Not used in NOM Format: Decimal between 0 and 1
Note on FI1: Optional: Description of reactive power requirements in an area. Unit/Format: Free text Note: Using this field will specify MVAr support required on ADV maps and thus not display other capacity related calculations (even if only a space is included " ")
Note on FJ1: AER Ref: DT017/ DT017_a NB: Leave BLANK if not applicable
Note on FK1: AER Ref: DT018 Emergency generation capacity available within constrained area Format: MVA NB: Leave BLANK if not applicable
Note on FL1: AER Ref: DT018_a Emergency generation capacity available within constrained area Format: MW
Note on FM1: AER Ref: DT019/ DT019_a Format: 'Yes' or 'No' Assets marked Yes will have 3yr half hourly data supplied in AER_NOM_emergencyresponse_data.xlsx and those with No will not.
Note on FN1: Mandatory (ALL data lines must have at least one connection specified): Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)

## Notes & Colour Key
This data template has been produced by the University of Technology Sydney on behalf of Energy Networks Austraila
Notes
This spreadsheet series combines the requirements of the Network Opportunity Maps and the AER DAPR digital data requirements in a single, consistent format that is machine readable for very large datasets.
The three spreadsheets in the series are as follows: | AER_NOM_annual_data_v3.1.xlsx | Main annual planning spreadsheet data input for all constrained assets under AER requirements for DNSPs, and all unconstrained Zone Substation data provided for NOM (only capacity and load forecast data dump required for latter assets)
| AER_NOM_loadtrace_data_mva_v3.1.xlsx | Detailed MVA load trace spreadsheet data for all constrained assets under AER requirement, and all unconstrained Zone Substation data provided for NOM. Machine linked to other spreadsheet using asset_code / ID. Responds to AER Ref: DT020
| AER_NOM_emergencyresponse_data_v3.xlsx | Only required to be filled out according to AER requirements for assets where emergency generation has been used in the past 3 years. Full 3yrs of half hourly data should be provided for any asset for which data is supplied. Responds to AER Ref: DT019 and DT019_a. This is only relevant for DNSPs.
The AER Reference number is shown in cell comments along with other relevant definitional information.
When this spreadsheet is saved as a .CSV (using the first worksheet only) it will be the machine readable input for online upload to the Network Opportunity Maps platform.
Cell Colour Key
Required by AER (and may be used in NOM)
NOM only (mandatory)
NOM only (optional)
Versions | Changes | Change (detail) | Data supplier Implication
Final, issued 15 December 2017
v1, issued 30 April 2018 | Corrects minor field name errors affecting data processing
v2, issued 30 November 2018 | Adjusts for 'support required' incompatibilies with AER requirements, and builds support for plotting multiple sub-projects at the one location with exclude_from_ADV column. Removes all drop down list to prevent errors in automated upload process. | Removed all drop-down boxes to eliminate automated upload issues | network, network_element & primary_driver must match prescribed case-sensitive list exactly (in cell comment and guideline) otherwise error will be drawn upon dataset upload.
|  | Cell formating changes and validations | If viewing $ value data entries in accounting format with , separators and/or $ sign need to "Edit>clear formats" for these cells before saving as CSV. No zero values allowed (if zero leave blank).
|  | New "exclude_from_capacity_ADV" field | Allows AER compliant dataset with multiple investments within one polygon to be mapped without errors. See Examples worksheet for application
|  | Added "summer_support_constraintyr_mw" and "summer_support_constraintyr_mva" | These are the AER requirements to disclose for the year the constraint bites. Previously this was the first year in the support required dataset (summer_support_yr1_mva) but this is often not the same as yr1 in the series. It should correspond with one of the years in the support required dataset, but this will differ depending on project_timing
|  | "connected_ZSX" changed to "connected_regionX": Terminology shift to be compatible with businesses using polygon that represent feeders rather than zone substation regions (or a mix thereof) | None
v2.1, issued 13 June 2019 | Adds cell comment guidance on year notations for Annual Data spreadsheet (only). Thus annual data template is v2.1 while others are still v2. | Yr1 now refers to Winter (Jun-Aug 2020) and Summer (Dec 2019-Feb 2020) | For any winter forecasts this may not align with TAPRs, as Jun-Aug 2019 will generally be the first year of 10-yr forecast series. Please check carefully, and we will change to naming specific years in the data templates for 2020 to avoid confusion, and request 11 years of data from TNSPs to manage the time mismatch between the 6-month DNSPs/TNSPs release timing (the final year can be extrapolated)
v3.0, issued 28 Nov 2020 | Minor changes to annual data template improve flexibility and streamline data entry | 1) Changed "exclude_from_capacity_ADV" (Col C) to "exclude_from_capacity_layers" as all investments are now able to be passed through to a specified polygon in ADV layers, and the exclude function now only applies to Available Capacity and Peak Day Available Capacity layers. 2) Includes new Col F "Use_5yr_forecast" for assets where 10yrs of data is not available. Marking TRUE in this field will keep yr5 loads static out to year 10, and automatically include a standard caveat explaining this in problem_context. Please use 10yr data wherever available. 3) Made connected_regionX field (Col FN onwards) mandatory for ALL data lines. This means that the asset_name and asset_code of the investments doesn't necessary need to match the polygon file, as the link to the polygon file occurs through the connected_regionX fields. | 1) Data entry basically the same as previous template. 2) If only 5 years of capacity, load forecast or support_required data is supplied, an error will be triggered unless the "Use_5yr_forecast" entry is marked as TRUE. 3) Every data line requires a linkage specified in Col FN.
v3.1, not yet issued | Added primary_driver category "market benefit" | Included in cell guidance in Col Q. Also no longer case sensitive. | Additional primary_driver category can now be used.
Note on A19: For assets for which this data is able to be produced (for example, a 10 yr forecast may be possibble for zone substations but not feeders)

## Examples
asset_name | asset_code | exclude_from_capacity_layers | network | network_element | use_5yr_forecast | voltage_highside | voltage_lowside | investment_description | reliability_criteria | latitude | longitude | latitude_end | longitude_end | res_cust_affected_no | res_cust_affected_percent | primary_driver | augmentation_invest | replacement_invest | connections_invest | other_invest | total_invest | cost_accuracy_plus | cost_accuracy_minus | annual_deferral | deferrable_invest | opex | project_timing | commitment_timing | summer_critical | winter_critical | spring_critical | autumn_critical | summer_nameplate_cap_mva | summer_secure_cap_mva | summer_acc_cap_yr_minus2_mva | summer_acc_cap_yr_minus1_mva | summer_acc_cap_yr0_mva | summer_acc_cap_yr1_mva | summer_acc_cap_yr2_mva | summer_acc_cap_yr3_mva | summer_acc_cap_yr4_mva | summer_acc_cap_yr5_mva | summer_acc_cap_yr6_mva | summer_acc_cap_yr7_mva | summer_acc_cap_yr8_mva | summer_acc_cap_yr9_mva | summer_acc_cap_yr10_mva | summer_load_yr1_poe50_mva | summer_load_yr2_poe50_mva | summer_load_yr3_poe50_mva | summer_load_yr4_poe50_mva | summer_load_yr5_poe50_mva | summer_load_yr6_poe50_mva | summer_load_yr7_poe50_mva | summer_load_yr8_poe50_mva | summer_load_yr9_poe50_mva | summer_load_yr10_poe50_mva | summer_load_yr1_poe10_mva | summer_load_yr2_poe10_mva | summer_load_yr3_poe10_mva | summer_load_yr4_poe10_mva | summer_load_yr5_poe10_mva | summer_load_yr6_poe10_mva | summer_load_yr7_poe10_mva | summer_load_yr8_poe10_mva | summer_load_yr9_poe10_mva | summer_load_yr10_poe10_mva | winter_nameplate_cap_mva | winter_secure_cap_mva | winter_acc_cap_yr_minus2_mva | winter_acc_cap_yr_minus1_mva | winter_acc_cap_yr0_mva | winter_acc_cap_yr1_mva | winter_acc_cap_yr2_mva | winter_acc_cap_yr3_mva | winter_acc_cap_yr4_mva | winter_acc_cap_yr5_mva | winter_acc_cap_yr6_mva | winter_acc_cap_yr7_mva | winter_acc_cap_yr8_mva | winter_acc_cap_yr9_mva | winter_acc_cap_yr10_mva | winter_load_yr1_poe50_mva | winter_load_yr2_poe50_mva | winter_load_yr3_poe50_mva | winter_load_yr4_poe50_mva | winter_load_yr5_poe50_mva | winter_load_yr6_poe50_mva | winter_load_yr7_poe50_mva | winter_load_yr8_poe50_mva | winter_load_yr9_poe50_mva | winter_load_yr10_poe50_mva | winter_load_yr1_poe10_mva | winter_load_yr2_poe10_mva | winter_load_yr3_poe10_mva | winter_load_yr4_poe10_mva | winter_load_yr5_poe10_mva | winter_load_yr6_poe10_mva | winter_load_yr7_poe10_mva | winter_load_yr8_poe10_mva | winter_load_yr9_poe10_mva | winter_load_yr10_poe10_mva | mapped_poe | load_at_risk_yr1_mw | load_at_risk_yr2_mw | load_at_risk_yr3_mw | load_at_risk_yr4_mw | load_at_risk_yr5_mw | EUSE_MWh_yr1 | EUSE_MWh_yr2 | EUSE_MWh_yr3 | EUSE_MWh_yr4 | EUSE_MWh_yr5 | EUSE_MWh_yr6 | EUSE_MWh_yr7 | EUSE_MWh_yr8 | EUSE_MWh_yr9 | EUSE_MWh_yr10 | hrs_exceedance_yr1 | hrs_exceedance_yr2 | hrs_exceedance_yr3 | hrs_exceedance_yr4 | hrs_exceedance_yr5 | hrs_exceedance_yr6 | hrs_exceedance_yr7 | hrs_exceedance_yr8 | hrs_exceedance_yr9 | hrs_exceedance_yr10 | EUSE_value_yr1 | EUSE_value_yr2 | EUSE_value_yr3 | EUSE_value_yr4 | EUSE_value_yr5 | EUSE_value_yr6 | EUSE_value_yr7 | EUSE_value_yr8 | EUSE_value_yr9 | EUSE_value_yr10 | summer_support_constraintyr_mw | summer_support_constraintyr_mva | summer_support_yr1_mva | summer_support_yr2_mva | summer_support_yr3_mva | summer_support_yr4_mva | summer_support_yr5_mva | summer_support_yr6_mva | summer_support_yr7_mva | summer_support_yr8_mva | summer_support_yr9_mva | summer_support_yr10_mva | winter_support_constraintyr_mw | winter_support_constraintyr_mva | winter_support_yr1_mva | winter_support_yr2_mva | winter_support_yr3_mva | winter_support_yr4_mva | winter_support_yr5_mva | winter_support_yr6_mva | winter_support_yr7_mva | winter_support_yr8_mva | winter_support_yr9_mva | winter_support_yr10_mva | power_factor | reactive_support_details | load_transfer_capability_mva | emergency_generation_mva | emergency_generation_mw | historic_emergency_generation_flag | connected_region1 | connected_region1_EF | connected_region2 | connected_region2_EF | connected_region3 | connected_region3_EF | connected_region4 | connected_region4_EF | connected_region5 | connected_region5_EF | connected_region6 | connected_region6_EF | connected_region7 | connected_region7_EF | connected_region8 | connected_region8_EF | connected_region9 | connected_region9_EF | connected_region10 | connected_region10_EF | connected_region11 | connected_region11_EF | connected_region12 | connected_region12_EF | connected_region13 | connected_region13_EF | connected_region14 | connected_region14_EF | connected_region15 | connected_region15_EF | connected_region16 | connected_region16_EF | connected_region17 | connected_region17_EF | connected_region18 | connected_region18_EF | connected_region19 | connected_region19_EF | connected_region20 | connected_region20_EF | connected_region21 | connected_region21_EF | connected_region22 | connected_region22_EF | connected_region23 | connected_region23_EF | connected_region24 | connected_region24_EF | connected_region25 | connected_region25_EF | connected_region26 | connected_region26_EF | connected_region27 | connected_region27_EF | connected_region28 | connected_region28_EF | connected_region29 | connected_region29_EF | connected_region30 | connected_region30_EF
Coburg North Zone Substation | CN |  | Jemena | ZS |  | 66 | 66 | Replace 66 kV 1-2 bus-tie circuit breaker at CN | economic/probabilistic | -37.7212 | 144.9778 | -37.7426 | 144.9626 | 21454 | 0.91649 | asset condition |  | 360000 |  |  | 360000 | 0.3 | 0.3 | 20000 | 360000 | 5400 | 2021-11-01 | 2019-06-01 | TRUE |  |  |  | 93 | 90 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 59.6001 | 60.1924 | 61.23 | 60.0791 | 59.8037 | 60.2273 | 59.8301 | 60.4631 | 60.1028 | 60.1366 | 65.6614 | 66.3525 | 67.4268 | 66.2315 | 66.1556 | 66.3655 | 66.0953 | 67.0858 | 66.4047 | 66.4442 | 93 | 90 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 57.2105 | 57.8859 | 58.9291 | 57.7878 | 57.6272 | 58.1072 | 57.9609 | 58.8006 | 59.1338 | 59.4636 | 58.5656 | 59.2324 | 60.2132 | 59.1372 | 59.0053 | 59.4382 | 59.2862 | 60.168 | 60.5061 | 60.8372 | 10 | 65.6264 | 66.3094 | 67.3695 | 66.1899 | 66.1149 | 1250 | 1250 | 1250 | 1250 | 1250 | [25 empty] | 65.6264 | 69.8575 | [22 empty] | 0.93943 |  | 18.6591 |  |  | No | JE_CN | 1
AW-03 Feeder | AW-03 |  | Jemena | DF | TRUE | 22 | 22 | Reconfigure AW-03 feeder loads. Deferral and capacity values shown are for an investment at AW-03 feeder and thus relate to a smaller area than shown in the map. Investments are also occuring to reconfigure AW-06, AW-07 and AW-08 feeder loads | economic/probabilistic | -37.7153 | 144.8859 | -37.7132 | 144.8607 | 1 | 0.011765 | capacity | 900000 |  |  |  | 900000 | 0.3 | 0.3 | 60000 | 900000 | 13500 | 2019-11-01 | 2018-06-01 | TRUE |  |  |  | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 5.9 | 5.8 | 5.8 | 5.9 | 6.1 | [5 empty] | 6.1 | 6.1 | 6.1 | 6.1 | 6.4 | [5 empty] | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 5.8 | 5.8 | 5.8 | 5.8 | 6 | [5 empty] | 5.9 | 5.9 | 5.9 | 6 | 6.2 | [5 empty] | 10 | 5.6 | 5.6 | 5.6 | 5.7 | 5.9 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 5.6 | 6.2222 | [22 empty] | 0.9 |  | 26.1 |  |  | No | JE_AW | 1
AW-06 Feeder | AW-06 | TRUE | Jemena | DF | TRUE | 22 | 22 | Reconfigure AW-06, AW-07 and AW-08 feeder loads | economic/probabilistic | -37.7153 | 144.8859 | -37.7572 | 144.8657 | 4952 | 0.97022 | capacity | 740000 |  |  |  | 740000 | 0.3 | 0.3 | 50000 | 740000 | 11100 | 2022-11-01 | 2020-06-01 | TRUE |  |  |  | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 12.1 | 12 | 11.9 | 11.7 | 11.7 | [5 empty] | 13.4 | 13.4 | 13.3 | 13 | 13.1 | [5 empty] | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 8.3 | 8.3 | 8.3 | 8.1 | 8.1 | [5 empty] | 8.5 | 8.5 | 8.4 | 8.3 | 8.3 | [5 empty] | 10 | 12.3 | 12.3 | 12.2 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 12.3 | 13.6667 | [22 empty] | 0.9 |  | 16.3 |  |  | No | JE_AW | 1
AW-07 Feeder | AW-07 | TRUE | Jemena | DF | TRUE | 22 | 22 | Reconfigure AW-06, AW-07 and AW-08 feeder loads | economic/probabilistic | -37.7153 | 144.8859 | -37.7497 | 144.8534 | 4702 | 0.96077 | capacity | 740000 |  |  |  | 740000 | 0.3 | 0.3 | 50000 | 740000 | 11100 | 2022-11-01 | 2020-06-01 | TRUE |  |  |  | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 11.7 | 11.7 | 11.6 | 11.4 | 11.5 | [5 empty] | 12.9 | 12.9 | 12.8 | 12.6 | 12.7 | [5 empty] | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | [5 empty] | 7.6 | 7.6 | 7.6 | 7.5 | 7.5 | [5 empty] | 10 | 11.8 | 11.8 | 11.8 | 11.6 | 11.7 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 11.8 | 13.1111 | [22 empty] | 0.9 |  | 16.7 |  |  | No | JE_AW | 1
Airport West Zone Substation | AW | TRUE | Jemena | ZS |  | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7155 | 144.8858 | -37.7155 | 144.8858 | 19949 | 0.88044 | [13 empty] | TRUE |  |  |  | 130 | 130 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 85.792 | 87.2799 | 86.4517 | 85.0735 | 85.4697 | 87.3576 | 88.0234 | 90.2939 | 91.0433 | 92.427 | 93.4014 | 95.0684 | 94.0486 | 92.6714 | 93.4399 | 95.115 | 96.0987 | 99.0093 | 99.4039 | 100.9174 | 130 | 130 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 66.1945 | 67.7915 | 67.178 | 66.1743 | 66.6425 | 68.1595 | 68.9543 | 70.9642 | 72.3914 | 73.8423 | 67.7787 | 69.3859 | 68.6548 | 67.7339 | 68.2524 | 69.7383 | 70.5504 | 72.6358 | 74.0988 | 75.586 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [49 empty] | 0.91931 |  | 39.0753 |  |  | No | JE_AW | 1
KTS-BY-ES Sub-transmission Loop | KTS-BY-ES |  | Jemena | STL |  | 66 | 66 | Augment KTS-BY-ES 66 kV loop | economic/probabilistic | -37.7382 | 144.8747 | -37.7824 | 144.8747 | 36197 | 0.92154 | capacity | 2210000 |  |  |  | 2210000 | 0.3 | 0.3 | 150000 | 2210000 | 33150 | 2019-11-01 | 2018-06-01 | TRUE |  |  |  | 72.6 | 72.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8999 | 81.0432 | 80.6774 | 78.9208 | 78.6048 | 79.9165 | 79.9521 | 81.4524 | 81.2159 | 81.5245 | 90.1368 | 90.2494 | 89.9716 | 88.0382 | 88.2057 | 89.2101 | 89.5089 | 91.4399 | 91.0864 | 91.0864 | 83.5 | 83.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.0109 | 63.2293 | 63.2786 | 61.9679 | 61.9679 | 62.988 | 63.3035 | 64.6413 | 65.4151 | 65.4151 | 64.6622 | 64.759 | 64.6372 | 63.4477 | 63.5693 | 64.4686 | 64.6622 | 66.2193 | 67.0439 | 67.0183 | 10 | 13.5412 | 14.0801 | 14.0729 | 12.6209 | 12.8906 | 1.3033 | 2.4165 | 2.5456 | 1.1263 | 1.3072 | 2.2063 | 1.1922 | 2.7583 | 3.4081 | 2.5182 | 38 | 43.5 | 43.5 | 35.5 | 37 | 43.5 | 47.5 | 45 | 50.5 | 43.5 | 52440.606 | 97231.176 | 102426.8758 | 45319.0291 | 52599.6885 | 88776.7755 | 47969.4996 | 110987.6172 | 137133.3043 | 101323.112 | 13.5412 | 15.0458 | [22 empty] | 0.9 |  | 43.5 |  |  | No | JE_BY | 1 | JE_ES | 1
x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Note on A1: Full asset name (or, for TNSPs, 'Project Name' if more relevant). Should include any spatially represented asset type for which you wish to present data. Must match NOM polygon files. Units/format: Free text field
Note on B1: AER Ref: DT004 'shorthand' code or asset ID of Network Asset. Should be consistent with RIN Sustained Interruptions sheet from Category Analysis template. Must match NOM polygon files. Units/format: Free text field but ideally short notation no spaces and be unique.
Note on C1: There may be multiple investments (data lines) that relate to a given mapping region/polygon (such as a transformer replacement, a feeder augmentation and a switchboard rebuild at the same Zone Substation), but only 1 data line can be associated with each polygon. Therefore this cell specifies - where multiple investments are occurring - which ones the NOM should map on "Proposed Investment" but ignore for all other capacity and deferral value maps. The sub-investment with the greatest opportunity for non-network solutions should be kept in the dataset Format: enter 'TRUE' to exclude. Otherwise leave blank or FALSE
Note on D1: Name of NSP or planning manager (for Vic transmission). Units/format: Text, but must conform exactly (case sensitive) to following list: United Energy, Tasnetworks, Transgrid, Essential Energy, Endeavour, Ausgrid, Evoenergy, Ergon Energy, Energex, SA Power Networks, Electranet, Jemena, Ausnet, Citipower-Powercor, AEMO
Note on E1: AER Ref: DT005 TL: Transmission Line TS: Transmission terminal station TCP: Transmission Connection Point ZS: Zone Substation DF: (Distribution) feeder Units/format: Defined code above. Must match exactly (case sensitive)
Note on F1: Some assets may not have a 10-yr forecast, and only have a 5-yr forecast available (e.g. feeders). However, the maps produced will be for 10 years. Marking this field TRUE will keep yr5 loads and support requirements static out to yr10, and automatically include a standard caveat explaining this in the investment_description field. Format: enter 'TRUE' to use 5yr forecast only. Otherwise leave blank.
Note on G1: AER Ref: DT009 Highest operational voltage level of the assets involved in the constraints Units/format: kV (integer)
Note on H1: AER Ref: DT009 Operational voltage level of the assets involved in the constraints on the low side of the transformer Units/format: kV (integer)
Note on I1: AER Ref: DT012 Description of the problem or general asset situation and proposed network solution. Units/format: Free text field. Include special data caveats here if relevant.
Note on J1: Indicate the reliability criteria applied to the network asset. For example n, n-1, n-2, n-1 + risk. Unit/Format: Free text.
Note on K1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on L1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on M1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on N1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on O1: AER Ref: DT006 Total number of customers affected
Note on P1: AER Ref: DT006_a Percent of customers affected Format: Percent, entered as a positive decimal between 0 and 1 (e.g. 15% would be entered as 0.15)
Note on Q1: AER Ref: DT001 Constraint primary investment driver Format: Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage. Must match list exactly (case sensitive)
Note on R1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Demand growth related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on S1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Age/condition related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on T1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Connections related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on U1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Related to investments not falling into one of the other categories. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on V1: AER Ref: DT013 Total value of proposed network solution - should be the sum of Cols P to S (all investment types). If zero leave blank. Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on W1: AER Ref: DT014_a Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on X1: AER Ref: DT014_b Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on Y1: AER Ref: DT017 Saving in cost of capital from defering the project. Note that this does not use Value of Customer Reliability as an Input, as originally specified in AER guidance. Units: $/a (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload. NB: This is not the same calculation as represented in the Annual Deferral Value (ADV) map on the Network Opportunity Maps.
Note on Z1: Provide the component of the total proposed investment (Col T) that is considered deferrable with the non-network alternative/ Includes: • Defering augmentation (reducing project demand growth) • Defering new infrastructure riven by revised reliability criteria • Retiring assets (by reducing demand) • Downsizing assets (by reducing demand) • Extending the life of assets (by reducing the load conditions) Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AA1: AER Ref: DT013_a Annual operating costs (including overheads, risk allowance and contingency allowance if included) Units/Formats: $ AUD (real) Note: It may be useful to view your $ figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AB1: AER Ref: DT015 Provide the expected month and year when investment is planned for commissioning. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AC1: Provide the expected month and year when investment decision is locked in and non-network solutions are no longer an option. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AD1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AE1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AF1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AG1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AH1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on AI1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on AJ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AK1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AL1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AM1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AN1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AO1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AP1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AQ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AR1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AW1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AX1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AY1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AZ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BA1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BB1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BC1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BD1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BE1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BF1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BG1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BH1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BI1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BJ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BK1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BL1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BM1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BN1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BO1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BP1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BQ1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on BR1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on BS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BW1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BX1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BY1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BZ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CA1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CB1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CC1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CD1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CE1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CF1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CG1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CH1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CI1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CJ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CK1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CL1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CM1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CN1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CO1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CP1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CQ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CR1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CS1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CT1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CU1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CV1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CW1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CX1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CY1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CZ1: Provide Probability of Exceedance (POE) to be used in the NOM calculations. Should be the forecast upon which investment decision is based. Unit/Format: integer (10 or 50 ONLY)
Note on DA1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DB1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DC1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DD1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DE1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DF1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DG1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DH1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DI1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DJ1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DK1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DL1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DM1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DN1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DO1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DP1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DQ1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DR1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DS1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DT1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DU1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DV1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DW1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DX1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DY1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DZ1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EA1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EB1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EC1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on ED1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EE1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EF1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EG1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EH1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EI1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EJ1: AER Ref: DT016_a Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EK1: AER Ref: DT016_b Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EL1: AER Ref: DT016 Support Required in Summer. Unit/Format: MVA
Note on EM1: Support Required in Summer. Unit/Format: MVA
Note on EN1: Support Required in Summer. Unit/Format: MVA
Note on EO1: Support Required in Summer. Unit/Format: MVA
Note on EP1: Support Required in Summer. Unit/Format: MVA
Note on EQ1: Support Required in Summer. Unit/Format: MVA
Note on ER1: Support Required in Summer. Unit/Format: MVA
Note on ES1: Support Required in Summer. Unit/Format: MVA
Note on ET1: Support Required in Summer. Unit/Format: MVA
Note on EU1: Support Required in Summer. Unit/Format: MVA
Note on EV1: AER Ref: DT016_a Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EW1: AER Ref: DT016_b Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EX1: AER Ref: DT016 Support Required in Winter. Unit/Format: MVA
Note on EY1: Support Required in winter. Unit/Format: MVA
Note on EZ1: Support Required in winter. Unit/Format: MVA
Note on FA1: Support Required in winter. Unit/Format: MVA
Note on FB1: Support Required in winter. Unit/Format: MVA
Note on FC1: Support Required in winter. Unit/Format: MVA
Note on FD1: Support Required in winter. Unit/Format: MVA
Note on FE1: Support Required in winter. Unit/Format: MVA
Note on FF1: Support Required in winter. Unit/Format: MVA
Note on FG1: Support Required in winter. Unit/Format: MVA
Note on FH1: Supports solution for AER Refs: DT007_a, DT008_a, DT017_a, DT021_a Asset specific power factor Format: Decimal between 0 and 1
Note on FI1: Optional: Description of reactive power requirements in an area. Unit/Format: Free text Note: Using this field will specify MVAr support required on ADV maps and thus not display other capacity related calculations (even if only a space is included " ")
Note on FJ1: AER Ref: DT017/ DT017_a NB: Leave BLANK if not applicable
Note on FK1: AER Ref: DT018 Emergency generation capacity available within constrained area Format: MVA NB: Leave BLANK if not applicable
Note on FL1: AER Ref: DT018_a Emergency generation capacity available within constrained area Format: MW
Note on FM1: AER Ref: DT019/ DT019_a Format: 'Yes' or 'No' Assets marked Yes will have 3yr half hourly data supplied in AER_NOM_emergencyresponse_data.xlsx and those with No will not.
Note on FN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on C2: Only 1 data line associated with CN asset_code so no need to specify exclusions
Note on C3: The capacity situation for feeder (DF) asset was selected as data line to map to available/peak day capacity maps as highest deferrable value. The Zone Sub data line may alternatively be selected based on DNSP preference
Note on F3: Only 5yr forecast available for feeder assets so marked as TRUE
Note on I3: Note comment inserted when mapping DF situation to ZS: "Deferral and capacity values shown are for an investment at AW-03 feeder and thus relate to a smaller area than shown in the map." This is useful IF you choose to map a feeder constraint to zone polygon. An alternative is to create some smaller feeder polygons where such constraints exist.
Note on C6: Zone Substation situation considered less important as no investment taking place, therefore excluded and feeder situation mapped in preference
Note on FN7: ALL data lines now require connections specified to connect data to polygon map regions