## Disclaimer
DISCLAIMER
Essential Energy is registered as a Distribution Network Service Provider. This Distribution Annual Planning Report 2025 has been prepared and published by Essential Energy under clause 5.12.2 and 5.13.2 of the National Electricity Rules to notify Registered Participants and Interested Parties of the results of the distribution network annual planning review and should only be used for those purposes.
This document does not purport to contain all of the information that a prospective investor, participant or potential participant in the National Electricity Market, or any other person or interested parties may require. In preparing this document it is not possible, nor is it intended, for Essential Energy to have regard to the investment objectives, financial situation and particular needs of each person who reads or uses this document.
In all cases, anyone proposing to rely on or use the information in this document should independently verify and check the accuracy, completeness, reliability and suitability of that information for their own purposes.
Accordingly, Essential Energy makes no representations or warranty as to the accuracy, reliability, completeness or suitability for particular purposes of the information in this document. Persons reading or utilising this document acknowledge that Essential Energy and their employees, agents and consultants shall have no liability (including liability to any person by reason of negligence or negligent misstatement) for any statements, opinions, information or matter (expressed or implied) arising out of, contained in or derived from, or for any omissions from, the information in this document, except in so far as liability under any New South Wales and Commonwealth statute cannot be excluded.
Contact
For all enquiries regarding the Distribution Annual Planning Report 2025 and for making written submissions contact:
Essential Energy DM Coordinator PO Box 5730 Port Macquarie NSW 2444 Email: dmcoordinator@essentialenergy.com.au

## ZSSummer
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 25/26 | 26/27 | 27/28 | 28/29 | 29/30
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 33 | 0.999 | 14.6 | 14.74 | 14.94 | 15.18 | 15.38 | 17.04 | 2.5
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 33 | 1 | 17.35 | 17.92 | 18.45 | 19 | 19.45 | 16.84 | 3.5
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 44 | 1 | 12.73 | 12.77 | 12.82 | 12.84 | 12.87 | 0 | 2.5
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 16.5 | 1 | 12.19 | 12.23 | 12.25 | 12.26 | 12.32 | 18.14 | 3
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.995 | 21.41 | 21.71 | 22.08 | 22.39 | 22.73 | 24.11 | 2
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 220 | 0.998 | 97.37 | 98.62 | 99.65 | 100.85 | 102.16 | 0 | 2.5
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 33 | 1 | 7.91 | 7.98 | 8.03 | 8.1 | 8.17 | 11.44 | 2
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 27.5 | 0.997 | 15.4 | 15.4 | 15.41 | 15.4 | 15.38 | 5.28 | 3
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 33 | 1 | 15.53 | 15.64 | 15.78 | 15.92 | 16.02 | 17.15 | 3.5
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 22 | 0.999 | 11.62 | 11.79 | 11.9 | 12.02 | 12.17 | 16.75 | 1.5
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 33 | 0.982 | 27.47 | 27.82 | 27.97 | 28.27 | 28.55 | 30.45 | 1.5
Lismore | Ballina 132kV | 132/66 | 35/45/60 |  |  | 0 | 0.947 | 20.18 | 20.54 | 20.76 | 21.06 | 21.3 | 0 | 0.5
Lismore | Dunoon | 132/11 | 10 | 10 |  | 11 | 0.991 | 6.03 | 6.03 | 6.03 | 6.04 | 6.01 | 8.61 | 2
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 49.5 | 0.999 | 18.81 | 19.06 | 19.27 | 19.5 | 19.67 | 19.09 | 1
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 11 | 0.991 | 7.45 | 7.36 | 7.27 | 7.18 | 7.13 | 7.6 | 3
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 17.6 | 0.993 | 5.95 | 6 | 6.05 | 6.09 | 6.14 | 8.71 | 1.5
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 264 | 0.983 | 93.63 | 94.55 | 95.2 | 95.75 | 96.4 | 0 | 1
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 25.3 | 0.998 | 13.47 | 13.4 | 13.38 | 13.35 | 13.31 | 17.07 | 1.5
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 52.8 | 0.963 | 7.47 | 7.56 | 7.54 | 7.61 | 7.68 | 7.88 | 4.5
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 33 | 0.997 | 22.08 | 22.34 | 22.63 | 22.85 | 23.04 | 16.2 | 4
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 11 | 0.998 | 7.98 | 7.99 | 8 | 8.02 | 8.05 | 12.34 | 2.5
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | 1 | 11.17 | 11.41 | 11.65 | 11.91 | 12.16 | 13.8 | 2
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 11 | 0.999 | 7.23 | 7.28 | 7.34 | 7.37 | 7.4 | 8.14 | 2
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 2.75 | 0.914 | 0.87 | 0.87 | 0.87 | 0.87 | 0.86 | 0.97 | 7
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0.991 | 33.75 | 33.68 | 33.63 | 33.63 | 33.63 | 0 | 1
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 33 | 0.995 | 25.66 | 25.78 | 25.87 | 25.92 | 26 | 18.44 | 3
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 3.85 | 0.996 | 3.16 | 3.13 | 3.11 | 3.08 | 3.06 | 0 | 4.5
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 2.75 | 1 | 1.22 | 1.21 | 1.21 | 1.2 | 1.2 | 1.02 | 11.5
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 5.5 | 0.999 | 0.55 | 0.55 | 0.55 | 0.56 | 0.56 | 0.71 | 1
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.996 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.75 | 7
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 27.5 | 1 | 16.01 | 15.92 | 15.99 | 15.98 | 15.98 | 12.23 | 0.5
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 26.95 | 0.992 | 15.93 | 15.84 | 15.89 | 15.88 | 15.86 | 13.44 | 0.5
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | 0.915 | 2.75 | 2.79 | 2.83 | 2.88 | 2.92 | 3.01 | 1
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.96 | 9.85 | 9.99 | 10.15 | 10.31 | 10.45 | 12.08 | 2
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0.991 | 0.44 | 0.44 | 0.45 | 0.45 | 0.45 | 0 | 2
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.66 | 0.952 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.36 | 2
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.55 | 0.991 | 0.44 | 0.44 | 0.45 | 0.45 | 0.46 | 0.27 | 2
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | 1 | 1.3 | 1.35 | 1.4 | 1.44 | 1.47 | 1.22 | 3
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 25.3 | 0.996 | 11.2 | 11.28 | 11.39 | 11.46 | 11.56 | 11.94 | 1
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 33 | 1 | 9.61 | 9.69 | 9.76 | 9.8 | 9.83 | 9.98 | 1.5
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 33 | 0.997 | 8.21 | 8.19 | 8.16 | 8.14 | 8.12 | 0 | 2.5
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 50.6 | 0.995 | 22.99 | 23.91 | 24.7 | 25.37 | 26.06 | 17.83 | 1.5
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 33 | 0.996 | 21.22 | 21.23 | 21.25 | 21.26 | 21.28 | 11.03 | 2
Coffs Harbour | Dorrigo | 132/11, 66/11 | 7.5/10 | 10 |  | 11 | 1 | 1.99 | 1.95 | 1.92 | 1.89 | 1.86 | 2.84 | 7
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 17.6 | 1 | 6.49 | 6.54 | 6.57 | 6.61 | 6.65 | 8.94 | 1.5
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 6.88 | 0.999 | 2.75 | 2.71 | 2.69 | 2.67 | 2.64 | 3.28 | 6
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 26.95 | 0.924 | 9.59 | 9.78 | 9.95 | 10.15 | 10.33 | 8.28 | 2.5
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.983 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.5 | 1.5
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 33 | 0.994 | 11.23 | 11.44 | 11.64 | 11.86 | 12.05 | 15.04 | 2
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 33 | 1 | 9.32 | 9.37 | 9.44 | 9.44 | 9.5 | 10.9 | 2
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 25.3 | 0.997 | 7.69 | 7.73 | 7.76 | 7.8 | 7.83 | 8.37 | 2.5
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 33 | 0.995 | 10.78 | 10.77 | 10.74 | 10.72 | 10.72 | 12.16 | 3.5
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.4 | 0.995 | 1.61 | 1.62 | 1.62 | 1.62 | 1.63 | 1.72 | 5
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.995 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 1.53 | 2.5
Kempsey | North St | 33/11 | 16 |  |  | 0 | 0.992 | 10.71 | 10.79 | 10.89 | 10.94 | 11.02 | 7.92 | 2.5
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 16.5 | 0.984 | 8.13 | 8.18 | 8.23 | 8.3 | 8.33 | 6.83 | 2
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 5.5 | 0.98 | 4.15 | 4.16 | 4.17 | 4.17 | 4.18 | 2.85 | 2.5
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 13.75 | 0.981 | 7.1 | 7.16 | 7.22 | 7.26 | 7.32 | 7.51 | 3.5
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 33 | 0.999 | 19.07 | 19.15 | 19.24 | 19.27 | 19.31 | 14.5 | 1.5
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.3 | 0.994 | 1.37 | 1.37 | 1.38 | 1.38 | 1.38 | 1.36 | 8
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 33 | 0.999 | 19.54 | 19.75 | 19.97 | 20.16 | 20.35 | 27.37 | 1.5
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 3.85 | 1 | 2.6 | 2.65 | 2.69 | 2.73 | 2.77 | 3 | 1
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 8.8 | 0.986 | 6.13 | 6.37 | 6.53 | 6.69 | 6.83 | 9.33 | 2
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 22 | 0.986 | 13.1 | 13.11 | 13.08 | 13.1 | 13.11 | 7.27 | 2
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 16.5 | 0.996 | 12.98 | 13.19 | 13.33 | 13.47 | 13.59 | 13.01 | 1
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.4 | 0.999 | 1.8 | 1.81 | 1.81 | 1.83 | 1.83 | 2.21 | 1
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0.994 | 13 | 13.13 | 13.23 | 13.38 | 13.45 | 0 | 0.5
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | 0.985 | 0.91 | 0.9 | 0.89 | 0.88 | 0.87 | 1.06 | 0.5
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.4 | 1 | 3.45 | 3.48 | 3.52 | 3.56 | 3.59 | 4.15 | 1.5
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 22 | 0.999 | 6.75 | 6.7 | 6.64 | 6.6 | 6.55 | 8.69 | 1
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 7.7 | 0.997 | 6.65 | 6.68 | 6.7 | 6.73 | 6.75 | 7.81 | 1.5
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 5.5 | 0.978 | 3.75 | 3.74 | 3.73 | 3.72 | 3.71 | 1.89 | 1.5
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.996 | 2.93 | 2.93 | 2.91 | 2.89 | 2.89 | 2.77 | 2
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.997 | 13.76 | 13.75 | 13.77 | 13.76 | 13.76 | 12.76 | 0.5
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.997 | 8.46 | 8.51 | 8.55 | 8.61 | 8.64 | 10.2 | 3
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 6.88 | 1 | 3.85 | 3.86 | 3.89 | 3.9 | 3.92 | 4.85 | 2
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 27.5 | 0.994 | 11.84 | 11.75 | 11.71 | 11.65 | 11.55 | 8.72 | 2.5
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 17.6 | 0.999 | 5.68 | 5.7 | 5.71 | 5.72 | 5.74 | 4.94 | 12
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 22 | 0.988 | 19.19 | 19.21 | 19.19 | 19.27 | 19.29 | 9.99 | 2.5
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 11 | 0.985 | 11.45 | 11.41 | 11.4 | 11.37 | 11.38 | 8.06 | 2.5
Stroud | Booral | 33/11 | 3 | 2.5 |  | 2.75 | 0.984 | 1.73 | 1.75 | 1.76 | 1.77 | 1.78 | 1.27 | 0.5
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.994 | 3.88 | 3.89 | 3.89 | 3.9 | 3.9 | 2.67 | 2
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.982 | 8.92 | 8.92 | 8.9 | 8.93 | 8.92 | 5.68 | 0.5
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.974 | 8.77 | 8.91 | 9.07 | 9.17 | 9.28 | 6.51 | 1.5
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.15 | 0.939 | 2.63 | 2.66 | 2.68 | 2.7 | 2.73 | 1.74 | 1.5
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.988 | 3.89 | 3.91 | 3.92 | 3.91 | 3.93 | 2.95 | 1.5
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 8.8 | 0.999 | 4.39 | 4.4 | 4.4 | 4.41 | 4.4 | 3.96 | 3
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 66 | 0.995 | 33.37 | 33.33 | 33.43 | 33.47 | 33.46 | 0.01 | 2
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 5.5 | 0.98 | 2.76 | 2.76 | 2.76 | 2.76 | 2.75 | 2.13 | 1.5
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 1 | 8.45 | 8.47 | 8.46 | 8.46 | 8.45 | 0 | 1
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.998 | 8.54 | 8.56 | 8.54 | 8.58 | 8.57 | 7.75 | 1
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply |  |  |  |  | 0 | 0.999 | 3.9 | 4.26 | 4.27 | 4.28 | 4.28 | 2.71 | 4
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 2.75 | 0.988 | 1.59 | 2.06 | 2.06 | 2.06 | 2.05 | 1.9 | 7.5
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 13.75 | 1 | 8.7 | 8.74 | 8.76 | 8.79 | 8.82 | 9.41 | 2
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.902 | 0.35 | 0.35 | 0.36 | 0.36 | 0.37 | 0.22 | 2
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 13.75 | 0.994 | 7.29 | 7.31 | 7.32 | 7.33 | 7.35 | 6.43 | 1
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 17.6 | 0.999 | 6.65 | 6.65 | 6.65 | 6.64 | 6.64 | 5.97 | 0.5
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 3.85 | 0.951 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.21 | 3.5
Armidale | Uralla | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 2.73 | 2.74 | 2.76 | 2.77 | 2.78 | 3.62 | 1.5
Armidale | Walcha South 66/22kV | 66/22 | 8 | 8/10 |  | 8.8 | 0.761 | 1.53 | 1.54 | 1.56 | 1.58 | 1.59 | 1.13 | 11
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.3 | 0.998 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.25 | 2
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.952 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 1.19 | 1
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | 0.74 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | 0.5
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 22 | 1 | 5.81 | 5.83 | 5.83 | 5.84 | 5.85 | 7.19 | 2
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 5.5 | 1 | 3.49 | 3.51 | 3.54 | 3.55 | 3.58 | 3.22 | 1.5
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.958 | 0.7 | 0.69 | 0.69 | 0.68 | 0.67 | 0.86 | 1
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.3 | 0.967 | 2.5 | 2.53 | 2.57 | 2.6 | 2.64 | 2.15 | 2
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 33 | 1 | 20.47 | 20.42 | 20.42 | 20.38 | 20.46 | 15.31 | 2.5
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | 0.777 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04 | 0.82 | 3
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.65 | 1 | 0.84 | 0.84 | 0.84 | 0.84 | 0.85 | 0 | 9
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 5.5 | 0.976 | 3.39 | 3.43 | 3.45 | 3.49 | 3.51 | 1.42 | 6.5
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 5.5 | 0.978 | 2.37 | 2.42 | 2.46 | 2.5 | 2.54 | 0.59 | 0.5
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | 0.909 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.12 | 3
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.4 | 0.996 | 2.8 | 2.79 | 2.77 | 2.76 | 2.75 | 2.46 | 6
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.95 | 2.19 | 2.21 | 2.22 | 2.23 | 2.25 | 0.95 | 6
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 16.5 | 1 | 18.14 | 18.42 | 18.66 | 18.9 | 19.07 | 6.85 | 2.5
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.999 | 6.51 | 6.58 | 6.67 | 6.72 | 6.77 | 2.72 | 8.5
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.991 | 1.38 | 1.42 | 1.46 | 1.49 | 1.53 | 0.56 | 2.5
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 2.75 | 0.918 | 1.16 | 1.18 | 1.19 | 1.21 | 1.22 | 0.54 | 6
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 33 | 0.998 | 22.07 | 23.85 | 27.89 | 31.55 | 34.74 | 14.47 | 3.5
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.95 | 2.92 | 2.92 | 2.91 | 2.91 | 2.91 | 1.33 | 1
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.996 | 1.36 | 1.37 | 1.39 | 1.42 | 1.45 | 0.24 | 2.5
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | 0.992 | 2.86 | 2.89 | 2.89 | 2.93 | 2.94 | 0.05 | 2.5
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.968 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 1.33 | 10.5
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 5.5 | 0.992 | 2.11 | 2.12 | 2.12 | 2.12 | 2.12 | 0.69 | 8
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 5.5 | 1 | 3.15 | 3.16 | 3.17 | 3.17 | 3.18 | 2.57 | 5.5
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0.861 | 1.58 | 1.6 | 1.61 | 1.62 | 1.63 | 0.74 | 2
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.993 | 17.39 | 17.56 | 17.73 | 17.85 | 17.95 | 10.15 | 2
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 11 | 0.983 | 5.37 | 5.4 | 5.44 | 5.48 | 5.51 | 3.32 | 6.5
Narrabri | Wee Waa | 66/22 | 8.8/10 | 16 |  | 11 | 0.969 | 8.08 | 8.06 | 8.03 | 8.01 | 7.99 | 2.89 | 3
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.15 | 0.987 | 4.08 | 4.12 | 4.14 | 4.17 | 4.2 | 1.75 | 3
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 33 | 1 | 24.99 | 25.01 | 25.04 | 24.98 | 25.03 | 13.03 | 0
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0.946 | 0.26 | 0.26 | 0.27 | 0.27 | 0.28 | 0.05 | 4
Tamworth | Attunga | 66/11 | 5 | 8 |  | 5.5 | 0.95 | 3.67 | 3.59 | 3.52 | 3.45 | 3.38 | 1.73 | 4.5
Tamworth | Barraba | 66/11 | 5 | 5 |  | 5.5 | 0.998 | 2.07 | 2.05 | 2.03 | 2.02 | 2.01 | 1.96 | 2.5
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.1 | 1 | 0.68 | 0.69 | 0.69 | 0.7 | 0.71 | 0.63 | 1
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.2 | 0.99 | 1 | 1 | 1 | 1.01 | 1.01 | 0.17 | 2.5
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.65 | 0.96 | 1.13 | 1.13 | 1.12 | 1.12 | 1.12 | 0.41 | 8
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.95 | 1.3 | 1.28 | 1.27 | 1.26 | 1.25 | 0.65 | 3
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 33 | 0.999 | 11.59 | 22.1 | 23.87 | 25.39 | 25.32 | 3.17 | 4.5
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.987 | 6.68 | 6.76 | 6.85 | 6.93 | 6.98 | 4.83 | 1.5
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 6.88 | 0.9 | 6.1 | 6.19 | 6.25 | 6.31 | 6.35 | 2.74 | 2.5
Tamworth | Murrurundi | 33/11 | 5/8 |  |  | 0 | 0.998 | 2.72 | 2.78 | 2.84 | 2.89 | 2.95 | 1.92 | 1
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 2.75 | 0.975 | 1.94 | 1.93 | 1.93 | 1.93 | 1.92 | 1.3 | 2.5
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 33 | 0.999 | 19.73 | 19.86 | 19.94 | 20.02 | 20.1 | 13 | 1.5
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.992 | 7.13 | 7.11 | 7.12 | 7.12 | 7.11 | 3.66 | 3
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 11 | 0.993 | 5.47 | 5.46 | 5.46 | 5.46 | 5.45 | 0 | 3
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.977 | 0.8 | 0.82 | 0.84 | 0.85 | 0.87 | 0.18 | 5.5
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 50.6 | 1 | 33.23 | 33.45 | 33.66 | 33.9 | 34.07 | 12.94 | 0.5
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 33 | 0.993 | 24.82 | 25.03 | 25.24 | 25.44 | 25.67 | 15 | 2.5
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.938 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.12 | 9
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 6.88 | 0.995 | 2.2 | 2.18 | 2.16 | 2.13 | 2.12 | 1.4 | 3
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 14.3 | 1 | 7.85 | 7.89 | 7.88 | 7.89 | 7.91 | 6.72 | 1.5
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 11 | 0.999 | 5.09 | 5.13 | 5.18 | 5.2 | 5.26 | 4.24 | 1
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | 0.999 | 3.8 | 3.83 | 3.84 | 3.86 | 3.89 | 2.33 | 1.5
Beryl | Mudgee | 132/22, 66/22 | 18/30 | 30 |  | 33 | 1 | 28.55 | 29.04 | 29.55 | 30.07 | 30.6 | 18.38 | 1.5
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 2.75 | 1 | 2.79 | 2.78 | 2.77 | 2.76 | 2.76 | 1.71 | 2
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 2.75 | 0.974 | 1.42 | 1.43 | 1.44 | 1.45 | 1.46 | 0.79 | 2
Wellington | Wellington 11kV | 132/11, 66/11 | 8/11 | 15 |  | 12.1 | 0.993 | 10.21 | 10.2 | 10.22 | 10.2 | 10.19 | 5.79 | 0.5
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 11 | 0.996 | 6.52 | 6.65 | 6.8 | 6.94 | 7.08 | 3.74 | 2
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 99 | 0.999 | 62.77 | 62.66 | 62.98 | 63.03 | 63.03 | 0 | 3.5
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 33 | 0.971 | 21.21 | 21.15 | 21.15 | 21.11 | 21.07 | 6.63 | 1.5
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 33 | 0.992 | 23.01 | 23.5 | 23.91 | 24.25 | 24.6 | 16.22 | 0.5
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 25.3 | 0.983 | 17.48 | 17.63 | 17.81 | 17.96 | 18.06 | 12.51 | 1
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 33 | 0.993 | 21.14 | 21.41 | 21.63 | 21.84 | 22.08 | 16.95 | 0.5
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | 0.977 | 1.57 | 1.57 | 1.57 | 1.56 | 1.56 | 1.19 | 2
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 13.2 | 0.994 | 7.55 | 7.59 | 7.62 | 7.66 | 7.69 | 4.77 | 1.5
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.95 | 1.7 | 1.72 | 1.73 | 1.75 | 1.77 | 1.02 | 2
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 26.4 | 0.996 | 14.02 | 14.22 | 14.41 | 14.6 | 14.74 | 7.9 | 2.5
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 11 | 0.997 | 7.24 | 7.36 | 7.49 | 7.59 | 7.7 | 3.54 | 0.5
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 27.5 | 0.983 | 8.78 | 8.97 | 9.16 | 9.31 | 9.48 | 2.39 | 6
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.985 | 6.46 | 6.56 | 6.63 | 6.71 | 6.78 | 2.46 | 4
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.84 | 3.54 | 3.6 | 3.65 | 3.7 | 3.74 | 0.83 | 6.5
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.1 | 0.992 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0.5
Nyngan | Cobar CSA | 132/11 | 15/18 | 30/45 |  | 19.8 | 0.932 | 24.57 | 25.04 | 25.51 | 25.9 | 26.31 | 0 | 2.5
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 16.5 | 0.776 | 4.36 | 4.65 | 4.78 | 4.87 | 5.01 | 0 | 56.5
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 22 | 0.912 | 14.06 | 14.34 | 14.56 | 14.79 | 14.99 | 0 | 143.5
Nyngan | Cobar Town | 66/22 | 8/11 | 10 |  | 11 | 0.952 | 6.62 | 6.69 | 6.77 | 6.86 | 6.93 | 4.94 | 6
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0.869 | 1.64 | 1.64 | 1.63 | 1.62 | 1.61 | 0 | 9.5
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 33 | 0.999 | 34.72 | 35.12 | 35.53 | 35.98 | 36.31 | 0 | 11
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 11 | 1 | 5.48 | 5.48 | 5.48 | 5.47 | 5.49 | 2.75 | 5
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply |  |  |  |  | 0 | 0.996 | 37.39 | 38.06 | 38.22 | 38.39 | 38.58 | 26.2 | 15
Broken Hill | Wilcannia 33kV |  |  |  |  | 0 | 0.897 | 0.7 | 0.71 | 0.72 | 0.72 | 0.73 | 0.33 | 3
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 5.5 | 0.999 | 0.99 | 0.99 | 1 | 1 | 1 | 1.03 | 2.5
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.65 | 0.987 | 1.29 | 1.34 | 1.38 | 1.44 | 1.48 | 0.95 | 5.5
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.65 | 1 | 0.43 | 0.42 | 0.42 | 0.42 | 0.42 | 0.13 | 2
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 16.5 | 0.914 | 5.57 | 5.93 | 5.92 | 5.92 | 5.92 | 0 | 2
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | 0.981 | 0.64 | 0.65 | 0.65 | 0.66 | 0.66 | 0.35 | 1
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.4 | 0.989 | 2.37 | 2.36 | 2.35 | 2.34 | 2.35 | 0.26 | 3.5
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 3.85 | 0.984 | 1.19 | 1.21 | 1.24 | 1.26 | 1.28 | 0.68 | 3.5
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 11 | 1 | 9.21 | 9.14 | 9.1 | 9.05 | 9.02 | 11.74 | 3
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 33 | 0.929 | 12.27 | 12.17 | 12.06 | 11.97 | 11.88 | 7.81 | 0.5
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 33 | 0.997 | 16.43 | 16.32 | 16.28 | 16.2 | 16.13 | 13.59 | 2.5
Orange | Orange West | 66/11 | 30 | 30 |  | 33 | 1 | 11.19 | 11.2 | 11.19 | 11.2 | 11.2 | 12.38 | 3
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 2.75 | 1 | 1.45 | 1.44 | 1.45 | 1.45 | 1.46 | 1.43 | 2.5
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 26.4 | 0.958 | 13.2 | 13.23 | 13.25 | 13.27 | 13.29 | 2.21 | 33
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.4 | 0.988 | 3.46 | 3.47 | 3.47 | 3.48 | 3.49 | 2.95 | 1
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 22 | 0.988 | 10.4 | 10.41 | 10.44 | 10.45 | 10.48 | 5.71 | 3
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 2.75 | 0.998 | 1.8 | 1.8 | 1.81 | 1.81 | 1.81 | 1.85 | 2
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 33 | 1 | 20.45 | 20.45 | 20.48 | 20.44 | 20.48 | 13.28 | 1
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 66 | 0.984 | 22.96 | 23.33 | 23.7 | 24.02 | 24.33 | 11.24 | 1.5
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 22 | 0.998 | 20.3 | 20.25 | 20.25 | 20.27 | 20.27 | 15.11 | 1
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0.882 | 0.36 | 0.35 | 0.34 | 0.34 | 0.34 | 0 | 0.5
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 49.5 | 0.97 | 32.61 | 33.03 | 33.52 | 34.02 | 34.54 | 0 | 3.5
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 16.5 | 0.957 | 3.53 | 3.57 | 3.54 | 3.59 | 3.62 | 4.04 | 1
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 33 | 0.993 | 19.33 | 19.41 | 19.48 | 19.51 | 19.6 | 12.68 | 1.5
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 11 | 0.967 | 4.85 | 5.06 | 5.26 | 5.44 | 5.61 | 1.73 | 1
Parkes | Trundle | 66/22 | 8 | 5 |  | 5.5 | 0.995 | 13.64 | 14.48 | 15.24 | 15.97 | 16.64 | 2.37 | 40
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 11 | 0.999 | 8.52 | 8.71 | 8.87 | 9.02 | 9.16 | 4.79 | 5.5
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 33 | 0.982 | 13.63 | 13.62 | 13.64 | 13.64 | 13.66 | 9.04 | 4.5
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 7.7 | 0.955 | 4.06 | 4.13 | 4.18 | 4.24 | 4.3 | 3.05 | 2.5
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 5.5 | 0.911 | 5.31 | 5.33 | 5.34 | 5.35 | 5.36 | 1.3 | 2
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.4 | 0.99 | 1.99 | 2 | 2.02 | 2.03 | 2.05 | 0.51 | 3.5
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 49.5 | 1 | 17.46 | 17.91 | 18.43 | 18.83 | 19.3 | 14.46 | 0.5
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.3 | 0.98 | 1.14 | 1.14 | 1.15 | 1.16 | 1.17 | 1.37 | 3.5
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 44 | 0.999 | 23.44 | 23.86 | 24.24 | 24.56 | 24.86 | 0 | 2.5
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.998 | 5.63 | 5.57 | 5.52 | 5.48 | 5.43 | 6.78 | 5
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 13.75 | 0.999 | 6.2 | 6.2 | 6.19 | 6.18 | 6.18 | 8.36 | 2.5
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 13.75 | 1 | 5.76 | 5.81 | 5.85 | 5.9 | 5.95 | 5.55 | 1
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | 0.981 | 2.24 | 2.24 | 2.23 | 2.23 | 2.22 | 2.82 | 3.5
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 5.5 | 0.996 | 0.81 | 0.82 | 0.83 | 0.84 | 0.85 | 0.75 | 2
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 5.5 | 0.931 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0 | 1.5
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 22 | 0.999 | 8.88 | 8.86 | 8.87 | 8.87 | 8.87 | 7.3 | 2
Cooma | Eucumbene | 66/11 | 3 |  |  | 0 | 0.941 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.08 | 0.5
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 33 | 1 | 4.06 | 4.11 | 4.16 | 4.2 | 4.25 | 4.12 | 8.5
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0.912 | 0.22 | 0.23 | 0.23 | 0.23 | 0.23 | 0.3 | 2
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 11 | 1 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 2.89 | 3.5
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 0.904 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 1
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.881 | 0.2 | 0.21 | 0.21 | 0.22 | 0.22 | 0 | 0.5
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 1 | 0.37 | 0.37 | 0.38 | 0.38 | 0.38 | 0.19 | 2.5
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0 | 1.5
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 11 | 0.95 | 1 | 1 | 1 | 1 | 1 | 0.14 | 1
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0.98 | 0.43 | 0.47 | 0.5 | 0.53 | 0.56 | 0 | 2
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0.992 | 2.59 | 2.61 | 2.62 | 2.63 | 2.63 | 0 | 3.5
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.991 | 2 | 2.01 | 2.02 | 2.04 | 2.04 | 0.03 | 1.5
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.991 | 30.6 | 30.67 | 30.78 | 30.92 | 30.99 | 0 | 2.5
Bega | Bermagui | 33/11 | 5 | 5 |  | 5.5 | 1 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 3.23 | 1.5
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0.983 | 0.78 | 0.79 | 0.79 | 0.8 | 0.81 | 0.66 | 5
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 2.75 | 0.999 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 2.15 | 1
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.998 | 4.03 | 4.07 | 4.12 | 4.16 | 4.21 | 5.98 | 2
Bega | Edrom | 66/11 | 5 | 5 |  | 5.5 | 0.876 | 2.27 | 2.23 | 2.19 | 2.17 | 2.14 | 0 | 0.5
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 1 | 3.86 | 3.83 | 3.8 | 3.77 | 3.76 | 0 | 3
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.986 | 12.82 | 12.88 | 12.87 | 12.92 | 12.93 | 10.65 | 3
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 17.6 | 0.999 | 11.5 | 11.52 | 11.56 | 11.6 | 11.64 | 12.51 | 2
Bega | Quira | 66/11 | 5 |  |  | 0 | 0.968 | 1.42 | 1.44 | 1.46 | 1.48 | 1.5 | 1.12 | 1.5
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 14.3 | 0.997 | 4.09 | 4.11 | 4.11 | 4.12 | 4.13 | 1.69 | 0.5
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | 1 | 4.63 | 4.56 | 4.53 | 4.5 | 4.46 | 0 | 0.5
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.902 | 0.72 | 0.75 | 0.77 | 0.78 | 0.8 | 0.45 | 1.5
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 2.75 | 0.994 | 1.35 | 1.36 | 1.38 | 1.39 | 1.4 | 1.52 | 2.5
Tumut | Batlow | 66/11 | 5 | 5 |  | 5.5 | 0.977 | 1.47 | 1.45 | 1.43 | 1.41 | 1.39 | 1.37 | 13.5
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 8.8 | 0.996 | 5.99 | 6.1 | 6.21 | 6.33 | 6.45 | 3.92 | 1.5
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.1 | 0.951 | 1.1 | 1.11 | 1.12 | 1.14 | 1.15 | 0.57 | 1
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 1
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | 0.629 | 0.69 | 0.71 | 0.74 | 0.76 | 0.78 | 0.41 | 0.5
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 8.8 | 0.992 | 6.8 | 6.75 | 6.71 | 6.68 | 6.65 | 3.63 | 6.5
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 33 | 0.992 | 12.12 | 12.09 | 12.04 | 12.04 | 12.02 | 7.5 | 4
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0.998 | 7.67 | 7.79 | 7.9 | 8.02 | 8.14 | 9.87 | 1.5
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 5.5 | 0.971 | 4.7 | 4.87 | 5.01 | 5.13 | 5.26 | 3.77 | 2
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 11 | 0.999 | 0.9 | 0.91 | 0.91 | 0.92 | 0.92 | 0 | 0.5
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 33 | 0.998 | 9.84 | 10.09 | 10.3 | 10.49 | 10.66 | 14.31 | 2.5
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 33 | 0.992 | 10.64 | 10.53 | 10.43 | 10.34 | 10.25 | 9.49 | 2
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 33 | 0.999 | 21.03 | 21.04 | 21.03 | 21.08 | 21 | 19.97 | 1.5
Queanbeyan | South Jerrabomberra | 132/11 | 30/40/50 | 30/40/50 |  | 55 | 0.998 | 4.05 | 9.45 | 14.85 | 20.25 | 25.65 | 0 | 0
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 8.8 | 1 | 3.59 | 3.59 | 3.58 | 3.58 | 3.59 | 5.21 | 1
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 2.75 | 0.941 | 2.17 | 2.18 | 2.18 | 2.19 | 2.2 | 2.76 | 2
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 20.9 | 0.999 | 12.94 | 13.18 | 13.48 | 13.76 | 14 | 8.8 | 4
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 11 | 0.996 | 3.75 | 3.76 | 3.77 | 3.79 | 3.8 | 4.76 | 1.5
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 33 | 1 | 8.21 | 8.42 | 8.63 | 8.82 | 9.04 | 4.44 | 2
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.998 | 39.78 | 39.73 | 39.69 | 39.74 | 39.72 | 0 | 1.5
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 16.5 | 0.993 | 8.87 | 8.93 | 9 | 9.07 | 9.11 | 8.67 | 1.5
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 16.5 | 0.99 | 6.72 | 6.81 | 6.89 | 6.95 | 7.03 | 3.07 | 2
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.957 | 7.39 | 7.5 | 7.58 | 7.69 | 7.78 | 0 | 13
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 15.4 | 0.848 | 5.59 | 5.28 | 5.1 | 5.02 | 5.04 | 1.58 | 3.5
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | 0.965 | 1.64 | 1.64 | 1.64 | 1.63 | 1.63 | 1.48 | 3.5
Cowra | Canowindra | 66/11 | 5 | 8 |  | 5.5 | 0.992 | 6.04 | 6.03 | 6.02 | 6.02 | 6.03 | 3.95 | 1.5
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 33 | 1 | 19.71 | 19.72 | 19.75 | 19.71 | 19.73 | 11.81 | 2
Cowra | Grenfell | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 3.69 | 3.62 | 3.55 | 3.49 | 3.43 | 4.39 | 2
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.98 | 0.85 | 0.87 | 0.88 | 0.9 | 0.91 | 0.68 | 3.5
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 5.5 | 0.991 | 3.35 | 3.38 | 3.42 | 3.46 | 3.5 | 3.22 | 1.5
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 20.9 | 0.994 | 11.77 | 11.79 | 11.84 | 11.85 | 11.86 | 8 | 6
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.15 | 0.962 | 1.71 | 1.72 | 1.73 | 1.75 | 1.76 | 0.41 | 12
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 11 | 0.988 | 4.58 | 4.64 | 4.71 | 4.78 | 4.85 | 3.99 | 4
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 33 | 1 | 17.38 | 17.45 | 17.47 | 17.5 | 17.55 | 11.03 | 4.5
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 2.75 | 1 | 1 | 1 | 1 | 1 | 1 | 1.36 | 2
Yass | Marilba | 66/11 | 3 |  |  | 0 | 0.999 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.37 | 1
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | 0.995 | 5.74 | 5.82 | 5.92 | 6.02 | 6.1 | 9.77 | 1.5
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 14.3 | 0.994 | 11.52 | 11.48 | 11.49 | 11.47 | 11.46 | 9.54 | 3.5
Temora | Anona | 66/22 | 3 | 2.5 |  | 2.75 | 0.983 | 1.34 | 1.36 | 1.37 | 1.37 | 1.38 | 1.02 | 3
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 2.75 | 0.993 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.65 | 3
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.3 | 0.999 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 0.77 | 3
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | 0.978 | 0.23 | 0.24 | 0.24 | 0.25 | 0.25 | 0.17 | 1.5
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.999 | 20.75 | 20.79 | 20.84 | 20.87 | 20.9 | 0 | 2
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 11 | 0.996 | 7.68 | 7.67 | 7.67 | 7.67 | 7.68 | 6.19 | 2
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 11 | 0.999 | 9.12 | 9.31 | 9.45 | 9.59 | 9.72 | 5.67 | 1.5
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.3 | 0.998 | 0.73 | 0.73 | 0.74 | 0.74 | 0.75 | 0.3 | 5.5
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 33 | 1 | 11.66 | 13.81 | 15.91 | 17.99 | 20.11 | 0.34 | 3
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/8 | 6.75/8 |  | 8.8 | 0.997 | 10.13 | 10.34 | 10.56 | 10.77 | 10.93 | 5.32 | 0
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.4 | 0.962 | 1.44 | 1.43 | 1.43 | 1.42 | 1.42 | 0 | 2
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 8.8 | 0.995 | 5.06 | 5.16 | 5.23 | 5.29 | 5.36 | 4.55 | 4
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.3 | 0.916 | 1.38 | 1.41 | 1.43 | 1.45 | 1.47 | 0.81 | 2.5
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 15.4 | 0.97 | 5.52 | 5.68 | 5.84 | 6 | 6.16 | 2.68 | 0.5
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | 0.994 | 0.57 | 0.58 | 0.59 | 0.6 | 0.61 | 0.26 | 3.5
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 16.5 | 0.999 | 7.22 | 7.25 | 7.27 | 7.31 | 7.33 | 4.08 | 5
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | 0.999 | 12.71 | 12.84 | 12.97 | 13.08 | 13.17 | 0 | 3.5
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.988 | 0.51 | 0.52 | 0.53 | 0.53 | 0.54 | 0.42 | 1
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.2 | 1 | 1.64 | 1.64 | 1.64 | 1.64 | 1.65 | 0 | 1
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 7.59 | 0.987 | 4.14 | 4.14 | 4.13 | 4.14 | 4.13 | 0.61 | 2.5
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.1 | 0.999 | 1.11 | 1.12 | 1.14 | 1.16 | 1.17 | 0.8 | 1.5
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 33 | 0.985 | 19.01 | 19.09 | 19.18 | 19.32 | 19.37 | 10.44 | 1
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 14.63 | 0.997 | 12.42 | 12.48 | 12.58 | 12.65 | 12.74 | 10.28 | 3
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0.992 | 0.19 | 0.18 | 0.17 | 0.16 | 0.15 | 0 | 11
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 33 | 0.998 | 17.62 | 17.61 | 17.63 | 17.6 | 17.62 | 4.9 | 1
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 5.5 | 0.995 | 2.47 | 2.55 | 2.64 | 2.71 | 2.8 | 2.12 | 1.5
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 27.5 | 0.999 | 18.34 | 18.36 | 18.39 | 18.39 | 18.45 | 12.96 | 2.5
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 5.5 | 0.985 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 2.5 | 2.5
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 22 | 0.98 | 11.47 | 11.71 | 11.9 | 12.09 | 12.34 | 2.53 | 1.5
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 17.6 | 0.997 | 4.99 | 4.98 | 4.98 | 4.98 | 4.97 | 3.55 | 4
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 7.7 | 0.989 | 3.58 | 3.55 | 3.53 | 3.5 | 3.47 | 3.85 | 3.5
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 7.7 | 1 | 3.3 | 3.32 | 3.33 | 3.34 | 3.35 | 3.16 | 4
Morven | Morven | 132/66 | 30 |  |  | 0 | 0.999 | 7.46 | 7.59 | 7.69 | 7.81 | 7.92 | 0 | 5
Albury | Corowa | 132/22 | 30 | 27/30 |  | 33 | 0.965 | 17.17 | 17.15 | 17.2 | 17.23 | 17.22 | 9.52 | 1.5
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 48.4 | 0.998 | 39.54 | 40.44 | 41.24 | 41.96 | 42.78 | 18.31 | 1
Albury | Mulwala | 132/22 | 30 | 30 |  | 33 | 0.989 | 13.01 | 13.03 | 13.1 | 13.17 | 13.24 | 6.96 | 3.5
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 77 | 0.997 | 60.62 | 61.04 | 61.48 | 61.86 | 62.2 | 49.36 | 3
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 33 | 0.998 | 13.6 | 13.62 | 13.61 | 13.58 | 13.59 | 10.4 | 2
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.998 | 3.93 | 3.96 | 3.99 | 4.02 | 4.03 | 2.21 | 5
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 11 | 0.997 | 5.56 | 5.59 | 5.6 | 5.61 | 5.62 | 3.98 | 6.5
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 33 | 0.991 | 21.51 | 21.87 | 22.24 | 22.56 | 22.94 | 12.31 | 3.5
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 5.5 | 0.996 | 4.67 | 4.7 | 4.74 | 4.78 | 4.81 | 2.85 | 17.5
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 33 | 0.999 | 14.68 | 14.82 | 14.95 | 15.07 | 15.17 | 9.13 | 8
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 5.5 | 0.999 | 1.54 | 1.58 | 1.61 | 1.65 | 1.7 | 1.04 | 5.5
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0.932 | 0.43 | 0.41 | 0.39 | 0.38 | 0.37 | 0 | 4
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 27.5 | 0.959 | 14.7 | 14.92 | 15.1 | 15.29 | 15.45 | 0.42 | 4
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 8.25 | 0.958 | 2.07 | 2.09 | 2.1 | 2.12 | 2.14 | 0.86 | 1
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 13.75 | 0.85 | 4.36 | 4.43 | 4.49 | 4.54 | 4.59 | 1.14 | 3
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 2.75 | 0.88 | 1.14 | 1.18 | 1.23 | 1.28 | 1.32 | 0.12 | 3
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.778 | 3.31 | 3.38 | 3.43 | 3.47 | 3.51 | 0.51 | 16.5
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.65 | 0.887 | 0.83 | 0.85 | 0.87 | 0.89 | 0.91 | 0.22 | 5.5
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 33 | 0.966 | 10.77 | 10.98 | 11.14 | 11.3 | 11.45 | 1.11 | 4
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 11 | 0.992 | 4.88 | 4.89 | 4.91 | 4.93 | 4.94 | 3.66 | 1.5
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 17.6 | 1 | 11.2 | 11.44 | 11.71 | 11.95 | 12.22 | 3.32 | 2.5
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.1 | 0.97 | 1.06 | 1.07 | 1.08 | 1.09 | 1.1 | 0.38 | 4.5
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 13.75 | 0.979 | 11.66 | 11.71 | 11.76 | 11.85 | 11.88 | 6.4 | 5.5
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 55 | 0.999 | 26.84 | 26.83 | 26.84 | 26.86 | 26.83 | 10.41 | 0.5
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 27.5 | 0.995 | 14.55 | 14.65 | 14.71 | 14.79 | 14.87 | 1.94 | 11.5
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | 0.983 | 1.87 | 1.9 | 1.92 | 1.94 | 1.96 | 0.54 | 6.5
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.997 | 14.41 | 14.42 | 14.49 | 14.52 | 14.56 | 6.53 | 1.5
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 2.75 | 0.929 | 1.25 | 1.24 | 1.24 | 1.24 | 1.23 | 0.23 | 12
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0.915 | 0.65 | 0.66 | 0.68 | 0.7 | 0.71 | 0 | 3
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.968 | 2.65 | 2.66 | 2.68 | 2.69 | 2.7 | 0.33 | 2
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 10.45 | 1 | 6.38 | 6.42 | 6.44 | 6.48 | 6.5 | 1.79 | 2
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.984 | 0.41 | 0.41 | 0.41 | 0.42 | 0.42 | 0.15 | 1
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.973 | 19.41 | 19.42 | 19.39 | 19.36 | 19.37 | 9.13 | 8
Yanco | Murrami | 33/11 | 5 | 5 |  | 5.5 | 0.878 | 1.35 | 1.36 | 1.39 | 1.41 | 1.42 | 0.45 | 2
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.948 | 10.45 | 10.49 | 10.52 | 10.54 | 10.61 | 5.93 | 2.5
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 6.88 | 0.963 | 4.08 | 4.09 | 4.1 | 4.11 | 4.11 | 0.93 | 4.5
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.98 | 2.71 | 2.74 | 2.77 | 2.79 | 2.82 | 1.71 | 3
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.968 | 11.08 | 11.1 | 11.12 | 11.15 | 11.18 | 0.96 | 2.5
Buronga | Powercor Robinvale 22kV Euston Distribution Supply |  |  |  |  | 0 | 0.977 | 7.61 | 7.69 | 7.75 | 7.81 | 7.85 | 1.33 | 1.5
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply |  |  |  |  | 0 | 0.996 | 3.99 | 3.99 | 3.99 | 4 | 4 | 1.34 | 6
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 33 | 0.977 | 17.41 | 17.73 | 17.99 | 18.21 | 18.42 | 5.79 | 3
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 33 | 0.973 | 8.14 | 8.19 | 8.24 | 8.28 | 8.34 | 4.55 | 6
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 1 | 3.21 | 3.25 | 3.29 | 3.34 | 3.37 | 0.65 | 6
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0.863 | 0.48 | 0.5 | 0.51 | 0.49 | 0.51 | 0 | 2.5
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0.323 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 6

## ZSWinter
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (MVA) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 2026 | 2027 | 2028 | 2029 | 2030
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 36 | 0.991 | 12.04 | 12.06 | 12.07 | 12.09 | 12.08 | 17.04 | 1.5
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 36 | 0.997 | 14.86 | 14.98 | 15.11 | 15.21 | 15.31 | 16.84 | 5
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 48 | 0.997 | 11.76 | 11.77 | 11.75 | 11.77 | 11.79 | 0 | 3.5
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 18 | 0.997 | 11.38 | 11.37 | 11.36 | 11.36 | 11.35 | 18.14 | 3.5
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 30 | 1 | 17.56 | 17.5 | 17.43 | 17.38 | 17.31 | 24.11 | 11.5
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 240 | 0.999 | 80.71 | 80.79 | 80.81 | 80.8 | 80.77 | 0 | 3.5
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 36 | 0.992 | 6.38 | 6.42 | 6.46 | 6.5 | 6.56 | 11.44 | 2
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 30 | 1 | 11.56 | 11.55 | 11.55 | 11.56 | 11.55 | 5.28 | 3
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 36 | 1 | 13.24 | 13.25 | 13.26 | 13.25 | 13.26 | 17.15 | 2
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 24 | 1 | 11.63 | 11.62 | 11.62 | 11.63 | 11.62 | 16.75 | 5
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 36 | 0.998 | 25.27 | 25.24 | 25.2 | 25.18 | 25.14 | 30.45 | 4
Lismore | Ballina 132kV | 132/66 | 35/45/60 |  |  | 0 | 0.995 | 20.71 | 20.88 | 21.05 | 21.19 | 21.35 | 0 | 5
Lismore | Dunoon | 132/11 | 10 | 10 |  | 12 | 0.994 | 6.52 | 6.53 | 6.55 | 6.56 | 6.57 | 8.61 | 4
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 54 | 0.999 | 18.4 | 18.48 | 18.56 | 18.63 | 18.73 | 19.09 | 8
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 12 | 1 | 6.81 | 6.84 | 6.88 | 6.9 | 6.93 | 7.6 | 7.5
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 19.2 | 0.988 | 6.67 | 6.69 | 6.69 | 6.69 | 6.71 | 8.71 | 3
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 288 | 1 | 91.86 | 92.35 | 92.83 | 93.28 | 93.55 | 0 | 1
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 27.6 | 1 | 12.39 | 12.55 | 12.67 | 12.79 | 12.91 | 17.07 | 5.5
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 57.6 | 0.998 | 6.89 | 6.89 | 6.88 | 6.88 | 6.88 | 7.88 | 7.5
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 36 | 1 | 19.18 | 19.53 | 19.87 | 20.17 | 20.45 | 16.2 | 12.5
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 12 | 0.999 | 11.58 | 11.82 | 12.02 | 12.2 | 12.35 | 12.34 | 2.5
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | 0.999 | 12.14 | 12.1 | 12.06 | 12.06 | 12.01 | 13.8 | 8
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 12 | 0.999 | 7.11 | 7.18 | 7.24 | 7.3 | 7.34 | 8.14 | 4
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 3 | 0.901 | 0.82 | 0.82 | 0.82 | 0.83 | 0.83 | 0.97 | 0.5
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0.998 | 23.38 | 23.57 | 23.72 | 23.86 | 23.99 | 0 | 8
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 36 | 0.998 | 19.61 | 19.71 | 19.76 | 19.83 | 19.91 | 18.44 | 9
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 4.2 | 1 | 3.26 | 3.28 | 3.31 | 3.33 | 3.35 | 0 | 4
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 3 | 0.997 | 1.3 | 1.32 | 1.33 | 1.34 | 1.34 | 1.02 | 6
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 6 | 0.996 | 0.44 | 0.44 | 0.44 | 0.45 | 0.45 | 0.71 | 1.5
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 3 | 0.999 | 0.95 | 0.95 | 0.96 | 0.97 | 0.97 | 0.75 | 10
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 30 | 0.99 | 13.49 | 13.6 | 13.71 | 13.81 | 13.91 | 12.23 | 1.5
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 29.4 | 0.999 | 13.96 | 13.96 | 13.96 | 13.96 | 13.95 | 13.44 | 1
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | 0.991 | 2.52 | 2.57 | 2.62 | 2.66 | 2.7 | 3.01 | 1
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.944 | 9.32 | 9.64 | 9.94 | 10.23 | 10.51 | 12.08 | 2
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0.996 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0 | 2
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.72 | 0.951 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.36 | 1
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.6 | 0.996 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.27 | 2
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | 0.997 | 0.91 | 0.92 | 0.92 | 0.93 | 0.94 | 1.22 | 5
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 27.6 | 0.997 | 11.55 | 11.61 | 11.66 | 11.75 | 11.81 | 11.94 | 1
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 36 | 0.999 | 10.15 | 10.25 | 10.34 | 10.42 | 10.49 | 9.98 | 2.5
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 36 | 0.975 | 9.29 | 9.3 | 9.29 | 9.29 | 9.3 | 0 | 2.5
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 55.2 | 1 | 23.14 | 23.25 | 23.34 | 23.44 | 23.52 | 17.83 | 6
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 36 | 0.998 | 17.93 | 18.06 | 18.17 | 18.28 | 18.38 | 11.03 | 6
Coffs Harbour | Dorrigo | 132/11, 66/11 | 7.5/10 | 10 |  | 12 | 1 | 2.73 | 2.74 | 2.75 | 2.77 | 2.78 | 2.84 | 3.5
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.999 | 6.46 | 6.56 | 6.65 | 6.74 | 6.82 | 8.94 | 1.5
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 7.5 | 0.999 | 2.88 | 2.93 | 2.96 | 3 | 3.03 | 3.28 | 1.5
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 29.4 | 0.944 | 10.5 | 10.53 | 10.56 | 10.55 | 10.6 | 8.28 | 3
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.948 | 0.5 | 0.51 | 0.51 | 0.51 | 0.52 | 0.5 | 1
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 36 | 0.993 | 13.21 | 13.33 | 13.41 | 13.5 | 13.59 | 15.04 | 4
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 36 | 1 | 9.98 | 10.05 | 10.08 | 10.15 | 10.17 | 10.9 | 3
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 27.6 | 0.988 | 9.14 | 9.17 | 9.2 | 9.23 | 9.25 | 8.37 | 6.5
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 36 | 0.997 | 11.35 | 11.39 | 11.44 | 11.47 | 11.51 | 12.16 | 4
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.8 | 0.997 | 1.88 | 1.89 | 1.9 | 1.91 | 1.92 | 1.72 | 1.5
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.6 | 0.997 | 1.32 | 1.33 | 1.34 | 1.35 | 1.36 | 1.53 | 0.5
Kempsey | North St | 33/11 | 16 |  |  | 0 | 0.998 | 10.01 | 10.03 | 10.06 | 10.08 | 10.1 | 7.92 | 4.5
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 18 | 0.999 | 8.32 | 8.41 | 8.49 | 8.56 | 8.64 | 6.83 | 1
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 6 | 0.989 | 4.22 | 4.25 | 4.26 | 4.28 | 4.29 | 2.85 | 4
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 15 | 0.971 | 7.36 | 7.4 | 7.44 | 7.47 | 7.5 | 7.51 | 4.5
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 36 | 0.994 | 20.02 | 20.01 | 20.02 | 20.04 | 20.05 | 14.5 | 1.5
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.6 | 0.997 | 1.24 | 1.24 | 1.24 | 1.25 | 1.25 | 1.36 | 2
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 36 | 0.998 | 21.6 | 21.75 | 21.82 | 21.96 | 22.04 | 27.37 | 0.5
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 4.2 | 1 | 2.16 | 2.2 | 2.24 | 2.27 | 2.3 | 3 | 1
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 9.6 | 0.997 | 7.04 | 7.11 | 7.17 | 7.23 | 7.29 | 9.33 | 1
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 24 | 0.999 | 15.98 | 16.01 | 16.04 | 16.07 | 16.09 | 7.27 | 1.5
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 18 | 1 | 11.26 | 11.35 | 11.44 | 11.52 | 11.6 | 13.01 | 1.5
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.8 | 0.999 | 2.12 | 2.15 | 2.18 | 2.21 | 2.24 | 2.21 | 7.5
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 1 | 11.69 | 11.71 | 11.74 | 11.78 | 11.82 | 0 | 1
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | 0.973 | 0.97 | 0.98 | 0.98 | 0.99 | 0.99 | 1.06 | 2.5
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.8 | 1 | 3.84 | 3.89 | 3.92 | 3.97 | 4 | 4.15 | 2
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 24 | 1 | 7.54 | 7.47 | 7.41 | 7.35 | 7.29 | 8.69 | 8
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 8.4 | 1 | 6.97 | 7.03 | 7.08 | 7.13 | 7.19 | 7.81 | 6.5
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 6 | 0.99 | 3.69 | 3.69 | 3.68 | 3.68 | 3.67 | 1.89 | 3
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 1 | 2.27 | 2.27 | 2.26 | 2.26 | 2.26 | 2.77 | 5
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 30 | 1 | 16.67 | 16.74 | 16.82 | 16.9 | 16.97 | 12.76 | 1.5
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 19.2 | 0.999 | 8.69 | 8.78 | 8.88 | 8.95 | 9.03 | 10.2 | 9
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 7.5 | 0.998 | 3.72 | 3.74 | 3.75 | 3.77 | 3.78 | 4.85 | 3
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 30 | 1 | 13.5 | 13.67 | 13.85 | 14 | 14.15 | 8.72 | 1.5
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 19.2 | 0.999 | 6.7 | 6.69 | 6.68 | 6.68 | 6.67 | 4.94 | 13
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 24 | 0.996 | 15.48 | 15.66 | 15.82 | 15.96 | 16.09 | 9.99 | 3.5
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 12 | 1 | 8.22 | 8.21 | 8.21 | 8.2 | 8.2 | 8.06 | 5.5
Stroud | Booral | 33/11 | 3 | 2.5 |  | 3 | 0.994 | 1.28 | 1.29 | 1.3 | 1.31 | 1.31 | 1.27 | 1
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 1 | 3.03 | 3.05 | 3.06 | 3.07 | 3.08 | 2.67 | 2
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 19.2 | 1 | 6.12 | 6.14 | 6.16 | 6.18 | 6.2 | 5.68 | 2
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.999 | 6.73 | 6.72 | 6.71 | 6.69 | 6.69 | 6.51 | 5.5
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.8 | 0.99 | 1.77 | 1.8 | 1.84 | 1.87 | 1.92 | 1.74 | 2
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 9.6 | 0.999 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.95 | 12
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 9.6 | 1 | 5.06 | 5.14 | 5.23 | 5.3 | 5.39 | 3.96 | 0.5
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 72 | 0.997 | 29.6 | 29.65 | 29.61 | 29.45 | 29.47 | 0.01 | 2
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 6 | 1 | 2.04 | 2.04 | 2.06 | 2.06 | 2.08 | 2.13 | 2
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0.969 | 8.73 | 8.81 | 8.87 | 8.92 | 8.96 | 0 | 2
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 19.2 | 1 | 8.15 | 8.14 | 8.14 | 8.15 | 8.15 | 7.75 | 2
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply |  |  |  |  | 0 | 1 | 6.72 | 6.76 | 6.79 | 6.82 | 6.86 | 2.71 | 3.5
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 3 | 0.999 | 3.29 | 3.31 | 3.33 | 3.34 | 3.36 | 1.9 | 6
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 15 | 1 | 14.41 | 14.56 | 14.71 | 14.83 | 14.95 | 9.41 | 4.5
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.945 | 0.46 | 0.46 | 0.47 | 0.47 | 0.48 | 0.22 | 0.5
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 15 | 0.995 | 12.07 | 12.18 | 12.28 | 12.38 | 12.46 | 6.43 | 3
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 19.2 | 1 | 11.64 | 11.63 | 11.61 | 11.6 | 11.58 | 5.97 | 3.5
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 4.2 | 0.95 | 0.46 | 0.46 | 0.47 | 0.47 | 0.48 | 0.21 | 3.5
Armidale | Uralla | 66/11 | 8 | 5 |  | 6 | 0.95 | 4.58 | 4.62 | 4.65 | 4.69 | 4.72 | 3.62 | 2.5
Armidale | Walcha South 66/22kV | 66/22 | 8 | 8/10 |  | 9.6 | 0.735 | 2.16 | 2.18 | 2.21 | 2.23 | 2.25 | 1.13 | 2.5
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.6 | 1 | 1.89 | 1.92 | 1.95 | 1.97 | 1.99 | 1.25 | 5
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.949 | 1.15 | 1.16 | 1.17 | 1.18 | 1.19 | 1.19 | 1
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | 0.782 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.13 | 3
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 24 | 1 | 9.52 | 9.58 | 9.62 | 9.68 | 9.72 | 7.19 | 5
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 6 | 1 | 5.47 | 5.51 | 5.54 | 5.57 | 5.59 | 3.22 | 1
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 0.684 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.95 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.86 | 10
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.6 | 0.94 | 2.45 | 2.46 | 2.46 | 2.47 | 2.48 | 2.15 | 4.5
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 36 | 1 | 23.16 | 23.38 | 23.6 | 23.73 | 23.91 | 15.31 | 2.5
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | 0.792 | 1.15 | 1.15 | 1.16 | 1.17 | 1.17 | 0.82 | 9
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.8 | 0.997 | 0.94 | 0.97 | 0.99 | 1.02 | 1.05 | 0 | 0.5
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 6 | 1 | 2.33 | 2.35 | 2.36 | 2.38 | 2.39 | 1.42 | 7
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 6 | 0.994 | 1.83 | 1.86 | 1.89 | 1.92 | 1.95 | 0.59 | 0.5
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | 0.843 | 0.22 | 0.22 | 0.23 | 0.23 | 0.23 | 0.12 | 0.5
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.8 | 0.985 | 3.06 | 3.09 | 3.11 | 3.13 | 3.16 | 2.46 | 0.5
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.95 | 1.87 | 1.89 | 1.91 | 1.93 | 1.94 | 0.95 | 4
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 18 | 1 | 18.93 | 19.22 | 19.46 | 19.7 | 19.92 | 6.85 | 6.5
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.988 | 5.65 | 5.72 | 5.77 | 5.82 | 5.87 | 2.72 | 5.5
Moree | Ashley | 66/22 | 8 |  |  | 0 | 1 | 3.59 | 3.63 | 3.66 | 3.68 | 3.71 | 0.56 | 350.5
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 3 | 0.977 | 1.05 | 1.07 | 1.09 | 1.1 | 1.11 | 0.54 | 1.5
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 36 | 0.998 | 22.52 | 24.44 | 28.61 | 32.4 | 35.73 | 14.47 | 25.5
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.95 | 5.39 | 5.4 | 5.4 | 5.39 | 5.39 | 1.33 | 18.5
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.985 | 3.69 | 3.67 | 3.65 | 3.65 | 3.64 | 0.24 | 13
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | 0.853 | 2.98 | 3.09 | 3.19 | 3.29 | 3.39 | 0.05 | 14
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | 0.909 | 2.34 | 2.36 | 2.37 | 2.38 | 2.39 | 1.33 | 8
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 6 | 0.954 | 1.72 | 1.74 | 1.75 | 1.77 | 1.78 | 0.69 | 21
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 6 | 0.998 | 3.19 | 3.23 | 3.27 | 3.3 | 3.34 | 2.57 | 1
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0.999 | 2.9 | 2.89 | 2.89 | 2.88 | 2.88 | 0.74 | 21
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 36 | 0.996 | 17.61 | 17.85 | 18.07 | 18.28 | 18.48 | 10.15 | 9.5
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 12 | 0.956 | 4.95 | 5.01 | 5.05 | 5.11 | 5.16 | 3.32 | 4.5
Narrabri | Wee Waa | 66/22 | 8.8/10 | 16 |  | 12 | 0.969 | 9.99 | 10.12 | 10.26 | 10.39 | 10.49 | 2.89 | 6
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.8 | 0.994 | 4.91 | 4.93 | 4.94 | 4.96 | 4.97 | 1.75 | 25.5
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 36 | 0.998 | 21.95 | 21.95 | 21.92 | 21.93 | 21.93 | 13.03 | 0
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 0.989 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 2
Tamworth | Attunga | 66/11 | 5 | 8 |  | 6 | 0.95 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 1.73 | 4.5
Tamworth | Barraba | 66/11 | 5 | 5 |  | 6 | 1 | 2.4 | 2.41 | 2.42 | 2.44 | 2.45 | 1.96 | 1
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.2 | 0.995 | 0.74 | 0.75 | 0.75 | 0.76 | 0.76 | 0.63 | 2
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.4 | 0.942 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.17 | 0.5
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.8 | 0.985 | 0.9 | 0.89 | 0.89 | 0.88 | 0.88 | 0.41 | 3.5
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.951 | 1.11 | 1.12 | 1.13 | 1.14 | 1.15 | 0.65 | 0.5
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 36 | 0.998 | 11.83 | 21.42 | 22.7 | 24.68 | 26.35 | 3.17 | 10
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.999 | 5.77 | 5.81 | 5.84 | 5.87 | 5.9 | 4.83 | 1.5
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 7.5 | 0.9 | 4.4 | 4.43 | 4.45 | 4.48 | 4.5 | 2.74 | 1
Tamworth | Murrurundi | 33/11 | 5/8 |  |  | 0 | 1 | 2.46 | 2.47 | 2.47 | 2.48 | 2.48 | 1.92 | 2.5
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 3 | 0.991 | 1.64 | 1.66 | 1.67 | 1.69 | 1.71 | 1.3 | 0.5
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 36 | 0.994 | 17.45 | 17.64 | 17.8 | 17.98 | 18.14 | 13 | 4.5
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 15.96 | 0.998 | 6.29 | 6.34 | 6.4 | 6.44 | 6.49 | 3.66 | 1
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 12 | 1 | 4.31 | 4.33 | 4.35 | 4.36 | 4.37 | 0 | 6.5
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.982 | 0.57 | 0.57 | 0.56 | 0.56 | 0.55 | 0.18 | 2
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 55.2 | 0.996 | 30.88 | 32.08 | 33.12 | 34.01 | 34.81 | 12.94 | 2
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 36 | 0.998 | 26.16 | 26.28 | 26.38 | 26.49 | 26.58 | 15 | 0.5
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.977 | 0.38 | 0.37 | 0.37 | 0.37 | 0.37 | 0.12 | 0.5
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 7.5 | 1 | 1.98 | 1.98 | 1.98 | 1.98 | 1.99 | 1.4 | 3
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 15.6 | 0.99 | 8.15 | 8.12 | 8.11 | 8.09 | 8.08 | 6.72 | 8.5
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 12 | 0.99 | 4.87 | 4.85 | 4.84 | 4.84 | 4.83 | 4.24 | 7.5
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | 0.997 | 3.37 | 3.36 | 3.36 | 3.35 | 3.35 | 2.33 | 3.5
Beryl | Mudgee | 132/22, 66/22 | 18/30 | 30 |  | 36 | 0.996 | 25.04 | 25.12 | 25.22 | 25.31 | 25.4 | 18.38 | 12
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 3 | 0.995 | 2.56 | 2.59 | 2.61 | 2.64 | 2.66 | 1.71 | 1
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 3 | 0.998 | 1.13 | 1.14 | 1.14 | 1.15 | 1.16 | 0.79 | 6
Wellington | Wellington 11kV | 132/11, 66/11 | 8/11 | 15 |  | 13.2 | 0.999 | 8.86 | 8.92 | 8.98 | 9.04 | 9.11 | 5.79 | 9.5
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 12 | 0.96 | 5.32 | 5.4 | 5.47 | 5.54 | 5.61 | 3.74 | 14.5
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 108 | 1 | 54.46 | 54.9 | 55.24 | 55.65 | 56.01 | 0 | 6.5
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 36 | 0.988 | 21.18 | 21.43 | 21.65 | 21.81 | 22 | 6.63 | 3
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 36 | 1 | 17.05 | 17.17 | 17.25 | 17.33 | 17.4 | 16.22 | 4
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 27.6 | 1 | 13.52 | 13.58 | 13.64 | 13.7 | 13.75 | 12.51 | 5
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 36 | 1 | 17.24 | 17.31 | 17.38 | 17.45 | 17.5 | 16.95 | 9
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | 0.996 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12 | 1.19 | 7.5
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 14.4 | 1 | 6.07 | 6.07 | 6.07 | 6.07 | 6.07 | 4.77 | 1.5
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.95 | 1.54 | 1.55 | 1.56 | 1.57 | 1.58 | 1.02 | 2
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 28.8 | 0.999 | 13.35 | 13.37 | 13.39 | 13.43 | 13.45 | 7.9 | 21.5
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 12 | 0.997 | 6.95 | 6.91 | 6.86 | 6.84 | 6.8 | 3.54 | 4
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 30 | 0.957 | 7.71 | 7.86 | 8 | 8.13 | 8.26 | 2.39 | 12.5
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 12 | 0.933 | 6.49 | 6.63 | 6.78 | 6.92 | 7.04 | 2.46 | 5
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.722 | 2.94 | 2.99 | 3.05 | 3.09 | 3.14 | 0.83 | 2
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.2 | 0.923 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.05 | 1
Nyngan | Cobar CSA | 132/11 | 15/18 | 30/45 |  | 21.6 | 0.981 | 19.56 | 19.71 | 19.8 | 19.93 | 20.04 | 0 | 32.5
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 18 | 0.628 | 4.45 | 4.47 | 4.46 | 4.47 | 4.44 | 0 | 17.5
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 24 | 0.877 | 20.81 | 21.33 | 21.82 | 22.28 | 22.69 | 0 | 72.5
Nyngan | Cobar Town | 66/22 | 8/11 | 10 |  | 12 | 0.95 | 5.86 | 5.88 | 5.9 | 5.91 | 5.93 | 4.94 | 2.5
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0.876 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0 | 1.5
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 36 | 0.99 | 31.96 | 32.21 | 32.49 | 32.75 | 32.95 | 0 | 29
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 12 | 0.991 | 4.67 | 4.69 | 4.71 | 4.73 | 4.75 | 2.75 | 4
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply |  |  |  |  | 0 | 1 | 34.01 | 35.09 | 35.08 | 35.08 | 35.02 | 26.2 | 15
Broken Hill | Wilcannia 33kV |  |  |  |  | 0 | 0.789 | 0.64 | 0.65 | 0.65 | 0.66 | 0.66 | 0.33 | 2
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 6 | 0.998 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73 | 1.03 | 0.5
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.8 | 0.813 | 1.24 | 1.33 | 1.43 | 1.51 | 1.58 | 0.95 | 8
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.8 | 0.999 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 0.13 | 4.5
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 18 | 0.808 | 5.11 | 5.93 | 5.95 | 5.98 | 6 | 0 | 0.5
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | 1 | 0.44 | 0.45 | 0.45 | 0.45 | 0.45 | 0.35 | 0.5
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.8 | 0.974 | 2.34 | 2.36 | 2.37 | 2.39 | 2.4 | 0.26 | 0.5
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 4.2 | 0.993 | 1.37 | 1.39 | 1.41 | 1.43 | 1.45 | 0.68 | 0.5
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 12 | 1 | 12.56 | 12.68 | 12.8 | 12.89 | 13.01 | 11.74 | 12
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 36 | 0.94 | 17.63 | 17.69 | 17.74 | 17.78 | 17.81 | 7.81 | 5
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 36 | 0.998 | 23.54 | 23.66 | 23.75 | 23.85 | 23.94 | 13.59 | 24.5
Orange | Orange West | 66/11 | 30 | 30 |  | 36 | 1 | 15.03 | 15.04 | 15.04 | 15.05 | 15.04 | 12.38 | 14
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 3 | 0.966 | 1.58 | 1.59 | 1.61 | 1.63 | 1.65 | 1.43 | 3
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 28.8 | 0.963 | 13.13 | 13.26 | 13.36 | 13.49 | 13.59 | 2.21 | 46
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.8 | 0.991 | 3.44 | 3.44 | 3.44 | 3.44 | 3.44 | 2.95 | 10.5
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 24 | 0.992 | 14.46 | 14.78 | 15.02 | 15.27 | 15.53 | 5.71 | 6.5
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 3 | 1 | 2.22 | 2.21 | 2.2 | 2.19 | 2.19 | 1.85 | 6.5
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 36 | 0.997 | 20.59 | 20.7 | 20.84 | 20.93 | 21.04 | 13.28 | 7
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 72 | 0.995 | 25.14 | 25.55 | 25.91 | 26.33 | 26.72 | 11.24 | 8
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 24 | 0.991 | 20.18 | 20.39 | 20.59 | 20.78 | 20.96 | 15.11 | 14
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0.858 | 0.46 | 0.46 | 0.45 | 0.45 | 0.45 | 0 | 1.5
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 54 | 0.993 | 31.72 | 32.26 | 32.76 | 33.24 | 33.68 | 0 | 48
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 18 | 1 | 5.78 | 5.76 | 5.75 | 5.74 | 5.72 | 4.04 | 8
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 36 | 0.999 | 16.52 | 16.87 | 17.19 | 17.51 | 17.81 | 12.68 | 13.5
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 12 | 0.973 | 3.53 | 3.66 | 3.78 | 3.9 | 4.01 | 1.73 | 3.5
Parkes | Trundle | 66/22 | 8 | 5 |  | 6 | 0.994 | 13.53 | 14.34 | 15.11 | 15.83 | 16.5 | 2.37 | 64.5
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 12 | 0.996 | 7.42 | 7.5 | 7.57 | 7.63 | 7.7 | 4.79 | 11
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 36 | 0.988 | 11.64 | 11.71 | 11.77 | 11.84 | 11.89 | 9.04 | 6.5
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 8.4 | 0.906 | 3.49 | 3.57 | 3.65 | 3.72 | 3.79 | 3.05 | 2.5
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 6 | 0.912 | 3.87 | 3.91 | 3.95 | 3.99 | 4.01 | 1.3 | 1
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.8 | 0.998 | 1.39 | 1.44 | 1.48 | 1.53 | 1.57 | 0.51 | 6.5
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 54 | 0.999 | 20.34 | 20.39 | 20.42 | 20.47 | 20.52 | 14.46 | 3.5
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.6 | 0.999 | 1.35 | 1.35 | 1.35 | 1.35 | 1.35 | 1.37 | 7
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 48 | 1 | 29.04 | 29.03 | 29.07 | 29.05 | 29.06 | 0 | 2
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 19.2 | 1 | 7.44 | 7.46 | 7.49 | 7.51 | 7.54 | 6.78 | 6.5
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 15 | 0.998 | 8.81 | 8.83 | 8.85 | 8.87 | 8.89 | 8.36 | 3
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 15 | 1 | 7.61 | 7.6 | 7.6 | 7.61 | 7.61 | 5.55 | 7.5
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | 0.982 | 3.46 | 3.48 | 3.51 | 3.53 | 3.56 | 2.82 | 1.5
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 6 | 0.997 | 1.33 | 1.34 | 1.34 | 1.34 | 1.34 | 0.75 | 5.5
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 6 | 0.99 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0 | 1.5
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 24 | 0.999 | 14.66 | 14.81 | 14.94 | 15.06 | 15.19 | 7.3 | 17.5
Cooma | Eucumbene | 66/11 | 3 |  |  | 0 | 0.948 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.08 | 1.5
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 36 | 0.999 | 14 | 14.11 | 14.2 | 14.32 | 14.4 | 4.12 | 14.5
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | 0.991 | 0.7 | 0.7 | 0.7 | 0.7 | 0.71 | 0.3 | 10.5
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 12 | 0.998 | 5.16 | 5.17 | 5.19 | 5.21 | 5.23 | 2.89 | 9
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 0.974 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0 | 0.5
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.938 | 2.88 | 2.84 | 2.8 | 2.78 | 2.76 | 0 | 17.5
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 1 | 1.21 | 1.22 | 1.23 | 1.24 | 1.25 | 0.19 | 5.5
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 0.981 | 1.44 | 1.47 | 1.51 | 1.54 | 1.57 | 0 | 1
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 12 | 0.95 | 9.53 | 9.62 | 9.68 | 9.74 | 9.8 | 0.14 | 4
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0.994 | 0.47 | 0.5 | 0.53 | 0.56 | 0.59 | 0 | 1
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 1 | 8.12 | 8.19 | 8.24 | 8.3 | 8.35 | 0 | 4.5
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 19.2 | 0.961 | 14.27 | 14.38 | 14.45 | 14.49 | 14.55 | 0.03 | 16
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.995 | 42.59 | 42.69 | 42.81 | 42.95 | 43.05 | 0 | 4
Bega | Bermagui | 33/11 | 5 | 5 |  | 6 | 1 | 3.3 | 3.36 | 3.41 | 3.46 | 3.51 | 3.23 | 4
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0.993 | 0.66 | 0.66 | 0.66 | 0.66 | 0.67 | 0.66 | 2.5
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 3 | 0.999 | 1.56 | 1.57 | 1.58 | 1.59 | 1.6 | 2.15 | 7
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 19.2 | 1 | 4.95 | 4.96 | 4.96 | 4.97 | 4.97 | 5.98 | 4.5
Bega | Edrom | 66/11 | 5 | 5 |  | 6 | 0.942 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 0 | 3.5
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0.999 | 5.57 | 5.56 | 5.56 | 5.55 | 5.54 | 0 | 6
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 36 | 0.997 | 15.37 | 15.45 | 15.52 | 15.61 | 15.68 | 10.65 | 5.5
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 19.2 | 1 | 16.47 | 16.5 | 16.53 | 16.57 | 16.61 | 12.51 | 5
Bega | Quira | 66/11 | 5 |  |  | 0 | 0.985 | 1.35 | 1.36 | 1.35 | 1.35 | 1.35 | 1.12 | 2.5
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 15.6 | 1 | 4.83 | 4.82 | 4.82 | 4.83 | 4.84 | 1.69 | 3.5
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | 0.987 | 6.77 | 7.31 | 7.8 | 8.24 | 8.65 | 0 | 2
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.976 | 0.9 | 0.91 | 0.92 | 0.93 | 0.94 | 0.45 | 9.5
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 3 | 0.999 | 1.26 | 1.25 | 1.25 | 1.24 | 1.23 | 1.52 | 7
Tumut | Batlow | 66/11 | 5 | 5 |  | 6 | 0.994 | 1.76 | 1.73 | 1.71 | 1.69 | 1.68 | 1.37 | 7
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 9.6 | 1 | 5.5 | 5.54 | 5.57 | 5.61 | 5.64 | 3.92 | 20
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.2 | 0.987 | 0.55 | 0.56 | 0.56 | 0.57 | 0.58 | 0.57 | 5
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.994 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.09 | 1.5
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | 0.509 | 0.63 | 0.65 | 0.67 | 0.7 | 0.72 | 0.41 | 2
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 9.6 | 0.999 | 7.89 | 7.81 | 7.75 | 7.68 | 7.64 | 3.63 | 18
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 36 | 0.991 | 14.44 | 14.47 | 14.51 | 14.54 | 14.57 | 7.5 | 2.5
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 12 | 0.998 | 10.35 | 10.45 | 10.54 | 10.62 | 10.7 | 9.87 | 8.5
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 6 | 0.982 | 8.06 | 8.31 | 8.55 | 8.76 | 8.96 | 3.77 | 6.5
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 12 | 0.975 | 1.59 | 1.61 | 1.63 | 1.65 | 1.67 | 0 | 6
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 36 | 0.998 | 14.2 | 14.49 | 14.78 | 15.04 | 15.26 | 14.31 | 5
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 36 | 0.998 | 19.09 | 19.36 | 19.57 | 19.74 | 19.89 | 9.49 | 4
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 36 | 0.998 | 28.66 | 28.91 | 29.09 | 29.28 | 29.46 | 19.97 | 6.5
Queanbeyan | South Jerrabomberra | 132/11 | 30/40/50 | 30/40/50 |  | 60 | 0.998 | 4.05 | 9.45 | 14.85 | 20.25 | 25.65 | 0 | 0
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 9.6 | 1 | 5.04 | 5.07 | 5.12 | 5.15 | 5.18 | 5.21 | 11
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 3 | 0.951 | 2.64 | 2.65 | 2.66 | 2.67 | 2.68 | 2.76 | 4
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 22.8 | 1 | 16.61 | 16.74 | 16.84 | 16.94 | 17.04 | 8.8 | 10.5
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 12 | 1 | 6.65 | 6.83 | 6.99 | 7.13 | 7.28 | 4.76 | 0.5
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 36 | 1 | 10.51 | 10.63 | 10.74 | 10.85 | 10.93 | 4.44 | 8
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.996 | 53 | 54.02 | 54.86 | 55.61 | 56.28 | 0 | 10.5
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 18 | 0.995 | 11.3 | 11.47 | 11.63 | 11.78 | 11.92 | 8.67 | 5
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 18 | 0.994 | 7.51 | 7.63 | 7.74 | 7.85 | 7.95 | 3.07 | 3
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.956 | 7.51 | 7.54 | 7.58 | 7.61 | 7.64 | 0 | 1
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 16.8 | 0.91 | 5.22 | 4.83 | 4.52 | 4.27 | 4.12 | 1.58 | 43.5
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | 0.995 | 1.35 | 1.37 | 1.38 | 1.39 | 1.41 | 1.48 | 12.5
Cowra | Canowindra | 66/11 | 5 | 8 |  | 6 | 1 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72 | 3.95 | 2
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 36 | 0.993 | 16.71 | 16.77 | 16.82 | 16.89 | 16.94 | 11.81 | 2
Cowra | Grenfell | 66/11 | 8 | 5 |  | 6 | 0.95 | 3.07 | 2.95 | 2.84 | 2.74 | 2.66 | 4.39 | 5
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | 0.99 | 0.89 | 0.9 | 0.9 | 0.9 | 0.9 | 0.68 | 5
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 6 | 0.994 | 3.75 | 3.77 | 3.79 | 3.81 | 3.82 | 3.22 | 5
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 22.8 | 0.982 | 12.18 | 12.55 | 12.87 | 13.19 | 13.52 | 8 | 4.5
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.8 | 0.978 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 0.41 | 3.5
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 12 | 0.999 | 4.77 | 4.79 | 4.8 | 4.82 | 4.84 | 3.99 | 6.5
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 36 | 0.998 | 17.57 | 17.76 | 17.93 | 18.08 | 18.24 | 11.03 | 10.5
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 3 | 1 | 1.31 | 1.32 | 1.33 | 1.34 | 1.34 | 1.36 | 2.5
Yass | Marilba | 66/11 | 3 |  |  | 0 | 1 | 1.45 | 1.44 | 1.44 | 1.44 | 1.44 | 1.37 | 8.5
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | 0.987 | 7.61 | 7.72 | 7.81 | 7.88 | 7.96 | 9.77 | 8
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 15.6 | 0.993 | 13.99 | 14.08 | 14.18 | 14.25 | 14.35 | 9.54 | 7.5
Temora | Anona | 66/22 | 3 | 2.5 |  | 3 | 0.947 | 1.18 | 1.19 | 1.19 | 1.2 | 1.2 | 1.02 | 3.5
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 3 | 0.999 | 0.7 | 0.71 | 0.71 | 0.72 | 0.72 | 0.65 | 2.5
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.6 | 0.998 | 0.92 | 0.93 | 0.93 | 0.93 | 0.94 | 0.77 | 9.5
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | 0.999 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.17 | 0.5
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 72 | 0.986 | 17.07 | 17.19 | 17.31 | 17.41 | 17.53 | 0 | 10
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 12 | 1 | 6.85 | 6.91 | 6.95 | 6.99 | 7.03 | 6.19 | 8
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 12 | 0.99 | 7.36 | 7.44 | 7.52 | 7.6 | 7.67 | 5.67 | 15
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.6 | 1 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.3 | 26
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 36 | 0.95 | 11.45 | 13.73 | 15.98 | 18.21 | 20.44 | 0.34 | 31
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/8 | 6.75/8 |  | 9.6 | 1 | 8.72 | 8.85 | 8.97 | 9.08 | 9.19 | 5.32 | 0
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.8 | 0.927 | 0.59 | 0.59 | 0.59 | 0.59 | 0.59 | 0 | 1.5
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 9.6 | 0.999 | 4.32 | 4.35 | 4.38 | 4.41 | 4.43 | 4.55 | 13
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.6 | 0.973 | 0.83 | 0.82 | 0.8 | 0.79 | 0.78 | 0.81 | 4
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 16.8 | 0.995 | 4.88 | 4.94 | 4.99 | 5.04 | 5.1 | 2.68 | 4
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | 0.997 | 0.51 | 0.51 | 0.52 | 0.52 | 0.53 | 0.26 | 2.5
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 18 | 0.999 | 6.8 | 6.86 | 6.91 | 6.95 | 7 | 4.08 | 12
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | 0.999 | 11.38 | 11.41 | 11.42 | 11.44 | 11.46 | 0 | 10
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.969 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.42 | 3
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.4 | 0.999 | 1.44 | 1.44 | 1.45 | 1.46 | 1.46 | 0 | 3
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 8.28 | 0.995 | 3.37 | 3.4 | 3.42 | 3.45 | 3.47 | 0.61 | 2.5
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.2 | 1 | 1.08 | 1.09 | 1.1 | 1.12 | 1.13 | 0.8 | 0.5
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 36 | 0.996 | 19.68 | 19.96 | 20.2 | 20.44 | 20.63 | 10.44 | 4
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 15.96 | 1 | 11 | 11.09 | 11.16 | 11.23 | 11.3 | 10.28 | 9
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 0.983 | 0.15 | 0.14 | 0.14 | 0.13 | 0.13 | 0 | 20
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 36 | 1 | 15.13 | 15.17 | 15.25 | 15.32 | 15.35 | 4.9 | 2
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 6 | 1 | 2.14 | 2.13 | 2.12 | 2.11 | 2.11 | 2.12 | 7.5
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 30 | 1 | 15.47 | 15.54 | 15.59 | 15.66 | 15.7 | 12.96 | 10.5
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 6 | 0.951 | 2.99 | 2.99 | 2.99 | 2.99 | 3 | 2.5 | 3
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 24 | 0.991 | 9.42 | 9.42 | 9.41 | 9.43 | 9.41 | 2.53 | 3.5
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 19.2 | 0.997 | 4.87 | 4.9 | 4.92 | 4.95 | 4.97 | 3.55 | 6.5
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 8.4 | 0.995 | 4.41 | 4.45 | 4.49 | 4.52 | 4.55 | 3.85 | 2
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 8.4 | 0.992 | 3.36 | 3.37 | 3.38 | 3.38 | 3.39 | 3.16 | 10
Morven | Morven | 132/66 | 30 |  |  | 0 | 1 | 7.28 | 7.33 | 7.37 | 7.4 | 7.44 | 0 | 1.5
Albury | Corowa | 132/22 | 30 | 27/30 |  | 36 | 0.983 | 14.2 | 14.37 | 14.52 | 14.66 | 14.78 | 9.52 | 6
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 52.8 | 0.991 | 34.1 | 34.14 | 34.2 | 34.26 | 34.31 | 18.31 | 5
Albury | Mulwala | 132/22 | 30 | 30 |  | 36 | 0.998 | 11.19 | 11.27 | 11.35 | 11.44 | 11.5 | 6.96 | 31.5
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 84 | 0.999 | 49.09 | 49.73 | 50.33 | 50.91 | 51.41 | 49.36 | 4
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 36 | 1 | 10.06 | 10.14 | 10.2 | 10.26 | 10.31 | 10.4 | 6
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 12 | 1 | 3.63 | 3.69 | 3.75 | 3.8 | 3.85 | 2.21 | 3
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 12 | 0.987 | 5.39 | 5.52 | 5.65 | 5.77 | 5.88 | 3.98 | 8
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 36 | 1 | 17.39 | 17.55 | 17.69 | 17.8 | 17.93 | 12.31 | 3.5
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 6 | 1 | 3.55 | 3.63 | 3.7 | 3.76 | 3.82 | 2.85 | 5.5
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 36 | 0.994 | 11.28 | 11.43 | 11.56 | 11.67 | 11.76 | 9.13 | 3
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 6 | 0.951 | 2.29 | 2.38 | 2.47 | 2.55 | 2.63 | 1.04 | 6
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0.907 | 0.4 | 0.38 | 0.37 | 0.36 | 0.35 | 0 | 4
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 30 | 0.949 | 9.86 | 9.95 | 10.02 | 10.09 | 10.15 | 0.42 | 1
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 9 | 0.956 | 1.7 | 1.73 | 1.75 | 1.77 | 1.79 | 0.86 | 1
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 15 | 0.901 | 2.83 | 2.85 | 2.88 | 2.9 | 2.92 | 1.14 | 6.5
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 3 | 0.88 | 1.07 | 1.16 | 1.24 | 1.3 | 1.36 | 0.12 | 3
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.778 | 2.22 | 2.25 | 2.29 | 2.31 | 2.33 | 0.51 | 3.5
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.8 | 0.882 | 0.71 | 0.79 | 0.85 | 0.9 | 0.95 | 0.22 | 1
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 36 | 0.957 | 17.15 | 17.27 | 17.36 | 17.46 | 17.55 | 1.11 | 11.5
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 12 | 0.995 | 6.61 | 6.57 | 6.56 | 6.55 | 6.52 | 3.66 | 20.5
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 19.2 | 0.987 | 7.11 | 7.09 | 7.07 | 7.07 | 7.06 | 3.32 | 1
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.2 | 0.959 | 0.87 | 0.89 | 0.91 | 0.92 | 0.93 | 0.38 | 2
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 15 | 0.997 | 7.45 | 7.5 | 7.54 | 7.59 | 7.63 | 6.4 | 1
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 60 | 0.995 | 21.1 | 21.26 | 21.41 | 21.53 | 21.64 | 10.41 | 2
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 30 | 0.999 | 12.25 | 12.33 | 12.41 | 12.49 | 12.56 | 1.94 | 15.5
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | 0.989 | 1.1 | 1.08 | 1.05 | 1.03 | 1.02 | 0.54 | 2.5
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 30 | 1 | 9.94 | 10.03 | 10.11 | 10.19 | 10.25 | 6.53 | 7
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 3 | 0.889 | 1.16 | 1.2 | 1.22 | 1.25 | 1.27 | 0.23 | 1
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0.912 | 0.37 | 0.38 | 0.38 | 0.38 | 0.38 | 0 | 2.5
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.982 | 1.54 | 1.52 | 1.52 | 1.5 | 1.49 | 0.33 | 15.5
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 11.4 | 0.993 | 5.27 | 5.35 | 5.45 | 5.53 | 5.61 | 1.79 | 7.5
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.991 | 0.3 | 0.3 | 0.3 | 0.3 | 0.31 | 0.15 | 1.5
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 30 | 0.989 | 15.72 | 15.67 | 15.62 | 15.58 | 15.52 | 9.13 | 5
Yanco | Murrami | 33/11 | 5 | 5 |  | 6 | 0.86 | 1.76 | 1.84 | 1.93 | 2.01 | 2.09 | 0.45 | 1.5
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 19.2 | 0.994 | 8.28 | 8.35 | 8.41 | 8.47 | 8.54 | 5.93 | 8.5
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 7.5 | 0.947 | 2.18 | 2.17 | 2.16 | 2.15 | 2.15 | 0.93 | 3
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | 0.987 | 2.17 | 2.18 | 2.2 | 2.22 | 2.23 | 1.71 | 3.5
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.99 | 9.21 | 9.33 | 9.43 | 9.51 | 9.6 | 0.96 | 1.5
Buronga | Powercor Robinvale 22kV Euston Distribution Supply |  |  |  |  | 0 | 0.99 | 3.91 | 3.95 | 3.99 | 4.03 | 4.06 | 1.33 | 0.5
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply |  |  |  |  | 0 | 0.935 | 3.35 | 3.42 | 3.48 | 3.54 | 3.59 | 1.34 | 4.5
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 36 | 0.999 | 9.15 | 9.27 | 9.37 | 9.48 | 9.57 | 5.79 | 7
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 36 | 1 | 4.25 | 4.28 | 4.32 | 4.36 | 4.4 | 4.55 | 9.5
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.974 | 1.64 | 1.65 | 1.66 | 1.67 | 1.68 | 0.65 | 1.5
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0.99 | 0.08 | 0.07 | 0.08 | 0.08 | 0.08 | 0 | 2
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0.138 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0 | 0.5

## Lines
Supply Area | Feeder # | Feeder Voltage kV | Feeder Origin | Feeder Destination | Summer | [5 empty] | Winter
[5 empty] | Line Rating | Line Forecast MVA |  |  |  |  | Line Rating | Line Forecast MVA
[5 empty] | MVA | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 | MVA | 2026 | 2027 | 2028 | 2029 | 2030
Casino | 96L | 132 | Transgrid Casino 132kV 96L Tee | Casino ZS | 140 | 32.15 | 32.25 | 32.26 | 32.33 | 32.31 | 157 | 23.89 | 24.05 | 24.21 | 24.35 | 24.49
Casino | 6501 | 66 | Casino ZS | Rappville Tee | 16 | 0.55 | 0.55 | 0.55 | 0.56 | 0.56 | 25 | 0.44 | 0.44 | 0.44 | 0.45 | 0.45
Casino | 8401 | 33 | Casino ZS | Mallanganee ZS | 4 | 2.58 | 2.58 | 2.57 | 2.56 | 2.56 | 6 | 2.69 | 2.71 | 2.72 | 2.74 | 2.76
Casino | 8402 | 33 | Mallanganee ZS | Bonalbo ZS | 4 | 1.68 | 1.68 | 1.67 | 1.67 | 1.67 | 6 | 1.71 | 1.72 | 1.73 | 1.74 | 1.74
Casino | 8403 | 33 | Bonalbo ZS | Urbenville ZS | 4 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 7 | 0.95 | 0.95 | 0.96 | 0.97 | 0.97
Coffs Harbour | 96C/2(D) | 132 | TransGrid 96C Armidale Coffs Harbour Dorrigo Tee | Dorrigo ZS | 41 | 1.99 | 1.95 | 1.92 | 1.89 | 1.86 | 76 | 2.73 | 2.74 | 2.75 | 2.77 | 2.78
Coffs Harbour | 702 | 66 | Boambee South 132/66kV STS | Sawtell ZS | 61 | 9.59 | 9.78 | 9.95 | 10.15 | 10.33 | 68 | 10.5 | 10.53 | 10.56 | 10.55 | 10.6
Coffs Harbour | 705 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 15.73 | 15.72 | 15.71 | 15.71 | 15.72 | 58 | 16.07 | 16.15 | 16.25 | 16.34 | 16.43
Coffs Harbour | 706 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 17.92 | 17.91 | 17.89 | 17.89 | 17.9 | 58 | 18.3 | 18.39 | 18.5 | 18.61 | 18.71
Coffs Harbour | 7501 | 66 | Nana Glen ZS | Woolgoolga ZS | 29 | 5.87 | 5.86 | 5.86 | 5.86 | 5.86 | 33 | 5.99 | 6.02 | 6.06 | 6.1 | 6.13
Coffs Harbour | 7502 | 66 | Nana Glen ZS | Ulong Tee | 9 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 15 | 0.5 | 0.51 | 0.51 | 0.51 | 0.52
Coffs Harbour | 7502/1 | 66 | Ulong Tee | Ulong ZS | 9 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 15 | 0.5 | 0.51 | 0.51 | 0.51 | 0.52
Coffs Harbour | 7502/2 | 66 | Ulong Tee | Dorrigo ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | 7509 | 66 | Moonee ZS | Woolgoolga ZS | 30 | 11.23 | 11.44 | 11.64 | 11.86 | 12.05 | 36 | 13.21 | 13.33 | 13.41 | 13.5 | 13.59
Coffs Harbour | 7510 | 66 | North Coffs ZS | Moonee ZS | 61 | 7.62 | 7.61 | 7.61 | 7.6 | 7.61 | 68 | 7.78 | 7.82 | 7.87 | 7.91 | 7.96
Coffs Harbour | 703:NGN | 66 | TransGrid Coffs Harbour 132/66 kV STS | Nana Glen ZS | 62 | 9.61 | 9.61 | 9.6 | 9.6 | 9.61 | 69 | 9.82 | 9.87 | 9.93 | 9.99 | 10.04
Coffs Harbour | 711:CHN | 66 | TransGrid Coffs Harbour 132/66 kV STS | North Coffs ZS | 62 | 19.35 | 19.34 | 19.33 | 19.32 | 19.34 | 69 | 19.77 | 19.87 | 19.99 | 20.1 | 20.21
Coffs Harbour | 87C | 66 | North Coffs ZS | South Coffs ZS | 68 | 12.11 | 12.1 | 12.1 | 12.09 | 12.1 | 68 | 12.37 | 12.43 | 12.51 | 12.58 | 12.65
Grafton | 825 | 66 | TransGrid Koolkhan 132/66kV STS | Koolkhan ZS | 62 | 20.21 | 20.3 | 20.42 | 20.51 | 20.56 | 69 | 18.09 | 18.13 | 18.16 | 18.19 | 18.23
Grafton | 826 | 66 | TransGrid Koolkhan 132/66kV STS | Grafton North ZS | 61 | 16.49 | 16.56 | 16.67 | 16.73 | 16.77 | 68 | 14.4 | 14.43 | 14.45 | 14.48 | 14.51
Grafton | 6503 | 66 | Grafton North ZS | South Grafton ZS | 24 | 10.77 | 10.82 | 10.89 | 10.93 | 10.96 | 25 | 8.42 | 8.44 | 8.45 | 8.47 | 8.49
Grafton | 6504 | 66 | Five Mile Sw Stn | South Grafton ZS | 61 | 4.66 | 4.68 | 4.71 | 4.73 | 4.74 | 68 | 3.64 | 3.65 | 3.65 | 3.66 | 3.67
Grafton | 6505 | 66 | Koolkhan SS | Grafton ZS | 52 | 17.93 | 18.01 | 18.12 | 18.2 | 18.24 | 58 | 15.54 | 15.57 | 15.6 | 15.63 | 15.66
Grafton | 6506 | 66 | Shannon Creek ZS | Nymboida ZS | 14 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 21 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Grafton | 6508 | 66 | Maclean ZS | Yamba ZS | 28 | 11.2 | 11.28 | 11.39 | 11.46 | 11.56 | 32 | 11.55 | 11.61 | 11.66 | 11.75 | 11.81
Grafton | 6509 | 66 | Shannon Creek ZS | Five Mile Sw Stn | 14 | 1.28 | 1.28 | 1.29 | 1.3 | 1.3 | 21 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Grafton | 6510 | 66 | Grafton North ZS | Five Mile Sw Stn | 28 | 5.83 | 5.85 | 5.89 | 5.91 | 5.93 | 34 | 4.52 | 4.53 | 4.54 | 4.55 | 4.56
Grafton | 896:MLN | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 21 | 9.61 | 9.65 | 9.71 | 9.75 | 9.77 | 25 | 8.73 | 8.75 | 8.77 | 8.78 | 8.8
Grafton | 8G1 | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 68 | 12.33 | 12.38 | 12.46 | 12.51 | 12.54 | 68 | 11.07 | 11.09 | 11.11 | 11.13 | 11.16
Grafton | 6402 | 33 | Maclean ZS | Yamba Tee | 8 | 0.5 | 0.5 | 0.51 | 0.51 | 0.51 | 9 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31
Grafton | 6403 | 33 | Yamba Tee | Redcliff ZS | 3 | 0.5 | 0.5 | 0.51 | 0.51 | 0.51 | 5 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Grafton | 6404 | 33 | Yamba Tee | Yamba ZS | 10 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7Y1 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 4.43 | 4.45 | 4.43 | 4.45 | 4.45 | 12 | 4.23 | 4.23 | 4.23 | 4.23 | 4.23
Hawks Nest | 7Y2 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 4.07 | 4.08 | 4.07 | 4.09 | 4.08 | 12 | 3.88 | 3.88 | 3.88 | 3.88 | 3.88
Hawks Nest | 7V1 | 33 | Ausgrid Salt Ash ZS | Tee with 7Y1 | 7 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Herons Creek | 866:KEW | 66 | Herons Creek 132/66kV STS | Kew ZS | 16 | 13.06 | 13.32 | 13.53 | 13.71 | 13.87 | 25 | 11.74 | 11.78 | 11.82 | 11.88 | 11.89
Herons Creek | 871 | 66 | Kew ZS | Laurieton ZS | 36 | 6.75 | 6.7 | 6.64 | 6.6 | 6.55 | 42 | 7.54 | 7.47 | 7.41 | 7.35 | 7.29
Herons Creek | 862/1 | 66 | Kew ZS | Johns River ZS | 16 | 0.91 | 0.9 | 0.89 | 0.88 | 0.87 | 25 | 0.97 | 0.98 | 0.98 | 0.99 | 0.99
Herons Creek | 862/2 | 66 | TransGrid Taree 132/66/33kV STS | Johns River ZS | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Kempsey | 7R1 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 30 | 7.52 | 7.58 | 7.64 | 7.67 | 7.72 | 34 | 7.7 | 7.74 | 7.77 | 7.82 | 7.85
Kempsey | 7R2/1 | 33 | TransGrid Kempsey 132/33kV STS | North St Tee | 26 | 8.71 | 8.77 | 8.85 | 8.88 | 8.93 | 29 | 8.52 | 8.57 | 8.6 | 8.65 | 8.69
Kempsey | 7R2/2 | 33 | North St Tee | Smithtown ZS | 19 | 4.35 | 4.38 | 4.42 | 4.44 | 4.47 | 21 | 5.01 | 5.03 | 5.05 | 5.08 | 5.1
Kempsey | 7R2/3 | 33 | North St Tee | North St ZS | 10 | 4.29 | 4.32 | 4.36 | 4.37 | 4.4 | 19 | 3.48 | 3.5 | 3.52 | 3.54 | 3.55
Kempsey | 7R3 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 26 | 7.56 | 7.61 | 7.68 | 7.7 | 7.75 | 29 | 7.73 | 7.77 | 7.8 | 7.85 | 7.88
Kempsey | 7R4 | 33 | TransGrid Kempsey 132/33kV STS | Munga ZS | 3 | 1.57 | 1.57 | 1.57 | 1.57 | 1.57 | 4 | 1.32 | 1.33 | 1.34 | 1.35 | 1.36
Kempsey | 7R5 | 33 | TransGrid Kempsey 132/33kV STS | North St ZS | 19 | 6.59 | 6.64 | 6.7 | 6.72 | 6.76 | 21 | 6.46 | 6.5 | 6.52 | 6.56 | 6.59
Kempsey | 7R6/1 | 33 | Prince St ZS | South West Rocks Tee | 15 | 5.51 | 5.55 | 5.59 | 5.61 | 5.65 | 18 | 6.05 | 6.09 | 6.11 | 6.14 | 6.17
Kempsey | 7R6/2 | 33 | South West Rocks Tee | South West Rocks ZS | 19 | 2.79 | 2.8 | 2.83 | 2.84 | 2.86 | 21 | 3.14 | 3.15 | 3.17 | 3.18 | 3.2
Kempsey | 7R6/3 | 33 | South West Rocks Tee | Smithtown ZS | 19 | 2.59 | 2.61 | 2.63 | 2.64 | 2.66 | 21 | 2.76 | 2.77 | 2.78 | 2.8 | 2.81
Kempsey | 7R7 | 33 | Prince St ZS | Crescent Head ZS | 5 | 1.61 | 1.62 | 1.62 | 1.62 | 1.63 | 8 | 1.88 | 1.89 | 1.9 | 1.91 | 1.92
Kempsey | 7R8 | 33 | Smithtown ZS | South West Rocks ZS | 30 | 3.3 | 3.32 | 3.35 | 3.36 | 3.38 | 34 | 3.67 | 3.7 | 3.71 | 3.73 | 3.75
Lismore | 9U8 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 183 | 59.13 | 59.66 | 60.17 | 60.89 | 61.34 | 214 | 59.38 | 60.53 | 61.56 | 62.45 | 63.22
Lismore | 9U9 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 54.72 | 55.21 | 55.68 | 56.35 | 56.77 | 143 | 54.92 | 55.99 | 56.94 | 57.76 | 58.48
Lismore | 9W1 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 50.63 | 51.09 | 51.53 | 52.14 | 52.53 | 143 | 50.8 | 51.79 | 52.67 | 53.43 | 54.09
Lismore | 9G2 | 132 | Ballina ZS | Lennox Head ZS | 124 | 13.07 | 13.18 | 13.3 | 13.46 | 13.56 | 139 | 11.88 | 12.11 | 12.31 | 12.49 | 12.64
Lismore | 9G3 | 132 | Lennox Head ZS | Suffolk Park ZS | 124 | 17.48 | 17.63 | 17.78 | 18 | 18.13 | 139 | 17.32 | 17.65 | 17.95 | 18.21 | 18.44
Lismore | 9G4 | 132 | Suffolk Park ZS | Ewingsdale ZS | 124 | 24.34 | 24.55 | 24.77 | 25.06 | 25.25 | 139 | 24.91 | 25.39 | 25.82 | 26.19 | 26.52
Lismore | 9G5 | 132 | Ewingsdale ZS | Mullumbimby ZS | 122 | 42.47 | 42.85 | 43.22 | 43.73 | 44.06 | 137 | 47.34 | 48.26 | 49.07 | 49.78 | 50.4
Lismore | 9U6 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 78.4 | 79.1 | 79.78 | 80.73 | 81.34 | 123 | 79.17 | 80.71 | 82.08 | 83.26 | 84.3
Lismore | 9U6/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 63.7 | 64.27 | 64.82 | 65.6 | 66.09 | 123 | 64.33 | 65.57 | 66.69 | 67.65 | 68.49
Lismore | 9U7 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 81.67 | 82.4 | 83.11 | 84.1 | 84.73 | 123 | 82.47 | 84.07 | 85.5 | 86.73 | 87.81
Lismore | 9U7/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 66.97 | 67.57 | 68.15 | 68.96 | 69.48 | 123 | 67.62 | 68.94 | 70.11 | 71.12 | 72
Lismore | 892 | 66 | Lismore 132/66kV STS | Woodburn ZS | 11 | 7.23 | 7.28 | 7.34 | 7.37 | 7.4 | 19 | 7.11 | 7.18 | 7.24 | 7.3 | 7.34
Lismore | 893 | 66 | Lismore 132/66kV STS | Casino ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Lismore | 894:LME | 66 | Lismore 132/66kV STS | Kyogle ZS | 11 | 7.45 | 7.36 | 7.27 | 7.18 | 7.13 | 19 | 6.81 | 6.84 | 6.88 | 6.9 | 6.93
Lismore | 0897:LME | 66 | Lismore 132/66kV STS | Alstonville ZS | 62 | 20.74 | 20.93 | 21.11 | 21.36 | 21.52 | 69 | 22.27 | 22.7 | 23.08 | 23.42 | 23.71
Lismore | 8502 | 66 | Lismore East ZS | Alstonville ZS | 62 | 10.94 | 11.04 | 11.14 | 11.27 | 11.35 | 69 | 12.37 | 12.61 | 12.82 | 13.01 | 13.17
Lismore | 8503 | 66 | Ballina ZS | Alstonville ZS | 62 | 9.64 | 9.72 | 9.81 | 9.92 | 10 | 69 | 9.9 | 10.09 | 10.26 | 10.41 | 10.54
Lismore | 8507 | 66 | Alstonville ZS | Ballina ZS | 61 | 11.11 | 11.21 | 11.3 | 11.44 | 11.52 | 68 | 11.55 | 11.77 | 11.97 | 12.14 | 12.29
Lismore | 8510 | 66 | Lismore Sw Stn | East Lismore ZS | 61 | 24.99 | 25.21 | 25.43 | 25.73 | 25.93 | 68 | 26.56 | 27.07 | 27.53 | 27.93 | 28.27
Lismore | 8511 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 21.89 | 22.08 | 22.27 | 22.54 | 22.71 | 69 | 21.94 | 22.36 | 22.74 | 23.07 | 23.36
Lismore | 8512 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 11.04 | 11.17 | 11.32 | 11.42 | 11.52 | 54 | 9.59 | 9.76 | 9.93 | 10.08 | 10.23
Lismore | 8513 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 11.04 | 11.17 | 11.32 | 11.42 | 11.52 | 54 | 9.59 | 9.76 | 9.93 | 10.08 | 10.23
Lismore | 8514 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 3.74 | 3.78 | 3.77 | 3.8 | 3.84 | 68 | 3.45 | 3.45 | 3.44 | 3.44 | 3.44
Lismore | 8515 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 3.61 | 3.66 | 3.64 | 3.68 | 3.71 | 68 | 3.34 | 3.34 | 3.34 | 3.34 | 3.34
Lismore | 8516 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 21.72 | 21.92 | 22.11 | 22.37 | 22.54 | 69 | 21.77 | 22.19 | 22.57 | 22.9 | 23.18
Nambucca Heads | 751 | 66 | TransGrid Nambucca 132/66 kV STS | Nambucca ZS | 15 | 7.69 | 7.73 | 7.76 | 7.8 | 7.83 | 25 | 9.14 | 9.17 | 9.2 | 9.23 | 9.25
Port Macquarie | 70Y | 33 | Rocks Ferry ZS | Telegraph Point ZS | 8 | 1.8 | 1.81 | 1.81 | 1.83 | 1.83 | 12 | 2.12 | 2.15 | 2.18 | 2.21 | 2.24
Port Macquarie | 701 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 22 | 10.9 | 10.99 | 11.1 | 11.24 | 11.31 | 26 | 10.79 | 10.85 | 10.9 | 10.96 | 11.01
Port Macquarie | 703:BPM | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 9.03 | 9.11 | 9.2 | 9.32 | 9.38 | 29 | 9.24 | 9.29 | 9.34 | 9.38 | 9.43
Port Macquarie | 707 | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 10.23 | 10.32 | 10.42 | 10.55 | 10.62 | 29 | 10.38 | 10.44 | 10.49 | 10.54 | 10.6
Port Macquarie | 708 | 33 | TransGrid Port Macquarie 132/33kV STS | Owen Street ZS | 26 | 11.87 | 11.97 | 12.09 | 12.24 | 12.32 | 29 | 13.49 | 13.56 | 13.63 | 13.7 | 13.77
Port Macquarie | 710 | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 31 | 12.91 | 13.03 | 13.15 | 13.32 | 13.4 | 34 | 15.53 | 15.61 | 15.7 | 15.77 | 15.85
Port Macquarie | 711:CPM | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 20 | 12.84 | 12.95 | 13.08 | 13.24 | 13.33 | 20 | 15.53 | 15.61 | 15.7 | 15.77 | 15.85
Port Macquarie | 712 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 12 | 7.24 | 7.3 | 7.38 | 7.47 | 7.52 | 14 | 7.11 | 7.15 | 7.19 | 7.22 | 7.26
Port Macquarie | 715 | 33 | Clearwater ZS | Owen Street ZS | 31 | 5.37 | 5.42 | 5.47 | 5.54 | 5.58 | 34 | 4.25 | 4.27 | 4.3 | 4.32 | 4.34
Port Macquarie | 719/1 | 33 | Clearwater ZS | Lake Cathie ZS | 20 | 6.13 | 6.37 | 6.53 | 6.69 | 6.83 | 20 | 7.04 | 7.11 | 7.17 | 7.23 | 7.29
Port Macquarie | 719/2 | 33 | Lake Cathie ZS | Laurieton ZS | 12 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0
Port Macquarie | 765 | 33 | Rocks Ferry ZS | Koree ZS | 9 | 4.85 | 4.89 | 4.94 | 5.01 | 5.04 | 11 | 5.31 | 5.34 | 5.37 | 5.4 | 5.42
Port Macquarie | 784 | 33 | Koree ZS | Byabarra ZS | 9 | 1.27 | 1.28 | 1.29 | 1.31 | 1.32 | 11 | 1.31 | 1.31 | 1.32 | 1.33 | 1.33
Stroud | 9C9/3 | 33 | Stroud 132/33kV STS | Dungog ZS | 27 | 8.26 | 8.27 | 8.28 | 8.3 | 8.3 | 27 | 5.25 | 5.28 | 5.3 | 5.33 | 5.35
Stroud | 9C9/2 | 33 | Dungog ZS | Martins Creek ZS | 21 | 6.49 | 6.52 | 6.54 | 6.54 | 6.57 | 27 | 4.05 | 4.08 | 4.1 | 4.13 | 4.16
Stroud | STR4B3/1 | 33 | Stroud 132/33kV STS | Booral ZS | 7 | 5.08 | 5.08 | 5.09 | 5.1 | 5.1 | 12 | 6.09 | 6.19 | 6.23 | 6.3 | 6.38
Stroud | STR4B3/2 | 33 | Booral ZS | Bulahdelah ZS | 7 | 3.64 | 3.64 | 3.65 | 3.66 | 3.66 | 12 | 4.39 | 4.46 | 4.49 | 4.54 | 4.59
Stroud | STR4B4 | 33 | Stroud 132/33kV STS | Dungog ZS | 4 | 2.86 | 2.86 | 2.87 | 2.87 | 2.87 | 6 | 1.75 | 1.76 | 1.77 | 1.78 | 1.78
Stroud | STR4B5/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 7.21 | 7.21 | 7.23 | 7.24 | 7.25 | 19 | 6.7 | 6.81 | 6.86 | 6.94 | 7.02
Stroud | STR4B5/2 | 33 | Wards River Sw Stn | Stratford Tee | 19 | 8.49 | 8.64 | 8.78 | 8.91 | 9.05 | 21 | 7.36 | 7.34 | 7.35 | 7.35 | 7.35
Stroud | STR4B5/2a | 33 | Stratford Tee | Stratford Coal ZS | 7 | 5.28 | 5.38 | 5.46 | 5.55 | 5.65 | 12 | 4.91 | 4.89 | 4.9 | 4.91 | 4.92
Stroud | STR4B5/3 | 33 | Stratford Tee | Gloucester ZS | 19 | 2.98 | 3.03 | 3.08 | 3.12 | 3.16 | 21 | 2.29 | 2.29 | 2.28 | 2.28 | 2.27
Stroud | STR4B6/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 8.32 | 8.32 | 8.34 | 8.35 | 8.36 | 19 | 7.76 | 7.88 | 7.94 | 8.03 | 8.12
Stroud | STR4B6/2 | 33 | Wards River Sw Stn | Gloucester ZS | 17 | 5.79 | 5.88 | 5.99 | 6.05 | 6.13 | 19 | 4.44 | 4.44 | 4.43 | 4.42 | 4.41
Stroud | STR4B7 | 33 | Stroud 132/33kV STS | Dungog ZS | 7 | 4.29 | 4.3 | 4.3 | 4.31 | 4.31 | 12 | 3.16 | 3.18 | 3.19 | 3.21 | 3.22
Stroud | STR4B8 | 33 | Stroud 132/33kV STS | Bulahdelah ZS | 7 | 4.6 | 4.6 | 4.61 | 4.62 | 4.62 | 12 | 5.2 | 5.29 | 5.33 | 5.39 | 5.45
Stroud | 3801 | 33 | Bulahdelah ZS | Pacific Palms ZS | 7 | 4.39 | 4.4 | 4.4 | 4.41 | 4.4 | 12 | 5.06 | 5.14 | 5.23 | 5.3 | 5.39
Stroud | 3803 | 33 | Bulahdelah ZS | Bungwahl Sw Stn | 7 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0
Stroud | BLH4B4 | 33 | Bulahdelah ZS | Hawks Nest 132/33kV STS | 7 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 12 | 0.31 | 0.31 | 0.31 | 0.32 | 0.32
Stroud | 7J1 | 33 | Ausgrid Recloser 33175 (Patterson) | Martins Creek Tee | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0
Stroud | 7J1/2 | 33 | Martins Creek Tee | Martins Creek ZS | 4 | 2.63 | 2.66 | 2.68 | 2.7 | 2.73 | 7 | 1.77 | 1.8 | 1.84 | 1.87 | 1.92
Stroud | 7J1/3 | 33 | Martins Creek Tee | Gresford ZS | 4 | 2.63 | 2.66 | 2.68 | 2.7 | 2.73 | 7 | 1.77 | 1.8 | 1.84 | 1.87 | 1.92
Taree | 861 | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 10.45 | 10.46 | 10.48 | 10.53 | 10.57 | 69 | 8.2 | 8.23 | 8.25 | 8.27 | 8.31
Taree | 863:WTE | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 10.83 | 10.84 | 10.85 | 10.91 | 10.95 | 69 | 8.42 | 8.45 | 8.47 | 8.49 | 8.53
Taree | 867 | 66 | TransGrid Taree 132/66/33kV STS | Hallidays Point ZS | 34 | 14.69 | 14.7 | 14.72 | 14.8 | 14.85 | 39 | 17.18 | 17.23 | 17.27 | 17.32 | 17.39
Taree | 867/1 | 66 | Hallidays Point Tee | Tuncurry ZS | 39 | 14.69 | 14.7 | 14.72 | 14.8 | 14.85 | 43 | 11.34 | 11.38 | 11.4 | 11.43 | 11.48
Taree | 868/1 | 66 | TransGrid Taree 132/66/33kV STS | Bohnock Tee | 36 | 17.21 | 17.22 | 17.25 | 17.33 | 17.39 | 41 | 20.76 | 20.82 | 20.86 | 20.92 | 21.01
Taree | 868/2 | 66 | Bohnock Tee | Bohnock ZS | 16 | 6.65 | 6.68 | 6.7 | 6.73 | 6.75 | 26 | 6.97 | 7.03 | 7.08 | 7.13 | 7.19
Taree | 868/3 | 66 | Bohnock Tee | Hallidays Point ZS | 38 | 12.6 | 12.61 | 12.63 | 12.69 | 12.73 | 43 | 14.37 | 14.41 | 14.44 | 14.48 | 14.55
Taree | 872 | 66 | Tuncurry ZS | Forster ZS | 30 | 7.4 | 7.4 | 7.41 | 7.45 | 7.48 | 37 | 9.08 | 9.11 | 9.13 | 9.16 | 9.2
Taree | 86C | 66 | Tuncurry ZS | Forster ZS | 42 | 6.49 | 6.49 | 6.5 | 6.53 | 6.56 | 46 | 8.09 | 8.12 | 8.14 | 8.16 | 8.19
Taree | 86R | 66 | Hallidays Point ZS | Tuncurry ZS | 38 | 12.33 | 12.34 | 12.36 | 12.42 | 12.46 | 43 | 15.03 | 15.08 | 15.11 | 15.15 | 15.22
Taree | 7G2/1 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Tee | 22 | 6.67 | 6.68 | 6.69 | 6.67 | 6.66 | 27 | 5.69 | 5.7 | 5.7 | 5.7 | 5.72
Taree | 7G2/2 | 33 | Kanangra Tee | Coopernook ZS | 7 | 5.7 | 5.71 | 5.72 | 5.71 | 5.7 | 12 | 5.13 | 5.13 | 5.14 | 5.14 | 5.15
Taree | 7G2/3 | 33 | Coopernook ZS | Harrington ZS | 8 | 3.85 | 3.86 | 3.89 | 3.9 | 3.92 | 13 | 3.72 | 3.74 | 3.75 | 3.77 | 3.78
Taree | 7G4 | 33 | Bootawa ZS | Wingham ZS | 18 | 2.65 | 2.65 | 2.66 | 2.65 | 2.65 | 21 | 2.46 | 2.46 | 2.46 | 2.46 | 2.47
Taree | 7G5 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Dr ZS | 17 | 9.81 | 9.83 | 9.85 | 9.82 | 9.81 | 17 | 8.44 | 8.45 | 8.46 | 8.46 | 8.48
Taree | 7G1 | 33 | TransGrid Taree 132/66/33kV STS | Bootawa ZS | 17 | 7.17 | 7.17 | 7.19 | 7.17 | 7.16 | 19 | 5.67 | 5.67 | 5.68 | 5.68 | 5.69
Taree | 7G3 | 33 | TransGrid Taree 132/66/33kV STS | Wingham ZS | 18 | 7.54 | 7.55 | 7.56 | 7.54 | 7.54 | 20 | 6.15 | 6.15 | 6.16 | 6.16 | 6.17
Terranora | 757 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 104.4 | 104.4 | 104.4 | 104.4 | 104.4 | 119 | 104.4 | 104.4 | 104.4 | 104.4 | 104.4
Terranora | 758 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 105.36 | 105.36 | 105.36 | 105.36 | 105.36 | 119 | 105.36 | 105.36 | 105.36 | 105.36 | 105.36
Terranora | 9501 | 66 | Terranora 110/66kV STS | Cudgen ZS | 59 | 27.08 | 27.62 | 28.15 | 28.66 | 29.08 | 66 | 23.88 | 23.99 | 24.08 | 24.16 | 24.25
Terranora | 9502 | 66 | Terranora 110/66kV STS | Murwillumbah ZS | 61 | 10.71 | 10.85 | 11.04 | 11.2 | 11.36 | 68 | 9.66 | 9.62 | 9.59 | 9.56 | 9.52
Terranora | 9503 | 66 | Terranora 110/66kV STS | Banora Pt ZS | 59 | 31.83 | 32.02 | 32.27 | 32.52 | 32.72 | 66 | 23.92 | 23.93 | 23.94 | 23.95 | 23.95
Terranora | 9504 | 66 | Terranora 110/66kV STS | Condong Sw Stn | 61 | 9.63 | 9.77 | 9.93 | 10.08 | 10.23 | 68 | 8.78 | 8.75 | 8.72 | 8.69 | 8.65
Terranora | 9505 | 66 | Cudgen ZS | Banora Point ZS | 53 | 1.28 | 1.29 | 1.3 | 1.31 | 1.32 | 59 | 1.01 | 1.01 | 1.01 | 1.01 | 1
Terranora | 9508 | 66 | Terranora 110/66kV STS | Tweed Heads ZS | 41 | 16.17 | 16.17 | 16.18 | 16.17 | 16.15 | 46 | 12.14 | 12.12 | 12.13 | 12.14 | 12.13
Terranora | 9510 | 66 | Banora Point ZS | Tweed Heads South ZS | 43 | 16.3 | 16.43 | 16.57 | 16.72 | 16.82 | 50 | 13.9 | 13.91 | 13.92 | 13.92 | 13.92
Terranora | 9514 | 66 | Condong Sw Stn | Murwillumbah ZS | 61 | 18.2 | 18.45 | 18.77 | 19.03 | 19.32 | 68 | 15.8 | 15.75 | 15.69 | 15.64 | 15.58
Terranora | 9516 | 66 | Tweed Head South ZS | Tweed Heads ZS | 43 | 3.85 | 3.85 | 3.85 | 3.85 | 3.85 | 50 | 2.89 | 2.89 | 2.89 | 2.89 | 2.89
Terranora | 9406 | 33 | Cudgen ZS | Casuarina Sw Stn | 17 | 12.19 | 12.23 | 12.25 | 12.26 | 12.32 | 19 | 11.38 | 11.37 | 11.36 | 11.36 | 11.35
Terranora | 9407 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Terranora | 9409 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 12.19 | 12.23 | 12.25 | 12.26 | 12.32 | 20 | 11.38 | 11.37 | 11.36 | 11.36 | 11.35
Armidale | 661/1 | 66 | TransGrid Armidale 330/132/66kV STS | Hillgrove Tee | 20 | 0.76 | 0.76 | 0.75 | 0.75 | 0.75 | 24 | 1.07 | 1.08 | 1.09 | 1.09 | 1.1
Armidale | 661/2 | 66 | Hillgrove Tee | Hillgrove ZS | 16 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 20 | 0.44 | 0.44 | 0.44 | 0.45 | 0.45
Armidale | 661/3 | 66 | Hillgrove Tee | Oaky ZS | 20 | 0.46 | 0.46 | 0.46 | 0.46 | 0.46 | 24 | 0.63 | 0.64 | 0.64 | 0.65 | 0.65
Armidale | 662/1 | 66 | TransGrid Armidale 330/132/66kV STS | Uralla Tee | 12 | 5.28 | 5.31 | 5.33 | 5.35 | 5.37 | 17 | 8.37 | 8.45 | 8.53 | 8.59 | 8.66
Armidale | 662/2 | 66 | Uralla Tee | Uralla ZS | 9 | 2.73 | 2.74 | 2.76 | 2.77 | 2.78 | 15 | 4.58 | 4.62 | 4.65 | 4.69 | 4.72
Armidale | 662/4 | 66 | Uralla Tee | Walcha South ZS | 9 | 2.56 | 2.57 | 2.58 | 2.59 | 2.6 | 15 | 3.8 | 3.84 | 3.88 | 3.91 | 3.95
Armidale | 664 | 66 | TransGrid Armidale 330/132/66kV STS | Galloway St ZS | 28 | 12.48 | 12.47 | 12.44 | 12.43 | 12.41 | 34 | 24.39 | 24.59 | 24.76 | 24.93 | 25.13
Armidale | 665 | 66 | TransGrid Armidale 330/132/66kV STS | Madgwick Dr ZS | 21 | 8.02 | 8.01 | 8 | 7.99 | 7.98 | 39 | 13.68 | 13.79 | 13.89 | 13.98 | 14.09
Armidale | 66C | 66 | Miller St ZS | Madgwick Dr ZS | 21 | 1.59 | 1.59 | 1.59 | 1.59 | 1.59 | 39 | 3.75 | 3.78 | 3.81 | 3.83 | 3.86
Armidale | 66F | 66 | Galloway St ZS | Miller St ZS | 15 | 5.73 | 5.72 | 5.71 | 5.7 | 5.7 | 25 | 9.59 | 9.67 | 9.74 | 9.8 | 9.88
Bathurst | 81H | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 62 | 8.53 | 8.5 | 8.5 | 8.52 | 8.51 | 69 | 8.47 | 8.56 | 8.65 | 8.73 | 8.8
Bathurst | 81G | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 64 | 12.18 | 12.15 | 12.15 | 12.16 | 12.16 | 71 | 12.11 | 12.23 | 12.35 | 12.47 | 12.58
Bathurst | 81F | 66 | TransGrid Panorama 132/66kV STS | Russell St ZS | 64 | 29.42 | 29.68 | 29.96 | 30.16 | 30.4 | 71 | 31.09 | 31.45 | 31.78 | 32.11 | 32.45
Bathurst | 81J | 66 | Raglan ZS | Russell St ZS | 64 | 5.62 | 5.67 | 5.73 | 5.77 | 5.81 | 71 | 5.94 | 6.01 | 6.08 | 6.14 | 6.2
Bathurst | 81L | 66 | TransGrid Panorama 132/66kV STS | Raglan ZS | 64 | 18.17 | 18.33 | 18.5 | 18.63 | 18.78 | 71 | 19.2 | 19.42 | 19.63 | 19.83 | 20.04
Bathurst | 81C | 66 | TransGrid Panorama 132/66kV STS | Blayney ZS | 25 | 12.8 | 12.81 | 12.86 | 12.87 | 12.89 | 29 | 17.49 | 17.81 | 18.07 | 18.31 | 18.57
Bathurst | 66:MAN | 66 | Blayney ZS | Mandurama ZS | 9 | 1.8 | 1.8 | 1.81 | 1.81 | 1.81 | 15 | 2.22 | 2.21 | 2.2 | 2.19 | 2.19
Beryl | 94M/4 | 132 | TransGrid 94M Mudgee Tee | Mudgee ZS | 128 | 28.32 | 28.85 | 29.37 | 29.85 | 30.38 | 143 | 25.03 | 25.11 | 25.23 | 25.32 | 25.42
Beryl | 851/1 | 66 | TransGrid Beryl 132/66kV STS | Gulgong ZS | 28 | 3.8 | 3.83 | 3.84 | 3.86 | 3.89 | 32 | 3.37 | 3.36 | 3.36 | 3.35 | 3.35
Beryl | 851/2 | 66 | Gulgong ZS | Mudgee ZS | 28 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0
Beryl | 852 | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Beryl | 86J | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 61 | 12.93 | 13.01 | 13.05 | 13.08 | 13.16 | 68 | 13.01 | 12.98 | 12.95 | 12.93 | 12.91
Beryl | 85A | 66 | Dunedoo ZS | Coonabarabran ZS | 11 | 8.7 | 8.74 | 8.73 | 8.73 | 8.76 | 19 | 9.08 | 9.05 | 9.05 | 9.03 | 9.02
Beryl | 80L | 66 | Ulan Sw Stn | Ulan Town ZS | 15 | 2.79 | 2.78 | 2.77 | 2.76 | 2.76 | 25 | 2.56 | 2.59 | 2.61 | 2.64 | 2.66
Beryl | 80R | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 64 | 44.39 | 44.47 | 44.45 | 44.54 | 44.62 | 71 | 43.06 | 43.1 | 43.26 | 43.22 | 43.2
Beryl | 80U | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 61 | 33.33 | 33.78 | 34.18 | 34.65 | 35.05 | 68 | 37.01 | 37.97 | 38.85 | 39.85 | 40.84
Beryl | 80T | 66 | Ulan Sw Stn | Moolarben No1 Mine ZS | 43 | 31.78 | 31.94 | 32.1 | 32.22 | 32.38 | 54 | 33.5 | 34.05 | 34.57 | 35.09 | 35.65
Beryl | 80W | 66 | Moolarben No1 Mine ZS | Moolarben No2 Mine ZS | 43 | 13.83 | 13.88 | 13.89 | 13.88 | 13.9 | 54 | 14.67 | 14.8 | 14.96 | 15.02 | 15.15
Beryl | 80X | 66 | Moolarben No2 Mine ZS | Wilpinjong Mine ZS | 43 | 5.29 | 5.29 | 5.29 | 5.3 | 5.3 | 54 | 5.43 | 5.45 | 5.44 | 5.46 | 5.47
Broken Hill | X4 | 220 | TransGrid Broken Hill 220/22kV STS | Perilya Mine | 427 | 24.62 | 24.62 | 24.6 | 24.62 | 24.6 | 477 | 24.28 | 24.26 | 24.28 | 24.24 | 24.26
Broken Hill | 5B1:PPL | 66 | Pinnacles Place ZS | Mt Gipps ZS | 19 | 5.57 | 5.93 | 5.92 | 5.92 | 5.92 | 33 | 5.11 | 5.93 | 5.95 | 5.98 | 6
Broken Hill | 5B1:MTG | 66 | Mt Gipps ZS | Sunset Strip ZS | 19 | 4.2 | 4.51 | 4.51 | 4.52 | 4.53 | 33 | 4.6 | 5.19 | 5.27 | 5.35 | 5.4
Broken Hill | 5B1:SUN | 66 | Sunset Strip ZS | Menindee ZS | 6 | 0.99 | 0.99 | 1 | 1 | 1 | 9 | 0.73 | 0.73 | 0.73 | 0.73 | 0.73
Dubbo | 94J/3 | 132 | 94J Tee | Dubbo South ZS | 106 | 50.93 | 50.9 | 50.99 | 50.98 | 51.03 | 119 | 38.96 | 39.19 | 39.33 | 39.49 | 39.64
Dubbo | 943/2 | 132 | Dubbo South ZS | Narromine South Sw Stn | 106 | 36.21 | 36.19 | 36.25 | 36.25 | 36.28 | 119 | 26.37 | 26.52 | 26.62 | 26.72 | 26.83
Dubbo | 94W/1 | 132 | Dubbo 132/66kV STS | Nevertire Tee | 128 | 139.51 | 139.38 | 139.24 | 139.13 | 139.01 | 143 | 120.23 | 120.19 | 120.16 | 120.12 | 120.1
Dubbo | 94W/2 | 132 | Nevertire Tee | Nevertire ZS | 124 | 7.24 | 7.36 | 7.49 | 7.59 | 7.7 | 139 | 6.95 | 6.91 | 6.86 | 6.84 | 6.8
Dubbo | 94W/3 | 132 | Nevertire Tee | Nevertire Sw Stn | 128 | 105.75 | 105.75 | 105.75 | 105.75 | 105.75 | 143 | 92.43 | 92.43 | 92.43 | 92.43 | 92.43
Dubbo | 9GX | 132 | Nevertire Sw Stn | Nyngan 132/66kV STS | 128 | 59.04 | 59.71 | 60.19 | 60.68 | 61.13 | 143 | 58.4 | 59.05 | 59.62 | 60.23 | 60.66
Dubbo | 9GP | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 14.02 | 14.22 | 14.41 | 14.6 | 14.74 | 139 | 13.35 | 13.37 | 13.39 | 13.43 | 13.45
Dubbo | 9GR | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GT | 132 | Dubbo West ZS | Narromine South Sw Stn | 140 | 48.65 | 49.23 | 49.8 | 50.42 | 50.87 | 157 | 45.13 | 45.39 | 45.66 | 45.94 | 46.14
Dubbo | 9GU | 132 | Narromine South Sw Stn | Nyngan 132/66kV STS | 106 | 76.38 | 77.26 | 78.16 | 79.15 | 79.88 | 119 | 70.3 | 70.86 | 71.47 | 72.05 | 72.5
Dubbo | 9GW | 132 | Dubbo 132/66kV STS | Dubbo West ZS | 140 | 39.39 | 39.37 | 39.44 | 39.43 | 39.47 | 157 | 34.26 | 34.46 | 34.59 | 34.72 | 34.86
Dubbo | 812 | 66 | Yarrandale ZS | Gilgandra ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Dubbo | 815 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 10.6 | 10.58 | 10.57 | 10.56 | 10.53 | 54 | 10.59 | 10.71 | 10.83 | 10.91 | 11
Dubbo | 816 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 10.6 | 10.58 | 10.57 | 10.56 | 10.53 | 54 | 10.59 | 10.71 | 10.83 | 10.91 | 11
Dubbo | 813:EUL | 66 | Eulomogo ZS | Geurie Tee | 12 | 1.57 | 1.57 | 1.57 | 1.56 | 1.56 | 18 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
Dubbo | 813/1:GUE | 66 | Geurie Tee | Geurie ZS | 16 | 1.57 | 1.57 | 1.57 | 1.56 | 1.56 | 27 | 1.12 | 1.12 | 1.12 | 1.12 | 1.12
Dubbo | 814/1 | 66 | Gilgandra ZS | Gulargambone ZS | 11 | 8.2 | 8.36 | 8.51 | 8.67 | 8.83 | 19 | 6.73 | 6.82 | 6.9 | 6.98 | 7.05
Dubbo | 814/2 | 66 | Gulargambone ZS | Coonamble ZS | 11 | 6.52 | 6.65 | 6.8 | 6.94 | 7.08 | 19 | 5.32 | 5.4 | 5.47 | 5.54 | 5.61
Dubbo | 81M | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 10.57 | 10.7 | 10.82 | 10.92 | 11.04 | 39 | 8.62 | 8.66 | 8.69 | 8.73 | 8.75
Dubbo | 81P | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 61 | 11 | 11.15 | 11.3 | 11.44 | 11.58 | 68 | 9.19 | 9.28 | 9.36 | 9.44 | 9.52
Dubbo | 81R | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 10.57 | 10.7 | 10.82 | 10.92 | 11.04 | 39 | 8.62 | 8.66 | 8.69 | 8.73 | 8.75
Dubbo | 81X | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 28 | 13.45 | 13.63 | 13.81 | 13.98 | 14.15 | 34 | 11.23 | 11.34 | 11.44 | 11.54 | 11.63
Dubbo | 81T | 66 | Yarrandale ZS | Gilgandra ZS | 43 | 15.84 | 16.03 | 16.22 | 16.41 | 16.6 | 54 | 12.86 | 12.94 | 13.03 | 13.1 | 13.18
Forbes | 858 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 13.63 | 13.62 | 13.64 | 13.64 | 13.66 | 34 | 11.64 | 11.71 | 11.77 | 11.84 | 11.89
Forbes | 859 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Forbes | 893/5 | 66 | TransGrid Forbes 132/66kV STS | Payten's Bridge ZS | 12 | 5.31 | 5.33 | 5.34 | 5.35 | 5.36 | 18 | 3.87 | 3.91 | 3.95 | 3.99 | 4.01
Forbes | 894:CDN | 66 | Condobolin ZS | Lake Cargelligo ZS | 15 | 4.06 | 4.13 | 4.18 | 4.24 | 4.3 | 25 | 3.49 | 3.57 | 3.65 | 3.72 | 3.79
Forbes | 896:WJL | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 20 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 24 | 21.54 | 21.54 | 21.54 | 21.54 | 21.54
Forbes | 897:CDN | 66 | West Jemalong ZS | Condobolin ZS | 20 | 11.19 | 11.15 | 11.1 | 11.05 | 11.01 | 24 | 10.84 | 10.9 | 10.96 | 11.01 | 11.06
Forbes | 89H | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 43 | 31.32 | 31.32 | 31.32 | 31.32 | 31.32 | 54 | 32.28 | 32.28 | 32.28 | 32.28 | 32.28
Glen Innes | 886 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 70 | 5.12 | 5.17 | 5.2 | 5.24 | 5.28 | 78 | 7.19 | 7.25 | 7.3 | 7.35 | 7.4
Glen Innes | 887 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 19 | 6.09 | 6.15 | 6.19 | 6.24 | 6.28 | 33 | 8.56 | 8.63 | 8.7 | 8.75 | 8.81
Glen Innes | 6NY | 66 | Glen Innes ZS | Guyra ZS | 11 | 3.49 | 3.51 | 3.54 | 3.55 | 3.58 | 19 | 5.47 | 5.51 | 5.54 | 5.57 | 5.59
Glen Innes | 6NE | 66 | Glen Innes ZS | Emmaville ZS | 17 | 1.03 | 1.04 | 1.05 | 1.06 | 1.06 | 30 | 1.34 | 1.35 | 1.36 | 1.37 | 1.38
Glen Innes | 6AE/A | 66 | Pindari ZS | Ashford ZS | 17 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0
Glen Innes | 6AE/E | 66 | Emmaville ZS | Pindari ZS | 17 | 0.36 | 0.36 | 0.36 | 0.37 | 0.37 | 30 | 0.42 | 0.43 | 0.43 | 0.43 | 0.44
Gunnedah | 877 | 66 | TransGrid Gunnedah 132/66kV STS | Keepit Dam ZS | 10 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 16 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28
Gunnedah | 88G/1 | 66 | Gunnedah ZS | Emerald Hill Sw Stn | 24 | 20.43 | 20.44 | 20.45 | 20.47 | 20.48 | 29 | 21.03 | 21.06 | 21.04 | 21.06 | 21.06
Gunnedah | 88G/2 | 66 | Emerald Hill Sw Stn | Boggabri ZS | 24 | 4.08 | 4.12 | 4.14 | 4.17 | 4.2 | 29 | 4.91 | 4.93 | 4.94 | 4.96 | 4.97
Gunnedah | 88K | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 21.5 | 21.5 | 21.49 | 21.46 | 21.47 | 68 | 20.59 | 20.58 | 20.55 | 20.54 | 20.52
Gunnedah | 88L | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 21.5 | 21.5 | 21.49 | 21.46 | 21.47 | 68 | 20.59 | 20.58 | 20.55 | 20.54 | 20.52
Inverell | 734 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 17.92 | 17.89 | 17.91 | 17.93 | 17.94 | 71 | 17.77 | 17.92 | 18.02 | 18.12 | 18.23
Inverell | 735 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 18.21 | 18.18 | 18.2 | 18.22 | 18.23 | 71 | 18.06 | 18.21 | 18.31 | 18.41 | 18.53
Inverell | 6AB | 66 | Borthwick St ZS | Ashford ZS | 17 | 6.54 | 6.53 | 6.54 | 6.54 | 6.55 | 30 | 5.23 | 5.27 | 5.3 | 5.33 | 5.37
Inverell | 6AF/A | 66 | Ashford ZS | Wallangra ZS | 11 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 19 | 0.93 | 0.94 | 0.94 | 0.95 | 0.96
Inverell | 6AF/F | 66 | Wallangra ZS | Coolatai Sw Stn | 11 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 19 | 0.79 | 0.79 | 0.8 | 0.8 | 0.81
Inverell | 6AX | 66 | Ashford ZS | Texas ZS | 9 | 5.46 | 5.45 | 5.45 | 5.46 | 5.46 | 15 | 3.55 | 3.58 | 3.6 | 3.62 | 3.64
Inverell | 6BC | 66 | Borthwick St ZS | Copeton ZS | 21 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 41 | 0.9 | 0.9 | 0.91 | 0.91 | 0.92
Inverell | 6BD | 66 | Borthwick St ZS | Bundarra ZS | 14 | 0.94 | 0.94 | 0.94 | 0.94 | 0.94 | 21 | 1.11 | 1.12 | 1.13 | 1.13 | 1.14
Inverell | 6BW | 66 | Borthwick St ZS | Warialda ZS | 15 | 7.19 | 7.18 | 7.19 | 7.19 | 7.2 | 25 | 6.2 | 6.25 | 6.29 | 6.32 | 6.36
Inverell | 6FH | 66 | Coolatai Sw Stn | Yallaroi ZS | 20 | 2.28 | 2.27 | 2.28 | 2.28 | 2.28 | 39 | 2.04 | 2.06 | 2.07 | 2.08 | 2.1
Inverell | 6FW | 66 | Warialda ZS | Coolatai Sw Stn | 11 | 1.73 | 1.73 | 1.73 | 1.74 | 1.74 | 19 | 1.22 | 1.23 | 1.24 | 1.24 | 1.25
Inverell | 6HG | 66 | Yallaroi ZS | Goondiwindi ZS | 20 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Inverell | 6WK | 66 | Warialda ZS | Bingara ZS | 11 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 19 | 2.62 | 2.64 | 2.65 | 2.67 | 2.68
Molong | 8C1 | 66 | TransGrid Molong 132/66kV STS | Cumnock / Orange West Tee | 61 | 1.45 | 1.44 | 1.45 | 1.45 | 1.46 | 68 | 1.58 | 1.59 | 1.61 | 1.63 | 1.65
Molong | 8C1/3 | 66 | Cumnock / Orange West Tee | Cumnock ZS | 9 | 1.45 | 1.44 | 1.45 | 1.45 | 1.46 | 15 | 1.58 | 1.59 | 1.61 | 1.63 | 1.65
Molong | 8C1/4 | 66 | Cumnock / Orange West Tee | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Moree | 876 | 66 | TransGrid Moree 132/66kV STS | Moree Solar Farm | 70 | 57.37 | 57.31 | 57.36 | 57.51 | 57.47 | 78 | 57.7 | 57.62 | 57.72 | 57.72 | 57.77
Moree | 87J | 66 | Moree Solar Farm | Bellata ZS | 25 | 1.16 | 1.18 | 1.19 | 1.21 | 1.22 | 27 | 1.05 | 1.07 | 1.09 | 1.1 | 1.11
Moree | 721 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 11.04 | 11.92 | 13.94 | 15.78 | 17.37 | 71 | 11.26 | 12.22 | 14.31 | 16.2 | 17.86
Moree | 722 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 11.7 | 12.64 | 14.78 | 16.72 | 18.41 | 71 | 11.93 | 12.95 | 15.16 | 17.17 | 18.93
Moree | 881/1 | 66 | TransGrid Moree 132/66kV STS | Ashley Tee | 15 | 4.44 | 4.47 | 4.5 | 4.52 | 4.55 | 25 | 9.11 | 9.15 | 9.18 | 9.2 | 9.22
Moree | 881/2 | 66 | Ashley Tee | Ashley ZS | 10 | 1.38 | 1.42 | 1.46 | 1.49 | 1.53 | 16 | 3.59 | 3.63 | 3.66 | 3.68 | 3.71
Moree | 6PU | 66 | Ashley Tee | Mungindi ZS | 10 | 2.92 | 2.92 | 2.91 | 2.91 | 2.91 | 16 | 5.39 | 5.4 | 5.4 | 5.39 | 5.39
Moree | 723:WTR/1 | 66 | TransGrid Moree 132/66kV STS | Wathagar ZS | 12 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 19 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26
Moree | 723:WTR/2 | 66 | Wathagar ZS | Wenna ZS | 15 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 25 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26
Narrabri | 879 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 18 | 4.16 | 4.16 | 4.16 | 4.15 | 4.15 | 22 | 5.17 | 5.22 | 5.27 | 5.32 | 5.36
Narrabri | 882 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 64 | 8.1 | 8.09 | 8.08 | 8.07 | 8.07 | 71 | 10.06 | 10.14 | 10.25 | 10.34 | 10.42
Narrabri | 885 | 66 | Burren Junction ZS | Merrywinebone ZS | 15 | 1.58 | 1.6 | 1.61 | 1.62 | 1.63 | 25 | 2.9 | 2.89 | 2.89 | 2.88 | 2.88
Narrabri | 833:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 8.69 | 8.78 | 8.86 | 8.92 | 8.98 | 43 | 8.8 | 8.92 | 9.03 | 9.14 | 9.24
Narrabri | 834:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 8.69 | 8.78 | 8.86 | 8.92 | 8.98 | 43 | 8.8 | 8.92 | 9.03 | 9.14 | 9.24
Narrabri | 861/1 | 66 | TransGrid Narrabri 132/66kV STS | Wilga Park ZS | 64 | 41.25 | 41.09 | 40.71 | 40.89 | 54.81 | 71 | 60.46 | 62.76 | 65.81 | 69.02 | 81.06
Narrabri | 861/2 | 66 | Wilga Park ZS | Walgett ZS | 64 | 11.82 | 11.85 | 11.9 | 11.95 | 11.99 | 71 | 10.89 | 11.01 | 11.12 | 11.22 | 11.32
Narrabri | 88F | 66 | Narrabri Sw Stn | Boggabri ZS | 24 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0
Narrabri | 878/3 | 66 | TransGrid Narrabri 132/66kV STS | Narrabri Sw Stn | 61 | 20.04 | 20.04 | 20.04 | 20.04 | 20.04 | 68 | 20.04 | 20.04 | 20.04 | 20.04 | 20.04
Narrabri | 88C | 66 | Narrabri Sw Stn | Narrabri Coal | 53 | 19.78 | 19.78 | 19.78 | 19.78 | 19.78 | 61 | 19.78 | 19.78 | 19.78 | 19.78 | 19.78
Narrabri | 880/1 | 66 | Wee Waa ZS | Burren Junction ZS | 13 | 3.15 | 3.16 | 3.17 | 3.18 | 3.19 | 18 | 4.1 | 4.11 | 4.13 | 4.14 | 4.15
Narrabri | 880/2 | 66 | Burren Junction ZS | Walgett ZS | 13 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Narrabri | 890:BRE | 66 | Walgett ZS | Brewarrina ZS | 15 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 25 | 2.34 | 2.36 | 2.37 | 2.38 | 2.39
Narrabri | 895:LGR | 66 | Walgett ZS | Lightning Ridge ZS | 15 | 3.15 | 3.16 | 3.17 | 3.17 | 3.18 | 25 | 3.19 | 3.23 | 3.27 | 3.3 | 3.34
Nyngan | 9UT | 132 | Nyngan 132/66kV STS | Nyngan Solar Farm | 106 | 68.31 | 68.02 | 67.75 | 67.73 | 67.35 | 119 | 76.9 | 76.52 | 76.4 | 76.13 | 75.93
Nyngan | 9UW | 132 | Nyngan Solar Farm | Scrubby Valley Sw Stn | 106 | 46.23 | 46.67 | 46.89 | 47.08 | 47.33 | 119 | 48.72 | 49.32 | 49.83 | 50.38 | 50.75
Nyngan | 946/2 | 132 | Scrubby Valley Sw Stn | Cobar CSA ZS | 106 | 24.84 | 25.24 | 25.47 | 25.64 | 25.91 | 119 | 21.3 | 21.44 | 21.5 | 21.64 | 21.67
Nyngan | 946/3 | 132 | Scrubby Valley Sw Stn | Cobar Peak ZS | 102 | 14.06 | 14.34 | 14.56 | 14.79 | 14.99 | 114 | 20.81 | 21.33 | 21.82 | 22.28 | 22.69
Nyngan | 94R | 132 | Cobar CSA ZS | Cobar Elura ZS | 128 | 4.36 | 4.65 | 4.78 | 4.87 | 5.01 | 143 | 4.45 | 4.47 | 4.46 | 4.47 | 4.44
Nyngan | 811 | 66 | Nyngan 132/66kV STS | Cobar Town ZS | 10 | 7.91 | 7.97 | 8.05 | 8.13 | 8.2 | 16 | 7.15 | 7.17 | 7.19 | 7.2 | 7.22
Nyngan | 854 | 66 | Nyngan 132/66kV STS | Nyngan Town ZS | 15 | 5.48 | 5.48 | 5.48 | 5.47 | 5.49 | 25 | 4.67 | 4.69 | 4.71 | 4.73 | 4.75
Nyngan | 820/1:NYN | 66 | Nyngan Town ZS | Nevertire Tee | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Nyngan | 820:NVE | 66 | Nyngan 132/66kV STS | Nevertire ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/1 | 66 | Nyngan 132/66kV STS | Girilambone Tee | 28 | 15.53 | 15.69 | 15.81 | 15.93 | 16.06 | 34 | 14.77 | 15.1 | 15.41 | 15.69 | 15.97
Nyngan | 855/1a | 66 | Girilambone Tee | Girilambone ZS | 24 | 10.7 | 10.74 | 10.78 | 10.82 | 10.86 | 29 | 10.66 | 10.82 | 10.97 | 11.1 | 11.25
Nyngan | 855/2 | 66 | Girilambone Tee | Byrock Tee | 28 | 8.83 | 8.97 | 9.08 | 9.19 | 9.29 | 34 | 8.55 | 8.77 | 8.98 | 9.17 | 9.35
Nyngan | 855/3 | 66 | Byrock Tee | Bourke ZS | 28 | 8.44 | 8.58 | 8.69 | 8.79 | 8.89 | 34 | 8.34 | 8.55 | 8.76 | 8.94 | 9.11
Nyngan | 855/3a | 66 | Byrock Tee | Byrock ZS | 15 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 25 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08
Nyngan | 855/4 | 66 | Girilambone ZS | Tritton Mine ZS | 24 | 9.93 | 9.98 | 10.02 | 10.05 | 10.1 | 29 | 10.38 | 10.55 | 10.69 | 10.82 | 10.97
Oberon | 94C | 132 | TransGrid Wallerawang 330/132/66kV STS | Oberon 132 ZS | 128 | 32.61 | 33.03 | 33.52 | 34.02 | 34.54 | 143 | 31.72 | 32.26 | 32.76 | 33.24 | 33.68
Oberon | 856 | 66 | TransGrid Wallerawang 330/132/66kV STS | Oberon Town ZS | 28 | 3.87 | 3.91 | 3.87 | 3.92 | 3.95 | 32 | 6.28 | 6.26 | 6.24 | 6.23 | 6.21
Oberon | 81B | 33 | Oberon Town ZS | Burraga ZS | 8 | 0.36 | 0.35 | 0.34 | 0.34 | 0.34 | 13 | 0.46 | 0.46 | 0.45 | 0.45 | 0.45
Orange | 94G | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 86 | 87.47 | 88.75 | 90.01 | 91.16 | 142 | 86.19 | 87.2 | 87.71 | 88.57 | 89.25
Orange | 9MC | 132 | TransGrid Orange North 132kV Sw Stn | Flyers Creek Sw Stn | 142 | 91.27 | 92.82 | 94.19 | 95.52 | 96.74 | 142 | 91.46 | 92.54 | 93.09 | 93.99 | 94.71
Orange | 9MR | 132 | Flyers Creek Sw Stn | Cadia ZS | 180 | 140.41 | 142.81 | 144.9 | 146.96 | 148.83 | 202 | 140.72 | 142.36 | 143.21 | 144.6 | 145.71
Orange | 807 | 66 | TransGrid Orange 132/66kV STS | Orange West & South Tee | 61 | 11.19 | 11.2 | 11.19 | 11.2 | 11.2 | 68 | 15.03 | 15.04 | 15.04 | 15.05 | 15.04
Orange | 807/2 | 66 | Orange West & South Tee | Orange South ZS | 63 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0
Orange | 807/3 | 66 | Orange West & South Tee | Orange West ZS | 62 | 11.19 | 11.2 | 11.19 | 11.2 | 11.2 | 69 | 15.03 | 15.04 | 15.04 | 15.05 | 15.04
Orange | 818/1 | 66 | TransGrid Orange 132/66kV STS | Blayney ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Orange | 8C2 | 66 | TransGrid Orange 132/66kV STS | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0
Orange | 8F1 | 66 | TransGrid Orange 132/66kV STS | Orange South ZS | 63 | 17.25 | 17.13 | 17.1 | 17.01 | 16.93 | 70 | 24.72 | 24.85 | 24.94 | 25.04 | 25.14
Orange | 8M1 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 11 | 9.21 | 9.14 | 9.1 | 9.05 | 9.02 | 19 | 12.56 | 12.68 | 12.8 | 12.89 | 13.01
Orange | 8M2 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 21 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Parkes | 9MX | 132 | TransGrid Parkes 132/66kV STS | Quorn Park Sw Stn | 87 | 33.7 | 41.83 | 49.9 | 58.04 | 60.81 | 108 | 33.83 | 41.9 | 50.12 | 58.36 | 61.43
Parkes | 300 | 132 | Quorn Park Sw Stn | North Parkes Mine ZS | 87 | 33.7 | 41.83 | 49.9 | 58.04 | 60.81 | 108 | 33.83 | 41.9 | 50.12 | 58.36 | 61.43
Parkes | 898 | 66 | TransGrid Parkes 132/66kV STS | Trundle ZS | 10 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 16 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92
Parkes | 899 | 66 | Parkes Town ZS | Peak Hill ZS | 12 | 12.95 | 13.64 | 14.32 | 15.02 | 15.71 | 19 | 11.76 | 11.89 | 12.09 | 12.21 | 12.36
Parkes | 89G | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 61 | 16.56 | 16.96 | 17.35 | 17.72 | 18.11 | 68 | 14.38 | 14.62 | 14.88 | 15.1 | 15.32
Parkes | 89L | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 39 | 14.91 | 15.26 | 15.61 | 15.95 | 16.3 | 43 | 12.94 | 13.16 | 13.39 | 13.59 | 13.79
Parkes | 89M | 66 | Peak Hill ZS | Tomingley Mine ZS | 32 | 9.68 | 10.26 | 10.83 | 11.43 | 12.02 | 40 | 9.39 | 9.47 | 9.61 | 9.69 | 9.8
Tamworth | 801 | 66 | Transgrid Tamworth 132/66kV STS | Oxley Vale ZS | 63 | 14.8 | 14.89 | 14.95 | 15.02 | 15.08 | 70 | 13.09 | 13.23 | 13.35 | 13.49 | 13.6
Tamworth | 803 | 66 | Transgrid Tamworth 132/66kV STS | South Tamworth ZS | 70 | 29.74 | 29.99 | 30.21 | 30.44 | 30.69 | 78 | 30.47 | 30.63 | 30.75 | 30.9 | 31.02
Tamworth | 804 | 66 | Transgrid Tamworth 132/66kV STS | Nundle ZS | 8 | 1.94 | 1.93 | 1.93 | 1.93 | 1.92 | 13 | 1.64 | 1.66 | 1.67 | 1.69 | 1.71
Tamworth | 806 | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 38 | 12.4 | 18.05 | 18.98 | 19.77 | 19.72 | 47 | 10.91 | 16.12 | 16.82 | 17.89 | 18.79
Tamworth | 873 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 16.28 | 16.39 | 16.5 | 16.61 | 16.69 | 61 | 15.13 | 15.72 | 16.23 | 16.66 | 17.06
Tamworth | 874 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 16.95 | 17.06 | 17.17 | 17.29 | 17.38 | 61 | 15.75 | 16.36 | 16.89 | 17.34 | 17.75
Tamworth | 803/2 | 66 | South Tamworth ZS | Oxley Vale ZS | 63 | 4.93 | 4.96 | 4.98 | 5.01 | 5.03 | 70 | 4.36 | 4.41 | 4.45 | 4.5 | 4.53
Tamworth | 806/1 | 66 | Goddard Lane ZS | Attunga ZS | 18 | 12.08 | 12.06 | 12.03 | 12.01 | 11.97 | 33 | 9.12 | 9.16 | 9.19 | 9.23 | 9.26
Tamworth | 806/2 | 66 | Attunga ZS | Manilla ZS | 18 | 8.41 | 8.48 | 8.52 | 8.56 | 8.59 | 33 | 6.75 | 6.79 | 6.83 | 6.86 | 6.89
Tamworth | 806/3 | 66 | Manilla ZS | Upper Manilla ZS | 18 | 2.4 | 2.38 | 2.37 | 2.35 | 2.34 | 33 | 2.49 | 2.5 | 2.51 | 2.53 | 2.54
Tamworth | 806/4 | 66 | Upper Manilla ZS | Barraba ZS | 15 | 2.07 | 2.05 | 2.03 | 2.02 | 2.01 | 25 | 2.4 | 2.41 | 2.42 | 2.44 | 2.45
Tamworth | 80C | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 61 | 11 | 16.01 | 16.83 | 17.53 | 17.48 | 68 | 9.68 | 14.3 | 14.91 | 15.86 | 16.67
Tamworth | 813:CLA | 66 | Transgrid Tamworth 132/66kV STS | Currububula ZS | 28 | 15.64 | 15.57 | 15.54 | 15.51 | 15.46 | 34 | 13.27 | 13.34 | 13.42 | 13.48 | 13.54
Tamworth | 813/1:QDI | 66 | Currububula ZS | Werris Creek ZS | 28 | 14.36 | 14.31 | 14.29 | 14.27 | 14.24 | 34 | 12.2 | 12.26 | 12.33 | 12.38 | 12.43
Tamworth | 813/2:QDI | 66 | Werris Creek ZS | Quirindi ZS | 28 | 12.61 | 12.57 | 12.58 | 12.58 | 12.57 | 34 | 10.6 | 10.67 | 10.74 | 10.79 | 10.85
Tamworth | 870/1:KTL | 66 | Transgrid Tamworth 132/66kV STS | Kootingal Tee | 14 | 7.36 | 7.43 | 7.54 | 7.62 | 7.68 | 21 | 6.51 | 6.56 | 6.59 | 6.62 | 6.66
Tamworth | 870/2:KTL | 66 | Kootingal Tee | Kootingal ZS | 12 | 6.68 | 6.76 | 6.85 | 6.93 | 6.98 | 20 | 5.77 | 5.81 | 5.84 | 5.87 | 5.9
Tamworth | 870/3:KTL | 66 | Kootingal Tee | Bendemeer ZS | 13 | 0.68 | 0.69 | 0.69 | 0.7 | 0.71 | 21 | 0.74 | 0.75 | 0.75 | 0.76 | 0.76
Tamworth | 798 | 33 | Quirindi ZS | Murrurundi ZS | 4 | 2.72 | 2.78 | 2.84 | 2.89 | 2.95 | 6 | 2.46 | 2.47 | 2.47 | 2.48 | 2.48
Tamworth | 799/1 | 33 | Quirindi ZS | Caroona Tee | 6 | 3.16 | 3.18 | 3.19 | 3.2 | 3.21 | 10 | 2.38 | 2.37 | 2.36 | 2.35 | 2.34
Tamworth | 799/2 | 33 | Caroona Tee | Caroona ZS | 4 | 1 | 1 | 1 | 1.01 | 1.01 | 6 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67
Tamworth | 799/3 | 33 | Caroona Tee | Spring Ridge ZS | 3 | 0.8 | 0.82 | 0.84 | 0.85 | 0.87 | 5 | 0.57 | 0.57 | 0.56 | 0.56 | 0.55
Tamworth | 799/4 | 33 | Spring Ridge ZS | Colly Blue ZS | 3 | 1.13 | 1.13 | 1.12 | 1.12 | 1.12 | 5 | 0.9 | 0.89 | 0.89 | 0.88 | 0.88
Wellington | 945/3 | 132 | TransGrid Line 945 Wellington 132kV Tee | Wellington 132kV ZS | 124 | 10.21 | 10.2 | 10.22 | 10.2 | 10.19 | 139 | 8.86 | 8.92 | 8.98 | 9.04 | 9.11
Wellington | 947/1 | 132 | TransGrid Line 947 Burrendong Tee | Burrendong Hydro | 36 | 6.63 | 6.63 | 6.64 | 6.63 | 6.63 | 64 | 9.05 | 9.13 | 9.21 | 9.36 | 9.43
Wellington | 94F | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 103.25 | 103.2 | 103.37 | 103.36 | 103.46 | 194 | 86.83 | 87.34 | 87.65 | 88 | 88.35
Wellington | 94J | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 95.69 | 95.65 | 95.8 | 95.79 | 95.89 | 194 | 81.46 | 81.94 | 82.23 | 82.55 | 82.88
Wellington | 805 | 66 | Wellington 132kV ZS | Mumbil ZS | 11 | 1.42 | 1.43 | 1.44 | 1.45 | 1.46 | 19 | 1.13 | 1.14 | 1.14 | 1.15 | 1.16
Wellington | 813:WGN | 66 | Wellington 132kV ZS | Geurie Tee | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Albury | 997/1 | 132 | Union Rd ZS | Corowa ZS | 128 | 51.57 | 51.67 | 51.72 | 51.81 | 51.88 | 143 | 56.05 | 55.88 | 55.75 | 55.71 | 55.5
Albury | 997/2 | 132 | Corowa ZS | Mulwala ZS | 128 | 63.66 | 63.74 | 63.81 | 63.92 | 63.98 | 143 | 65.86 | 65.77 | 65.71 | 65.74 | 65.58
Albury | 99E | 132 | Union Rd ZS | Jelbart ZS | 148 | 19.77 | 20.22 | 20.62 | 20.98 | 21.39 | 164 | 17.05 | 17.07 | 17.1 | 17.13 | 17.15
Albury | 99G | 132 | Union Rd ZS | Jelbart ZS | 148 | 19.77 | 20.22 | 20.62 | 20.98 | 21.39 | 164 | 17.05 | 17.07 | 17.1 | 17.13 | 17.15
Bega | 84G | 66 | Bega 132/66kV STS | Eden South ZS | 61 | 6.66 | 6.66 | 6.68 | 6.71 | 6.74 | 68 | 7.96 | 7.97 | 7.97 | 7.99 | 8
Bega | 84H | 66 | Eden South ZS | Edrom ZS | 38 | 2.27 | 2.23 | 2.19 | 2.17 | 2.14 | 43 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15
Bega | 84M | 66 | Bega 132/66kV STS | Maher St ZS | 61 | 8.61 | 8.61 | 8.58 | 8.59 | 8.57 | 68 | 10.74 | 10.77 | 10.81 | 10.85 | 10.87
Bega | 89A | 66 | Bega 132/66 | Pambula ZS | 38 | 10.35 | 10.37 | 10.41 | 10.44 | 10.48 | 43 | 14.82 | 14.85 | 14.88 | 14.91 | 14.95
Bega | 84P | 66 | Bega 132/66kV STS | Maher St ZS | 38 | 8.61 | 8.61 | 8.58 | 8.59 | 8.57 | 43 | 10.74 | 10.77 | 10.81 | 10.85 | 10.87
Bega | 89F | 66 | Pambula ZS | Eden South ZS | 30 | 2.58 | 2.59 | 2.59 | 2.61 | 2.61 | 36 | 2.95 | 2.95 | 2.95 | 2.96 | 2.96
Bega | 84R/1 | 66 | Maher St ZS | Quira ZS | 6 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0
Bega | 7802/1 | 33 | Maher St ZS | Brogo ZS | 12 | 3.86 | 3.83 | 3.8 | 3.77 | 3.76 | 24 | 5.57 | 5.56 | 5.56 | 5.55 | 5.54
Bega | 7802/2 | 33 | Brogo ZS | Cobargo ZS | 10 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 19 | 4.86 | 4.92 | 4.98 | 5.04 | 5.1
Bega | 7814 | 33 | Cobargo ZS | Bermagui ZS | 5 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 9 | 3.3 | 3.36 | 3.41 | 3.46 | 3.51
Buronga | 87G | 66 | Dareton ZS | Ellerslie ZS | 67 | 3.22 | 3.28 | 3.33 | 3.35 | 3.4 | 78 | 1.54 | 1.55 | 1.56 | 1.58 | 1.59
Buronga | 87H/1 | 66 | Ellerslie ZS | Ginkgo Snapper Tee | 45 | 0.4 | 0.42 | 0.43 | 0.41 | 0.42 | 56 | 0.08 | 0.07 | 0.07 | 0.08 | 0.08
Buronga | 87H/2 | 66 | Ginkgo Snapper Tee | Ginkgo ZS | 20 | 0.48 | 0.5 | 0.51 | 0.49 | 0.51 | 39 | 0.08 | 0.07 | 0.08 | 0.08 | 0.08
Buronga | 87H/3 | 66 | Ginkgo Snapper Tee | Snapper ZS | 12 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 19 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Buronga | 83U | 66 | Powercor Mildura ZS (NSW Border) | Buronga ZS | 22 | 27.34 | 27.64 | 28.18 | 28.42 | 28.58 | 43 | 16.11 | 16.18 | 16.29 | 16.33 | 16.33
Buronga | 83W | 66 | Buronga ZS | Dareton ZS | 22 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0
Buronga | Merbein - Dareton Line | 66 | Powercor Mildura ZS (NSW Border) | Dareton ZS | 49 | 9.01 | 8.99 | 9 | 8.99 | 9.07 | 61 | 6.86 | 6.9 | 7.03 | 7.17 | 7.2
Coleambally | CLY1526/1 | 33 | Coleambally 132/33kV STS | Coleambally Tee | 10 | 2.27 | 2.29 | 2.31 | 2.33 | 2.35 | 19 | 1.87 | 1.9 | 1.92 | 1.95 | 1.97
Coleambally | CLY1526/2 | 33 | Coleambally Tee | Coleambally ZS | 10 | 2.07 | 2.09 | 2.1 | 2.12 | 2.14 | 19 | 1.7 | 1.73 | 1.75 | 1.77 | 1.79
Coleambally | CLY1526/3 | 33 | Coleambally Tee | Egansford ZS | 8 | 1.25 | 1.3 | 1.36 | 1.41 | 1.46 | 13 | 1.18 | 1.28 | 1.36 | 1.43 | 1.49
Coleambally | CLY1530/1 | 33 | Coleambally 132/33kV STS | Ringwood Rd ZS | 8 | 7.05 | 7.17 | 7.28 | 7.36 | 7.45 | 13 | 4.62 | 4.67 | 4.73 | 4.78 | 4.82
Coleambally | CLY1530/2 | 33 | Ringwood Rd ZS | Darlington Point ZS | 8 | 4.36 | 4.43 | 4.49 | 4.54 | 4.59 | 13 | 2.83 | 2.85 | 2.88 | 2.9 | 2.92
Cooma | 974 | 132 | TransGrid Cooma 132/66kV STS | Bega 132/66kV STS | 128 | 14.8 | 14.78 | 14.71 | 14.68 | 14.63 | 143 | 19.02 | 18.92 | 18.86 | 18.71 | 18.59
Cooma | 97R/1 | 132 | TransGrid Cooma 132/66kV STS | Steeple Flat 132/66kV STS | 163 | 88.12 | 88.14 | 88.19 | 88.01 | 88.33 | 176 | 78.11 | 77.28 | 77.27 | 77.77 | 78
Cooma | 82D | 66 | TransGrid Cooma 132/66kV STS | Jindabyne East ZS | 20 | 4.07 | 4.08 | 4.11 | 4.13 | 4.15 | 39 | 12.37 | 12.44 | 12.51 | 12.58 | 12.64
Cooma | 84J | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 70 | 4.44 | 4.43 | 4.43 | 4.44 | 4.43 | 78 | 7.33 | 7.4 | 7.47 | 7.53 | 7.59
Cooma | 84L | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 64 | 4.44 | 4.43 | 4.43 | 4.44 | 4.43 | 71 | 7.33 | 7.4 | 7.47 | 7.53 | 7.59
Cooma | 82J/1 | 66 | Snowy Adit 132/66/11kV ZS | Snowy Lookout Sw Stn | 12 | 2.8 | 2.8 | 2.81 | 2.81 | 2.82 | 20 | 8.28 | 8.34 | 8.39 | 8.42 | 8.48
Cooma | 82J/2 | 66 | Snowy Lookout Sw Stn | Jindabyne ZS | 12 | 2.8 | 2.8 | 2.81 | 2.81 | 2.82 | 19 | 8.28 | 8.34 | 8.39 | 8.42 | 8.48
Cooma | 82R | 66 | Jindabyne East ZS | Jindabyne ZS | 20 | 2.03 | 2.05 | 2.08 | 2.1 | 2.13 | 39 | 7 | 7.05 | 7.1 | 7.16 | 7.2
Cooma | 888/1 | 66 | TransGrid Cooma 132/66kV STS | Rhine Falls Sw Stn | 16 | 1.36 | 1.37 | 1.38 | 1.39 | 1.39 | 25 | 2.01 | 2.01 | 2.01 | 2.02 | 2.02
Cooma | 888/3 | 66 | Rhine Falls Sw Stn | Adaminaby ZS | 16 | 0.99 | 1 | 1.01 | 1.02 | 1.02 | 25 | 1.57 | 1.57 | 1.58 | 1.58 | 1.58
Cooma | 888/4 | 66 | Rhine Falls Sw Stn | Eucumbene Tee | 15 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 25 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
Cooma | 888/6 | 66 | Eucumbene Tee | Eucumbene ZS | 15 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 25 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21
Cooma | 888/7 | 66 | Eucumbene Tee | Snowy Adit 132/66/11kV ZS | 20 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Cooma | 849/1 | 33 | Adaminaby ZS | Providence Portal ZS | 7 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 12 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
Cowra | 865 | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 9.86 | 9.86 | 9.88 | 9.85 | 9.86 | 25 | 8.36 | 8.38 | 8.41 | 8.44 | 8.47
Cowra | 863:CWD | 66 | TransGrid Cowra 132/66kV STS | Canowindra ZS | 9 | 6.04 | 6.03 | 6.02 | 6.02 | 6.03 | 15 | 4.72 | 4.72 | 4.72 | 4.72 | 4.72
Cowra | 866:COW | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 9.86 | 9.86 | 9.88 | 9.85 | 9.86 | 25 | 8.36 | 8.38 | 8.41 | 8.44 | 8.47
Cowra | 891/1 | 66 | TransGrid Cowra 132/66kV STS | Wyangala Dam Tee | 20 | 30.81 | 30.81 | 30.81 | 30.82 | 30.82 | 24 | 31.08 | 31.09 | 31.09 | 31.09 | 31.09
Cowra | 891/2 | 66 | Wyangala Dam Tee | Wyangala Dam | 19 | 23.88 | 23.88 | 23.88 | 23.88 | 23.88 | 33 | 23.88 | 23.88 | 23.88 | 23.88 | 23.88
Cowra | 891/5 | 66 | Monteagle Tee | Monteagle ZS | 13 | 0.85 | 0.87 | 0.88 | 0.9 | 0.91 | 22 | 0.89 | 0.9 | 0.9 | 0.9 | 0.9
Cowra | 891/6 | 66 | Monteagle Tee | Young ZS | 19 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0
Cowra | 891/7 | 66 | Bendick Murrell Tee | Bendick Murrell ZS | 19 | 1.64 | 1.64 | 1.64 | 1.63 | 1.63 | 33 | 1.35 | 1.37 | 1.38 | 1.39 | 1.41
Cowra | 891:BMU/1 | 66 | Wyangala Dam Tee | Bendick Murrell Tee | 19 | 2.37 | 2.38 | 2.39 | 2.4 | 2.41 | 33 | 2.12 | 2.14 | 2.15 | 2.17 | 2.18
Cowra | 891:BMU/2 | 66 | Bendick Murrell Tee | Monteagle Tee | 19 | 0.85 | 0.87 | 0.88 | 0.9 | 0.91 | 33 | 0.89 | 0.9 | 0.9 | 0.9 | 0.9
Cowra | 893/1 | 66 | TransGrid Cowra 132/66kV STS | Grenfell Tee | 12 | 3.69 | 3.62 | 3.55 | 3.49 | 3.43 | 18 | 3.07 | 2.95 | 2.84 | 2.74 | 2.66
Cowra | 893/4 | 66 | Grenfell Tee | Payten's Bridge ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Cowra | 893/6 | 66 | Grenfell Tee | Grenfell ZS | 12 | 3.69 | 3.62 | 3.55 | 3.49 | 3.43 | 18 | 3.07 | 2.95 | 2.84 | 2.74 | 2.66
Darlington Point | 99N | 132 | TransGrid Darlington Point 330/132kV STS | Hillston ZS | 128 | 15.48 | 15.95 | 16.39 | 16.78 | 17.17 | 143 | 14.07 | 14.38 | 14.76 | 15.08 | 15.41
Darlington Point | 99R | 132 | TransGrid Darlington Point 330/132kV STS | Hay 132 ZS | 128 | 12.27 | 12.48 | 12.64 | 12.8 | 12.95 | 143 | 17.65 | 17.77 | 17.87 | 17.97 | 18.06
Darlington Point | HAT 22 | 33 | Hay 132 ZS | Hay ZS | 8 | 4.76 | 4.79 | 4.81 | 4.84 | 4.86 | 14 | 6.64 | 6.61 | 6.61 | 6.6 | 6.58
Darlington Point | HAT 32 | 33 | Hay 132 ZS | Hay ZS | 8 | 1.19 | 1.2 | 1.2 | 1.21 | 1.21 | 14 | 1.66 | 1.65 | 1.65 | 1.65 | 1.64
Darlington Point | HAT 42 | 33 | Hay 132 ZS | Carrathool ZS | 7 | 8.35 | 8.52 | 8.65 | 8.78 | 8.9 | 12 | 9.27 | 9.41 | 9.51 | 9.61 | 9.71
Darlington Point | HIL1117 | 33 | Hillston ZS | Ivanhoe ZS | 8 | 5.51 | 5.62 | 5.74 | 5.84 | 5.95 | 14 | 3.65 | 3.66 | 3.67 | 3.68 | 3.69
Deniliquin | 844 | 66 | TransGrid Deniliquin 132/66kV STS | Barham ZS | 11 | 5.88 | 5.97 | 6.02 | 6.1 | 6.18 | 19 | 4.74 | 4.77 | 4.8 | 4.84 | 4.86
Deniliquin | 845 | 66 | TransGrid Deniliquin 132/66kV STS | Deniliquin ZS | 38 | 22.36 | 22.69 | 22.89 | 23.2 | 23.5 | 43 | 17.99 | 18.13 | 18.24 | 18.37 | 18.47
Deniliquin | 822/1 | 66 | TransGrid Deniliquin 132/66kV STS | Murgha ZS | 11 | 7.69 | 7.8 | 7.87 | 7.98 | 8.08 | 19 | 6.75 | 6.81 | 6.85 | 6.9 | 6.94
Deniliquin | 822/2 | 66 | Murgha ZS | Moulamein ZS | 11 | 6.43 | 6.53 | 6.58 | 6.67 | 6.76 | 19 | 5.76 | 5.81 | 5.84 | 5.89 | 5.92
Deniliquin | 84Y | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 66 | 8.64 | 8.77 | 8.85 | 8.97 | 9.08 | 66 | 4.55 | 4.59 | 4.62 | 4.65 | 4.67
Deniliquin | MM61 | 66 | Moulamein ZS | Koraleigh ZS | 15 | 4.27 | 4.33 | 4.37 | 4.43 | 4.49 | 25 | 2.72 | 2.74 | 2.75 | 2.77 | 2.79
Deniliquin | No.6 Moama | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 34 | 6.03 | 6.12 | 6.17 | 6.26 | 6.34 | 39 | 3.23 | 3.26 | 3.28 | 3.3 | 3.32
Finley | 9R4 | 132 | TransGrid Finley 132/66kV STS | Mulwala ZS | 140 | 73.59 | 73.7 | 73.82 | 73.98 | 74.1 | 157 | 74.31 | 74.3 | 74.32 | 74.43 | 74.33
Finley | 84A | 66 | TransGrid Finley 132/66kV STS | Jerilderie ZS | 15 | 3.93 | 3.96 | 3.99 | 4.02 | 4.03 | 25 | 3.63 | 3.69 | 3.75 | 3.8 | 3.85
Finley | 84B | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 4.76 | 4.77 | 4.76 | 4.75 | 4.76 | 70 | 3.52 | 3.55 | 3.57 | 3.59 | 3.61
Finley | 84C | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 8.84 | 8.86 | 8.84 | 8.83 | 8.84 | 70 | 6.54 | 6.59 | 6.63 | 6.67 | 6.7
Goulburn | 972 | 132 | TransGrid Marulan 330/132kV STS | Goulburn 132/66/33kV STS | 180 | 60.93 | 60.16 | 60.21 | 59.49 | 58.68 | 202 | 54.85 | 54.74 | 54.18 | 53.8 | 52.95
Goulburn | 9UR | 132 | TransGrid Marulan 330/132kV STS | Taralga Wind Farm | 140 | 104 | 104.08 | 104.86 | 104.84 | 104.81 | 157 | 110.07 | 110.48 | 110.46 | 110.7 | 110.28
Goulburn | 843 | 66 | Clinton St ZS | Goulburn North ZS | 46 | 4.4 | 4.48 | 4.58 | 4.68 | 4.76 | 52 | 5.65 | 5.69 | 5.73 | 5.76 | 5.79
Goulburn | 82K/2 | 66 | Woodlawn ZS | Bungendore ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Goulburn | 840:GOU | 66 | Goulburn 132/66/33kV STS | Goulburn North ZS | 61 | 8.43 | 8.48 | 8.55 | 8.61 | 8.65 | 68 | 10.74 | 10.9 | 11.05 | 11.19 | 11.32
Goulburn | 841:GBN | 66 | Goulburn North ZS | Crookwell ZS | 9 | 3.75 | 3.76 | 3.77 | 3.79 | 3.8 | 13 | 6.65 | 6.83 | 6.99 | 7.13 | 7.28
Goulburn | 850:GOU | 66 | Goulburn 132/66/33kV STS | Woodlawn ZS | 28 | 5.59 | 5.28 | 5.1 | 5.02 | 5.04 | 34 | 5.22 | 4.83 | 4.52 | 4.27 | 4.12
Goulburn | 86M/1 | 66 | Goulburn 132/66/33kV STS | Marulan North Tee | 25 | 12.67 | 12.85 | 12.99 | 13.15 | 13.3 | 29 | 13.45 | 13.59 | 13.73 | 13.85 | 13.97
Goulburn | 86M/2 | 66 | Marulan North Tee | Marulan South ZS | 25 | 7.39 | 7.5 | 7.58 | 7.69 | 7.78 | 29 | 7.51 | 7.54 | 7.58 | 7.61 | 7.64
Goulburn | 86L | 66 | Marulan North Tee | Marulan North ZS | 12 | 6.72 | 6.81 | 6.89 | 6.95 | 7.03 | 19 | 7.51 | 7.63 | 7.74 | 7.85 | 7.95
Goulburn | 870:GOU | 66 | Goulburn 132/66/33kV STS | Clinton St ZS | 34 | 19.6 | 19.86 | 20.18 | 20.48 | 20.72 | 41 | 25.07 | 25.34 | 25.58 | 25.82 | 26.03
Goulburn | GOU12 | 33 | Goulburn 132/66/33kV STS | Brisbane Grove ZS | 7 | 2.17 | 2.18 | 2.18 | 2.19 | 2.2 | 12 | 2.64 | 2.65 | 2.66 | 2.67 | 2.68
Griffith | 79C/1 | 33 | TransGrid Griffith 132/33kV STS | Widgelli / Willbriggie Tee | 10 | 6.27 | 6.29 | 6.32 | 6.33 | 6.35 | 19 | 5.8 | 5.85 | 5.88 | 5.92 | 5.95
Griffith | 79C/2 | 33 | Widgelli / Willbriggie Tee | Widgelli ZS | 10 | 1.22 | 1.22 | 1.23 | 1.23 | 1.23 | 19 | 1 | 1.01 | 1.01 | 1.02 | 1.02
Griffith | 79C/3 | 33 | Widgelli / Willbriggie Tee | Willbriggie Tee | 10 | 5.05 | 5.07 | 5.1 | 5.1 | 5.12 | 19 | 4.8 | 4.84 | 4.87 | 4.9 | 4.93
Griffith | 79C/4 | 33 | Willbriggie Tee | Willbriggie ZS | 10 | 4.49 | 4.51 | 4.53 | 4.54 | 4.55 | 19 | 4.24 | 4.27 | 4.3 | 4.33 | 4.35
Griffith | 79C/5 | 33 | Willbriggie Tee | 79C / 79P Tee | 10 | 0.56 | 0.56 | 0.57 | 0.57 | 0.57 | 19 | 0.5 | 0.5 | 0.51 | 0.51 | 0.51
Griffith | 79F | 33 | TransGrid Griffith 132/33kV STS | Yenda ZS | 22 | 12.26 | 12.3 | 12.36 | 12.38 | 12.42 | 27 | 8.54 | 8.61 | 8.67 | 8.72 | 8.77
Griffith | 79G | 33 | Beelbangera ZS | Griffith ZS | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0
Griffith | 79J | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0
Griffith | 79L | 33 | TransGrid Griffith 132/33kV STS | Beelbangera ZS | 22 | 13.67 | 13.71 | 13.78 | 13.8 | 13.84 | 27 | 8.1 | 8.17 | 8.23 | 8.27 | 8.32
Griffith | 79M | 33 | TransGrid Griffith 132/33kV STS | Hanwood ZS | 22 | 14.55 | 14.65 | 14.71 | 14.79 | 14.87 | 27 | 12.25 | 12.33 | 12.41 | 12.49 | 12.56
Griffith | 79P | 33 | TransGrid Griffith 132/33kV STS | Warrawidgee Tee | 22 | 9.64 | 9.67 | 9.72 | 9.74 | 9.77 | 27 | 7.6 | 7.67 | 7.72 | 7.76 | 7.81
Griffith | 79W/1 | 33 | Warrawidgee Tee | Warrawidgee ZS | 6 | 2.25 | 2.25 | 2.26 | 2.27 | 2.28 | 9 | 1.75 | 1.76 | 1.77 | 1.78 | 1.79
Griffith | 79W/2 | 33 | Warrawidgee Tee | Nericon Tee | 21 | 6.74 | 6.76 | 6.79 | 6.81 | 6.83 | 27 | 5.36 | 5.41 | 5.44 | 5.47 | 5.5
Griffith | 79W/3 | 33 | Nericon Tee | Nericon ZS | 20 | 3 | 3.01 | 3.02 | 3.02 | 3.03 | 23 | 1.87 | 1.89 | 1.9 | 1.91 | 1.92
Griffith | 79R | 33 | TransGrid Griffith 132/33kV STS | Tharbogang ZS | 31 | 14.41 | 14.42 | 14.49 | 14.52 | 14.56 | 34 | 9.94 | 10.03 | 10.11 | 10.19 | 10.25
Griffith | 79U | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 53 | 26.84 | 26.83 | 26.84 | 26.86 | 26.83 | 58 | 21.1 | 21.26 | 21.41 | 21.53 | 21.64
Harden - Murrumburrah | 836 | 66 | TransGrid Murrumburrah 132/66kV STS | Cootamundra ZS | 20 | 11.77 | 11.79 | 11.84 | 11.85 | 11.86 | 24 | 12.18 | 12.55 | 12.87 | 13.19 | 13.52
Harden - Murrumburrah | 837 | 66 | TransGrid Murrumburrah 132/66kV STS | Jugiong ZS | 12 | 1.71 | 1.72 | 1.73 | 1.75 | 1.76 | 18 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34
Harden - Murrumburrah | 847 | 66 | TransGrid Murrumburrah 132/66kV STS | Boorowa ZS | 10 | 5.85 | 5.88 | 5.9 | 5.94 | 5.96 | 16 | 6.22 | 6.23 | 6.24 | 6.25 | 6.27
Harden - Murrumburrah | 823/3 | 66 | Bogalara Sw Stn | Marilba ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 830/1:PCR | 66 | Bogalara Sw Stn | Parsons Creek ZS | 11 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 838/3 | 66 | Jugiong ZS | Bogalara Sw Stn | 12 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 83A | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 4.58 | 4.64 | 4.71 | 4.78 | 4.85 | 25 | 4.77 | 4.79 | 4.8 | 4.82 | 4.84
Harden - Murrumburrah | 83D | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 890:YOU | 66 | TransGrid Murrumburrah 132/66kV STS | Young ZS | 24 | 17.38 | 17.45 | 17.47 | 17.5 | 17.55 | 28 | 17.57 | 17.76 | 17.93 | 18.08 | 18.24
Moruya North | 98H | 132 | Endeavour Energy Evans Lane Sw Stn | Moruya North 132/33kV STS | 180 | 19.95 | 20.18 | 20.45 | 20.66 | 20.91 | 202 | 25.43 | 25.48 | 25.54 | 25.6 | 25.67
Moruya North | 98M | 132 | Endeavour Energy Evans Lane Sw Stn | Batemans Bay ZS | 50 | 17.65 | 17.85 | 18.09 | 18.27 | 18.5 | 62 | 22.5 | 22.54 | 22.59 | 22.65 | 22.7
Moruya North | 98T | 132 | Batemans Bay ZS | Moruya North 132/33kV STS | 61 | 3.84 | 3.88 | 3.93 | 3.97 | 4.02 | 70 | 4.89 | 4.9 | 4.91 | 4.92 | 4.94
Moruya North | 7703 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 30 | 6.33 | 6.33 | 6.33 | 6.33 | 6.34 | 34 | 8.51 | 8.53 | 8.55 | 8.58 | 8.6
Moruya North | 7704 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 26 | 8.1 | 8.1 | 8.1 | 8.1 | 8.11 | 30 | 10.89 | 10.91 | 10.94 | 10.97 | 11
Moruya North | 7706 | 33 | Moruya North 132/33kV STS | Mossy Point ZS | 25 | 6.51 | 6.51 | 6.5 | 6.49 | 6.48 | 28 | 9.25 | 9.27 | 9.29 | 9.31 | 9.33
Moruya North | 7712 | 33 | Bodalla Tee | Bodalla ZS | 10 | 1.19 | 1.2 | 1.21 | 1.22 | 1.23 | 19 | 1.41 | 1.41 | 1.41 | 1.42 | 1.42
Moruya North | 7713 | 33 | Bodalla Tee | Narooma ZS | 21 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0
Moruya North | 7817 | 33 | Narooma Tee | Cobargo ZS | 10 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/1 | 33 | Moruya Town ZS | Tuross Tee | 17 | 3.21 | 3.21 | 3.22 | 3.22 | 3.22 | 19 | 4.78 | 4.8 | 4.83 | 4.85 | 4.87
Moruya North | 7711/2 | 33 | Tuross Tee | Tuross ZS | 7 | 2.35 | 2.35 | 2.34 | 2.34 | 2.34 | 12 | 3.64 | 3.66 | 3.68 | 3.71 | 3.73
Moruya North | 7711/3 | 33 | Tuross Tee | Bodalla Tee | 21 | 1.23 | 1.24 | 1.24 | 1.25 | 1.26 | 27 | 1.45 | 1.45 | 1.46 | 1.46 | 1.46
Moruya North | 7715/1 | 33 | Moruya Town ZS | Narooma Tee | 30 | 6.33 | 6.39 | 6.44 | 6.49 | 6.55 | 34 | 8.37 | 8.36 | 8.37 | 8.37 | 8.37
Moruya North | 7715/2 | 33 | Narooma Tee | Narooma ZS | 10 | 6.04 | 6.1 | 6.15 | 6.19 | 6.25 | 19 | 7.99 | 7.98 | 7.98 | 7.99 | 7.99
Morven | 996/1 | 132 | TransGrid 132kV Line 996 Tee | Morven 132/66kV STS | 45 | 7.46 | 7.59 | 7.69 | 7.81 | 7.92 | 86 | 7.28 | 7.33 | 7.37 | 7.4 | 7.44
Morven | 83M/3 | 66 | Morven 132/66kV STS | Culcairn ZS | 15 | 3.58 | 3.55 | 3.53 | 3.5 | 3.47 | 25 | 4.41 | 4.45 | 4.49 | 4.52 | 4.55
Morven | 83M/4 | 66 | Morven 132/66kV STS | Holbrook ZS | 15 | 3.3 | 3.32 | 3.33 | 3.34 | 3.35 | 25 | 3.36 | 3.37 | 3.38 | 3.38 | 3.39
Munyang | 56 | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 1.98 | 1.99 | 2.01 | 2.02 | 2.02 | 23 | 16.88 | 17.03 | 17.14 | 17.22 | 17.32
Munyang | 57A | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 23 | 5.72 | 5.77 | 5.81 | 5.84 | 5.88
Munyang | 57B | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 23 | 3.81 | 3.85 | 3.87 | 3.9 | 3.92
Munyang | No.1 Perisher | 33 | TransGrid Munyang 132/33kV STS | Smiggin Sw Stn | 38 | 1.98 | 1.99 | 2.01 | 2.02 | 2.02 | 41 | 16.88 | 17.03 | 17.14 | 17.22 | 17.32
Munyang | No.2 Perisher/1 | 33 | TransGrid Munyang 132/33kV STS | Blue Cow Tee | 38 | 1.2 | 1.21 | 1.21 | 1.21 | 1.21 | 49 | 12.4 | 12.46 | 12.48 | 12.51 | 12.54
Munyang | No.2 Perisher/2 | 33 | Blue Cow Tee | Smiggin Sw Stn | 38 | 1 | 1 | 1 | 1 | 1 | 49 | 9.53 | 9.62 | 9.68 | 9.74 | 9.8
Munyang | 60/2 | 33 | Bullocks Portal ZS | Bullocks Flat ZS | 19 | 1.73 | 1.74 | 1.75 | 1.76 | 1.77 | 23 | 16.88 | 17.03 | 17.14 | 17.22 | 17.32
Munyang | 58 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 14 | 14.14 | 14.14 | 14.14 | 14.14 | 14.14
Munyang | 59 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 1.4 | 1.41 | 1.42 | 1.43 | 1.43 | 14 | 7.14 | 7.19 | 7.23 | 7.24 | 7.28
Munyang | Bullocks Portal Line | 33 | Perisher ZS | Bullocks Portal ZS | 20 | 1.98 | 1.99 | 2.01 | 2.02 | 2.02 | 23 | 16.88 | 17.03 | 17.14 | 17.22 | 17.32
Queanbeyan | 97Y | 132 | TransGrid Williamsdale 330/132kV STS | Googong Town ZS | 91 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 975 | 132 | TransGrid Queanbeyan 132/66kV STS | South Jerrabomberra ZS | 140 | 13.87 | 19.49 | 25.09 | 30.67 | 36.23 | 157 | 18.22 | 23.88 | 29.56 | 35.2 | 40.81
Queanbeyan | 9MU | 132 | South Jerrabomberra ZS | Googong Town ZS | 91 | 9.84 | 10.09 | 10.3 | 10.49 | 10.66 | 112 | 14.2 | 14.49 | 14.78 | 15.04 | 15.26
Queanbeyan | 82A | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 12.62 | 12.62 | 12.62 | 12.65 | 12.6 | 37 | 17.2 | 17.34 | 17.46 | 17.57 | 17.67
Queanbeyan | 82B | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 9.47 | 9.47 | 9.46 | 9.49 | 9.45 | 37 | 12.9 | 13.01 | 13.09 | 13.17 | 13.26
Queanbeyan | 82F | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 49 | 10.64 | 10.53 | 10.43 | 10.34 | 10.25 | 49 | 19.09 | 19.36 | 19.57 | 19.74 | 19.89
Queanbeyan | 82G | 66 | TransGrid Queanbeyan 132/66kV STS | Captains Flat ZS | 12 | 4.93 | 5.1 | 5.23 | 5.35 | 5.47 | 19 | 8.31 | 8.55 | 8.79 | 8.99 | 9.2
Queanbeyan | 82K | 66 | TransGrid Queanbeyan 132/66kV STS | Sutton / Bungendore Tee | 28 | 11.68 | 11.8 | 11.9 | 12.02 | 12.15 | 34 | 15.8 | 15.94 | 16.07 | 16.19 | 16.3
Queanbeyan | 82K/1 | 66 | Sutton / Bungendore Tee | Bungendore ZS | 28 | 7.99 | 8.11 | 8.22 | 8.34 | 8.46 | 34 | 10.67 | 10.77 | 10.86 | 10.94 | 11.03
Queanbeyan | 82K/3 | 66 | Sutton / Bungendore Tee | Sutton ZS | 28 | 3.69 | 3.69 | 3.69 | 3.68 | 3.69 | 34 | 5.14 | 5.17 | 5.22 | 5.25 | 5.28
Queanbeyan | 82M | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 830:QSH | 66 | Queanbeyan South ZS | Googong Dam ZS | 15 | 1.12 | 1.11 | 1.11 | 1.11 | 1.11 | 25 | 1.76 | 1.77 | 1.79 | 1.81 | 1.83
Steeple Flat | 97C | 132 | Steeple Flat 132/66kV STS | Boco Rock Wind Farm | 184 | 115.04 | 115.07 | 115.08 | 114.88 | 115.17 | 207 | 109.94 | 109.05 | 109.05 | 109.41 | 109.52
Steeple Flat | 97R/2 | 132 | Steeple Flat 132/66kV STS | Bega 132/66kV STS | 163 | 15.2 | 15.18 | 15.11 | 15.07 | 15.02 | 176 | 19.76 | 19.65 | 19.59 | 19.43 | 19.3
Steeple Flat | 84R/5 | 66 | Steeple Flat 132/66kV STS | Brown Mountain Hydro | 70 | 4.39 | 4.39 | 4.4 | 4.4 | 4.4 | 78 | 4.73 | 4.71 | 4.71 | 4.72 | 4.71
Steeple Flat | 810/4 | 66 | Steeple Flat 132/66kV STS | Bombala ZS | 21 | 4.09 | 4.11 | 4.11 | 4.12 | 4.13 | 25 | 4.83 | 4.82 | 4.82 | 4.83 | 4.84
Steeple Flat | 84R/3 | 66 | Brown Mountain Hydro | Quira ZS | 70 | 1.42 | 1.44 | 1.46 | 1.48 | 1.5 | 78 | 1.35 | 1.36 | 1.35 | 1.35 | 1.35
Temora | 901 | 132 | Temora 132/66 STS | Wyalong Switching Station | 108 | 88.77 | 88.77 | 88.77 | 88.77 | 88.77 | 135 | 88.77 | 88.77 | 88.77 | 88.77 | 88.77
Temora | 9JW | 132 | Wyalong Switching Station | West Wyalong Switching Station | 108 | 75.43 | 75.43 | 75.43 | 75.43 | 75.43 | 135 | 75.43 | 75.43 | 75.43 | 75.43 | 75.43
Temora | 9JX | 132 | West Wyalong Switching Station | Lake Cowal | 108 | 35.75 | 35.7 | 35.68 | 35.66 | 35.7 | 135 | 37.36 | 37.54 | 37.62 | 37.69 | 37.66
Temora | 4 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Temora | 5 | 66 | Temora 132/66 STS | Ariah Park Tee | 21 | 16.61 | 17.34 | 17.84 | 18.32 | 18.74 | 25 | 14.15 | 14.19 | 14.22 | 14.28 | 14.41
Temora | 6 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 7.68 | 7.67 | 7.67 | 7.67 | 7.68 | 25 | 6.85 | 6.91 | 6.95 | 6.99 | 7.03
Temora | 20-60 | 66 | Ariah Park Tee | West Wyalong ZS | 21 | 13.84 | 14.45 | 14.87 | 15.27 | 15.62 | 25 | 11.79 | 11.83 | 11.85 | 11.9 | 12.01
Temora | 60-70 | 66 | West Wyalong ZS | Anona ZS | 7 | 1.34 | 1.36 | 1.37 | 1.37 | 1.38 | 12 | 1.18 | 1.19 | 1.19 | 1.2 | 1.2
Temora | 80-140/1 | 66 | Ariah Park Tee | Ariah Park ZS | 15 | 2.77 | 2.89 | 2.97 | 3.05 | 3.12 | 25 | 2.36 | 2.37 | 2.37 | 2.38 | 2.4
Temora | 80-140/2 | 66 | Ariah Park ZS | Ardlethan ZS | 11 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 19 | 0.7 | 0.71 | 0.71 | 0.72 | 0.72
Temora | 835/J | 66 | Junee Reefs ZS | Junee ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Temora | 835/T | 66 | Temora 132/66 STS | Junee Reefs ZS | 12 | 0.23 | 0.24 | 0.24 | 0.25 | 0.25 | 18 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
Tumut | 827 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 12.12 | 12.09 | 12.04 | 12.04 | 12.02 | 34 | 14.44 | 14.47 | 14.51 | 14.54 | 14.57
Tumut | 828 | 66 | TransGrid Tumut 132/66kV STS | Gundagai South ZS | 11 | 7.11 | 7.22 | 7.34 | 7.46 | 7.58 | 19 | 6.16 | 6.2 | 6.24 | 6.27 | 6.31
Tumut | 829 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0
Tumut | 831 | 66 | Gundagai South ZS | Nangus ZS | 11 | 1.17 | 1.18 | 1.19 | 1.2 | 1.21 | 19 | 0.67 | 0.68 | 0.69 | 0.7 | 0.7
Tumut | 848 | 66 | Adelong Tee | Adelong ZS | 12 | 1.35 | 1.36 | 1.38 | 1.39 | 1.4 | 19 | 1.26 | 1.25 | 1.25 | 1.24 | 1.23
Tumut | 830/2:GUN | 66 | Gundagai South ZS | Parsons Creek ZS | 11 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 19 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23
Tumut | 848/1 | 66 | Adelong Tee | Batlow ZS | 21 | 7.85 | 7.78 | 7.73 | 7.69 | 7.64 | 25 | 9.16 | 9.06 | 8.99 | 8.9 | 8.84
Tumut | 848/2 | 66 | Batlow ZS | Tumbarumba ZS | 22 | 6.8 | 6.75 | 6.71 | 6.68 | 6.65 | 26 | 7.89 | 7.81 | 7.75 | 7.68 | 7.64
Tumut | 848/3 | 66 | TransGrid Tumut 132/66kV STS | Adelong Tee | 21 | 8.93 | 8.87 | 8.83 | 8.79 | 8.76 | 25 | 10.17 | 10.06 | 9.98 | 9.88 | 9.82
Tumut | 850:TAL | 66 | TransGrid Tumut 132/66kV STS | Talbingo ZS | 18 | 15.14 | 15.14 | 15.14 | 15.14 | 15.14 | 22 | 15.14 | 15.14 | 15.14 | 15.14 | 15.14
Wagga (Copland St) | 83L | 66 | Hammond Ave ZS | Bomen ZS | 54 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Uranquinty ZS | 64 | 7.46 | 7.54 | 7.62 | 7.69 | 7.77 | 80 | 7.01 | 7.02 | 7.04 | 7.06 | 7.08
Wagga (Copland St) | 840/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bulgary ZS | 15 | 3.39 | 3.38 | 3.37 | 3.37 | 3.36 | 25 | 3.12 | 3.12 | 3.12 | 3.11 | 3.11
Wagga (Copland St) | 840/2 | 66 | Bulgary ZS | Lockhart ZS | 15 | 3.21 | 3.21 | 3.21 | 3.21 | 3.21 | 24 | 2.99 | 2.99 | 2.99 | 2.99 | 3
Wagga (Copland St) | 840/3 | 66 | Lockhart Tee | Kywong ZS | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M/1 | 66 | Uranquinty ZS | Henty ZS | 15 | 2.47 | 2.55 | 2.64 | 2.71 | 2.8 | 25 | 2.14 | 2.13 | 2.12 | 2.11 | 2.11
Wagga (Copland St) | 83M/2 | 66 | Henty ZS | Culcairn ZS | 15 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8W9 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Ashmont ZS | 34 | 27.43 | 27.71 | 27.97 | 28.27 | 28.54 | 39 | 26.18 | 26.43 | 26.64 | 26.88 | 27.03
Wagga (Copland St) | 8WF/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bourkelands Tee | 34 | 12.42 | 12.48 | 12.58 | 12.65 | 12.74 | 39 | 11 | 11.09 | 11.16 | 11.23 | 11.3
Wagga (Copland St) | 8WF/2 | 66 | Bourkelands Tee | Kooringal ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WF/3 | 66 | Bourkelands Tee | Bourkelands ZS | 42 | 12.42 | 12.48 | 12.58 | 12.65 | 12.74 | 46 | 11 | 11.09 | 11.16 | 11.23 | 11.3
Wagga (Copland St) | 8WM | 66 | Hammond Ave ZS | Morrow St ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WO | 66 | Ashmont ZS | Bourkelands ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WP | 66 | Morrow St ZS | Cartwrights Hill ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WR | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 9.16 | 9.16 | 9.17 | 9.15 | 9.16 | 60 | 7.87 | 7.89 | 7.93 | 7.96 | 7.98
Wagga (Copland St) | 8WT | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 8.63 | 8.63 | 8.64 | 8.62 | 8.63 | 60 | 7.41 | 7.43 | 7.47 | 7.51 | 7.52
Wagga (Copland St) | 8WG | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Kooringal ZS | 34 | 18.34 | 18.36 | 18.39 | 18.39 | 18.45 | 39 | 15.47 | 15.54 | 15.59 | 15.66 | 15.7
Wagga North | 99U | 132 | TransGrid Wagga North 132/66kV STS | Sebastopol Sw Stn | 128 | 77.62 | 77.62 | 77.62 | 77.62 | 77.62 | 143 | 79.36 | 79.36 | 79.36 | 79.36 | 79.36
Wagga North | 9J6 | 132 | Sebastopol Sw Stn | Temora 132/66 STS | 128 | 35.79 | 36.68 | 37.29 | 37.88 | 38.42 | 143 | 32.66 | 32.82 | 32.92 | 33.04 | 33.2
Wagga North | 9J5/1 | 132 | TransGrid Wagga North 132/66kV STS | Junee 132/66/11kV ZS | 140 | 45.55 | 46.68 | 47.46 | 48.21 | 48.9 | 157 | 43.29 | 43.5 | 43.63 | 43.79 | 44.01
Wagga North | 9J5/2 | 132 | Junee 132/66/11kV ZS | Temora 132/66 STS | 140 | 34.41 | 35.34 | 35.96 | 36.57 | 37.13 | 157 | 29.79 | 29.94 | 30.03 | 30.14 | 30.3
Wagga North | 30-90 | 66 | Junee ZS | Coolamon ZS | 6 | 5.4 | 5.5 | 5.56 | 5.62 | 5.69 | 9 | 4.62 | 4.65 | 4.68 | 4.7 | 4.73
Wagga North | 834:JUN | 66 | Junee ZS | Bethungra ZS | 11 | 1.08 | 1.09 | 1.09 | 1.09 | 1.09 | 19 | 1.02 | 1.02 | 1.02 | 1.02 | 1.01
Wagga North | 83C/1 | 66 | TransGrid Wagga North 132/66kV STS | Oura ZS | 24 | 4.26 | 4.25 | 4.25 | 4.25 | 4.24 | 28 | 3.48 | 3.51 | 3.53 | 3.56 | 3.58
Wagga North | 83C/2 | 66 | Oura ZS | Forest Hill ZS | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0
Wagga North | 83G | 66 | TransGrid Wagga North 132/66kV STS | Bomen ZS | 34 | 19.6 | 21.73 | 23.82 | 25.88 | 27.93 | 39 | 17.97 | 20.1 | 22.2 | 24.29 | 26.38
Wagga North | 83J | 66 | Bomen ZS | Cartwrights Hill ZS | 34 | 10.34 | 10.55 | 10.77 | 10.98 | 11.14 | 39 | 8.93 | 9.06 | 9.18 | 9.29 | 9.4
Wagga North | 850:BET | 66 | Bethungra ZS | Cootamundra ZS | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0
Wagga North | 7CH/1 | 33 | Cartwrights Hill ZS | Euberta ZS | 4 | 1.99 | 2.03 | 2.06 | 2.09 | 2.11 | 6 | 1.39 | 1.38 | 1.38 | 1.37 | 1.36
Wagga North | 7CH/2 | 33 | Euberta ZS | Ganmurra ZS | 4 | 0.62 | 0.63 | 0.64 | 0.65 | 0.66 | 6 | 0.56 | 0.57 | 0.57 | 0.58 | 0.58
Wagga North | Oura-Mates Gully | 33 | Oura ZS | Mates Gully ZS | 3 | 1.73 | 1.75 | 1.77 | 1.79 | 1.8 | 6 | 1.57 | 1.58 | 1.59 | 1.6 | 1.6
Wagga North | Mates Gully-Tarcutta | 33 | Mates Gully ZS | Tarcutta ZS | 4 | 1.11 | 1.12 | 1.14 | 1.16 | 1.17 | 7 | 1.08 | 1.09 | 1.1 | 1.12 | 1.13
Wagga North | 8WJ | 66 | TransGrid Wagga North 132/66kV STS | Forest Hill ZS | 11 | 5.77 | 5.92 | 6.08 | 6.23 | 6.4 | 19 | 5.1 | 5.15 | 5.21 | 5.26 | 5.31
Yanco | 840/4 | 66 | Narrandra ZS | Kywong ZS | 16 | 0.41 | 0.41 | 0.41 | 0.42 | 0.42 | 25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.31
Yanco | 841:YNC | 66 | TransGrid Yanco 132/33/66kV STS | Narrandera ZS | 15 | 10.42 | 10.46 | 10.49 | 10.51 | 10.58 | 25 | 8.23 | 8.3 | 8.37 | 8.43 | 8.49
Yanco | 7L3 | 33 | TransGrid Yanco 132/33/66kV STS | Cudgel ZS | 8 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26 | 13 | 6.26 | 6.26 | 6.26 | 6.26 | 6.26
Yanco | 7L6/1 | 33 | TransGrid Yanco 132/33/66kV STS | Whitton / Murrami Tee | 15 | 6.69 | 6.71 | 6.74 | 6.76 | 6.77 | 18 | 5.26 | 5.34 | 5.41 | 5.48 | 5.55
Yanco | 7L6/2 | 33 | Whitton / Murrami Tee | Whitton ZS | 8 | 4.08 | 4.09 | 4.1 | 4.11 | 4.11 | 13 | 2.18 | 2.17 | 2.16 | 2.15 | 2.15
Yanco | 7L6/3 | 33 | Whitton / Murrami Tee | Murrami ZS | 6 | 1.35 | 1.36 | 1.39 | 1.41 | 1.42 | 9 | 1.76 | 1.84 | 1.93 | 2.01 | 2.09
Yanco | 7L5/1 | 33 | TransGrid Yanco 132/33/66kV STS | Yanco ZS | 8 | 12.02 | 12.06 | 12.08 | 12.09 | 12.11 | 13 | 8.74 | 8.73 | 8.73 | 8.73 | 8.71
Yanco | 7L5/2 | 33 | Yanco ZS | Leeton ZS | 6 | 9.32 | 9.32 | 9.31 | 9.3 | 9.3 | 9 | 7.55 | 7.52 | 7.5 | 7.48 | 7.45
Yanco | 7L4 | 33 | TransGrid Yanco 132/33/66kV STS | Leeton ZS | 31 | 10.09 | 10.1 | 10.08 | 10.07 | 10.07 | 34 | 7.86 | 7.83 | 7.81 | 7.79 | 7.76
Yass | 971(1) | 132 | TransGrid Yass 330/132/66kV STS | Cullerin Range Wind Farm | 106 | 75.98 | 76.18 | 76.15 | 76.14 | 76.4 | 119 | 78.75 | 78.96 | 78.84 | 78.81 | 79.1
Yass | 971(2) | 132 | Cullerin Range Wind Farm | Gunning Wind Farm | 140 | 48.33 | 48.48 | 48.34 | 48.4 | 48.56 | 157 | 49.46 | 49.63 | 49.46 | 49.53 | 49.81
Yass | 971(3) | 132 | Cullerin Range Wind Farm | Goulburn 132/66/33kV STS | 106 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0
Yass | 976/2 (M) | 132 | TransGrid 132kV Line 976/2(Y) / Murrumbateman Tee | Murrumbateman ZS | 42 | 5.75 | 5.84 | 5.93 | 6 | 6.09 | 82 | 7.57 | 7.68 | 7.79 | 7.91 | 8.03
Yass | 824 | 66 | TransGrid Yass 330/132/66kV STS | Yass ZS | 12 | 12.75 | 12.7 | 12.71 | 12.7 | 12.69 | 18 | 15.43 | 15.52 | 15.61 | 15.69 | 15.79
Yass | 823/5 | 66 | Yass ZS | Marilba ZS | 12 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 18 | 1.45 | 1.44 | 1.44 | 1.44 | 1.44

## BSP
Connection Point | Forecast PF | Summer Forecast (POE50 MVA) |  |  |  |  | Forecast PF | Winter Forecast (POE50 MVA) |  |  |  |  | Major Embedded Generation (MW)
|  | 25/26 | 26/27 | 27/28 | 28/29 | 29/30 |  | 2026 | 2027 | 2028 | 2029 | 2030
Albury (Corowa) | 0.965 | 17.17 | 17.15 | 17.2 | 17.23 | 17.22 | 0.983 | 14.2 | 14.37 | 14.52 | 14.66 | 14.78 | 30
Albury (Mulwala) | 0.989 | 13.01 | 13.03 | 13.1 | 13.17 | 13.24 | 0.998 | 11.19 | 11.27 | 11.35 | 11.44 | 11.5 | 5
Albury (Union Rd + Jelbart) | 0.998 | 94.86 | 96.22 | 97.51 | 98.72 | 100.06 | 0.996 | 81.93 | 82.63 | 83.3 | 83.85 | 84.43 | 0
Armidale | 0.999 | 27.01 | 26.98 | 26.92 | 26.89 | 26.87 | 1 | 48.69 | 49.08 | 49.42 | 49.75 | 50.16 | 10
Balranald | 0.996 | 3.99 | 3.99 | 3.99 | 4 | 4 | 0.935 | 3.35 | 3.42 | 3.48 | 3.54 | 3.59 | 0
Beryl | 0.969 | 78.62 | 79.11 | 79.48 | 80.08 | 80.55 | 0.983 | 80.17 | 80.13 | 80.16 | 80.15 | 80.09 | 87
Boambee South | 0.999 | 17.61 | 17.58 | 17.63 | 17.66 | 17.61 | 0.996 | 19.22 | 19.29 | 19.39 | 19.46 | 19.51 | 0
Broken Hill 22kV | 0.996 | 37.39 | 38.06 | 38.22 | 38.39 | 38.58 | 1 | 34.01 | 35.09 | 35.08 | 35.08 | 35.02 | 50
Casino | 0.98 | 34.2 | 34.31 | 34.32 | 34.4 | 34.38 | 0.979 | 23.89 | 24.05 | 24.21 | 24.35 | 24.49 | 0
Coffs Harbour | 0.979 | 62.43 | 62.39 | 62.35 | 62.33 | 62.38 | 0.982 | 63.76 | 64.08 | 64.48 | 64.85 | 65.21 | 0
Coleambally | 0.959 | 14.73 | 14.99 | 15.18 | 15.39 | 15.57 | 0.952 | 9.64 | 9.52 | 9.4 | 9.29 | 9.18 | 5
Cooma 132kV | 0.924 | 32.97 | 32.92 | 32.77 | 32.69 | 32.58 | 0.917 | 43.23 | 43.01 | 42.86 | 42.52 | 42.24 | 118
Cooma 66kV | 0.999 | 13.16 | 13.21 | 13.25 | 13.29 | 13.34 | 0.998 | 26.39 | 26.59 | 26.78 | 26.95 | 27.14 | 1.1
Cowra | 0.999 | 36.93 | 37.27 | 37.55 | 37.9 | 38.23 | 0.993 | 26.77 | 26.8 | 26.83 | 26.87 | 26.87 | 24
Darlington Point | 0.909 | 26.69 | 27.5 | 28.25 | 28.93 | 29.61 | 0.975 | 24.05 | 24.59 | 25.24 | 25.78 | 26.35 | 85
Deniliquin | 0.999 | 50.24 | 50.99 | 51.44 | 52.14 | 52.8 | 0.999 | 36.71 | 36.99 | 37.22 | 37.5 | 37.69 | 5
Dorrigo | 1 | 2.07 | 2.05 | 2.03 | 2.02 | 2 | 1 | 2.68 | 2.72 | 2.74 | 2.77 | 2.79 | 0
Dunoon | 0.991 | 6.03 | 6.04 | 6.03 | 6.03 | 6.03 | 0.994 | 6.52 | 6.53 | 6.54 | 6.56 | 6.57 | 0
Evans Lane | 1 | 37.85 | 37.81 | 37.82 | 37.89 | 37.78 | 1 | 46.95 | 46.76 | 46.59 | 46.49 | 46.41 | 0
Finley 132kV | 0.992 | 73.59 | 73.7 | 73.82 | 73.98 | 74.1 | 0.967 | 74.31 | 74.3 | 74.32 | 74.43 | 74.33 | 0
Finley 66kV | 0.998 | 15.9 | 15.94 | 15.95 | 15.94 | 15.98 | 0.985 | 13.38 | 13.51 | 13.61 | 13.72 | 13.8 | 2.5
Forbes | 0.999 | 32.44 | 32.32 | 32.17 | 32.02 | 31.9 | 0.999 | 25.62 | 25.76 | 25.91 | 26.02 | 26.14 | 54.1
Glen Innes | 0.922 | 11.2 | 11.3 | 11.38 | 11.47 | 11.55 | 0.987 | 15.73 | 15.86 | 15.98 | 16.09 | 16.2 | 5.5
Griffith | 1 | 93.6 | 93.91 | 94.36 | 94.52 | 94.81 | 0.994 | 62.33 | 62.85 | 63.27 | 63.62 | 64 | 0
Gunnedah 66kV | 0.998 | 29.18 | 29.31 | 38.49 | 38.58 | 38.68 | 0.957 | 27.93 | 28.33 | 36.76 | 37.02 | 37.32 | 7
Hawks Nest | 1 | 8.45 | 8.47 | 8.46 | 8.46 | 8.45 | 0.969 | 8.73 | 8.81 | 8.87 | 8.92 | 8.96 | 0
Herons Ck | 0.994 | 13.06 | 13.32 | 13.53 | 13.71 | 13.87 | 1 | 11.74 | 11.78 | 11.82 | 11.88 | 11.89 | 0
Inverell | 0.985 | 36.13 | 36.07 | 36.12 | 36.15 | 36.16 | 0.966 | 35.83 | 36.13 | 36.33 | 36.54 | 36.76 | 22.5
Kempsey 33kV | 0.994 | 32.01 | 32.24 | 32.53 | 32.63 | 32.84 | 0.998 | 31.68 | 31.86 | 31.98 | 32.16 | 32.29 | 0
Koolkhan | 0.954 | 55.52 | 55.76 | 56.11 | 56.33 | 56.47 | 0.988 | 51.98 | 52.09 | 52.18 | 52.27 | 52.38 | 0
Lismore 132kV | 0.996 | 94.35 | 95.22 | 96.06 | 97.35 | 98.12 | 1 | 98.41 | 101.27 | 103.69 | 105.87 | 107.79 | 37.5
Macksville | 0.999 | 9.32 | 9.36 | 9.4 | 9.43 | 9.42 | 1 | 10.04 | 10.08 | 10.12 | 10.15 | 10.18 | 0
Manildra | 0.932 | 13.26 | 13.31 | 13.38 | 13.44 | 13.52 | 0.955 | 13.14 | 13.16 | 13.2 | 13.23 | 13.26 | 48.5
Marulan | 0.998 | 50.21 | 51.28 | 52.24 | 53.19 | 54.23 | 0.979 | 66.63 | 67.37 | 68.21 | 69.1 | 69.8 | 118
Merbein | 0.999 | 8.93 | 8.92 | 8.93 | 8.92 | 9 | 0.977 | 6.86 | 6.9 | 7.03 | 7.17 | 7.2 | 0
Mildura | 0.974 | 27.34 | 27.64 | 28.18 | 28.42 | 28.58 | 0.999 | 16.11 | 16.18 | 16.29 | 16.33 | 16.33 | 3.3
Molong | 0.994 | 4.96 | 4.97 | 4.98 | 4.97 | 4.98 | 0.988 | 5.02 | 5.01 | 5.01 | 5.01 | 5.01 | 30
Moree | 0.999 | 28.49 | 30.27 | 34.27 | 37.86 | 41.08 | 0.975 | 41.78 | 44.27 | 48.82 | 53 | 56.75 | 66
Morven | 1 | 7.52 | 7.62 | 7.74 | 7.84 | 7.96 | 1 | 7.12 | 7.12 | 7.13 | 7.11 | 7.18 | 0
Mudgee | 1 | 28.32 | 28.85 | 29.37 | 29.85 | 30.38 | 0.996 | 25.03 | 25.11 | 25.23 | 25.32 | 25.42 | 0
Mullumbimby | 0.997 | 63.57 | 64.29 | 65 | 65.81 | 66.49 | 0.993 | 60.36 | 60.76 | 61.24 | 61.57 | 61.86 | 0
Munyang | 0.902 | 3.25 | 3.28 | 3.31 | 3.35 | 3.38 | 0.872 | 33.28 | 33.95 | 34.55 | 35.07 | 35.58 | 0
Murrumbateman | 0.995 | 5.75 | 5.84 | 5.93 | 6 | 6.09 | 0.985 | 7.57 | 7.68 | 7.79 | 7.91 | 8.03 | 0
Murrumburrah | 0.999 | 41.46 | 41.49 | 41.49 | 41.5 | 41.54 | 0.998 | 40.09 | 40.54 | 40.92 | 41.29 | 41.59 | 5
Nambucca | 0.997 | 7.68 | 7.73 | 7.76 | 7.8 | 7.82 | 0.988 | 9.14 | 9.16 | 9.19 | 9.21 | 9.24 | 0
Narrabri | 0.984 | 46.38 | 48.13 | 47.48 | 50.66 | 78.48 | 0.913 | 62 | 64.27 | 69.18 | 74.72 | 94.85 | 16
Orange 132kV | 0.998 | 175.51 | 178.51 | 181.13 | 183.7 | 186.03 | 0.994 | 175.89 | 177.95 | 179.01 | 180.75 | 182.13 | 145
Orange 66kV | 0.982 | 46.87 | 46.73 | 46.42 | 46.2 | 45.97 | 0.998 | 67.36 | 68.2 | 68.98 | 69.62 | 70.21 | 0
Panorama | 0.994 | 70.33 | 70.4 | 70.33 | 70.4 | 70.33 | 0.996 | 77.87 | 78.19 | 78.62 | 78.84 | 79.15 | 10
Parkes 132kV | 0.981 | 33.7 | 41.83 | 49.9 | 58.04 | 60.81 | 0.996 | 33.83 | 41.9 | 50.12 | 58.36 | 61.43 | 0
Parkes 66kV | 0.993 | 33.33 | 33.7 | 34.09 | 34.4 | 34.71 | 0.987 | 30.82 | 31.29 | 31.69 | 32.07 | 32.45 | 94
Port Macquarie | 0.999 | 74.64 | 75.3 | 76.04 | 77 | 77.48 | 0.999 | 81.74 | 82.18 | 82.61 | 83.03 | 83.43 | 0
Queanbeyan 132kV | 0.99 | 17.19 | 22.63 | 28.19 | 33.78 | 39.24 | 0.994 | 17.69 | 23.05 | 28.56 | 34.06 | 39.52 | 0
Queanbeyan 66kV | 0.999 | 48.58 | 48.79 | 48.97 | 49.08 | 49.27 | 1 | 63.78 | 64.26 | 64.77 | 65.11 | 65.52 | 0
Raleigh | 0.994 | 10.76 | 10.76 | 10.74 | 10.73 | 10.73 | 0.997 | 11.36 | 11.4 | 11.45 | 11.48 | 11.52 | 0
Robinvale | 0.977 | 7.61 | 7.69 | 7.75 | 7.81 | 7.85 | 0.99 | 3.91 | 3.95 | 3.99 | 4.03 | 4.06 | 0
Snowy Adit | 0.999 | 2.8 | 2.8 | 2.81 | 2.81 | 2.82 | 0.999 | 8.28 | 8.34 | 8.39 | 8.42 | 8.48 | 0
Stroud | 0.978 | 36.81 | 36.8 | 36.9 | 36.94 | 36.99 | 0.993 | 34.02 | 34.58 | 34.82 | 35.21 | 35.62 | 0
Tamworth | 0.987 | 128.48 | 138.05 | 139.67 | 140.63 | 140.36 | 0.996 | 112.26 | 121.98 | 123.82 | 126.39 | 128.6 | 10
Taree 33kV | 0.992 | 31.16 | 31.19 | 31.26 | 31.18 | 31.14 | 0.999 | 26.72 | 26.74 | 26.77 | 26.78 | 26.84 | 0
Taree 66kV | 0.997 | 53.6 | 53.65 | 53.73 | 54 | 54.19 | 0.999 | 55.06 | 55.22 | 55.34 | 55.5 | 55.74 | 0
Tenterfield | 0.999 | 3.9 | 4.26 | 4.27 | 4.28 | 4.28 | 1 | 6.72 | 6.76 | 6.79 | 6.82 | 6.86 | 0
Terranora | 0.999 | 103.93 | 105.03 | 105.9 | 106.86 | 107.59 | 0.999 | 85.58 | 85.3 | 85.12 | 85 | 84.83 | 30
Tumut | 0.998 | 28.13 | 28.24 | 28.34 | 28.5 | 28.67 | 0.999 | 30.9 | 30.93 | 30.91 | 30.94 | 30.98 | 14
Upper Tumut | 0.991 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.985 | 2.26 | 2.29 | 2.31 | 2.33 | 2.36 | 0
Wagga 66kV | 0.995 | 88.35 | 88.56 | 88.79 | 89.01 | 89.21 | 0.994 | 84.43 | 85.48 | 86.74 | 87.38 | 88.33 | 0
Wagga North 132kV | 0.993 | 81.34 | 83.36 | 84.75 | 86.08 | 87.32 | 0.991 | 75.94 | 76.32 | 76.55 | 76.83 | 77.2 | 268
Wagga North 66kV | 0.988 | 30.12 | 32.39 | 34.6 | 36.8 | 38.96 | 0.947 | 26.85 | 29.56 | 32.23 | 34.82 | 37.42 | 0
Waggamba | 0.997 | 19.04 | 19.07 | 19.07 | 19.12 | 19.1 | 0.999 | 24.05 | 24.41 | 24.78 | 25.07 | 25.38 | 0
Wallerawang 132kV | 0.884 | 36.34 | 37.44 | 38.51 | 39.58 | 40.46 | 0.677 | 47.02 | 49.5 | 51.8 | 53.88 | 55.85 | 0
Wallerawang 66kV | 0.995 | 3.86 | 3.8 | 3.76 | 3.72 | 3.69 | 0.997 | 6.06 | 6.1 | 6.14 | 6.17 | 6.19 | 0
Wellington 132kV | 1 | 198.93 | 198.85 | 199.17 | 199.15 | 199.35 | 0.999 | 167.95 | 168.94 | 169.54 | 170.21 | 170.88 | 15
Yanco | 0.959 | 44.61 | 44.78 | 44.87 | 45.02 | 45.1 | 0.98 | 35.94 | 36.15 | 36.33 | 36.51 | 36.71 | 16.5
Yass 132kV | 0.985 | 23.9 | 23.96 | 23.92 | 24 | 24 | 1 | 25.63 | 24.97 | 24.38 | 23.8 | 23.24 | 76.5
Yass 66kV | 0.984 | 12.93 | 12.97 | 13 | 13.04 | 13.05 | 0.994 | 16.2 | 16.31 | 16.43 | 16.54 | 16.63 | 0

## ZS Export
Region | Substation | kV | Transformer Rating (MVA) |  |  | Firm Normal Cyclic Rating (MVA) | Forecast PF | Forecast (POE50 MW) |  |  |  |  | Embedded Generation (MW) | 95% Peak Load Exceeded (Hrs)
|  |  | Tx.1 | Tx.2 | Tx.3 |  |  | 25/26 | 26/27 | 27/28 | 28/29 | 29/30
Terranora | Banora Point | 66/11 | 24/30 | 24/30 |  | 33 | -0.999 | 11.68 | 12.35 | 12.98 | 13.58 | 14.15 | 17.04 | 108
Terranora | Cudgen 11kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 33 | -0.97 | 10.82 | 11.45 | 12.04 | 12.61 | 13.16 | 16.84 | 80
Terranora | Cudgen 33kV | 66/33/11 | 70/40/30 | 70/40/30 |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Terranora | Hastings Point | 33/11 | 15 | 15 |  | 16.5 | -0.996 | 11.67 | 12.33 | 12.97 | 13.57 | 14.14 | 18.14 | 92
Terranora | Murwillumbah | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | -0.89 | 14 | 14.8 | 15.56 | 16.28 | 16.97 | 24.11 | 21
Terranora | Terranora 110/66kV | 110/66 | 70/100 | 70/100 | 70/100 | 220 | 0.862 | 29.95 | 29.95 | 29.95 | 29.95 | 29.95 | 0 | 6
Terranora | Terranora 11kV | 66/11 | 24/30 | 24/30 |  | 33 | -0.995 | 7.42 | 7.85 | 8.26 | 8.65 | 9.02 | 11.44 | 91
Terranora | Tweed Heads | 66/11 | 25 | 25 |  | 27.5 | 0.998 | 3.63 | 3.86 | 4.08 | 4.28 | 4.48 | 5.28 | 46
Terranora | Tweed Heads South | 66/11 | 20/30 | 20/30 |  | 33 | -0.992 | 10.89 | 11.53 | 12.14 | 12.72 | 13.28 | 17.15 | 67
Lismore | Alstonville | 66/11 | 20 | 16/20 |  | 22 | -0.994 | 10.02 | 10.59 | 11.13 | 11.65 | 12.14 | 16.75 | 44
Lismore | Ballina | 66/11 | 24/30 | 24/30 |  | 33 | -0.871 | 20.71 | 21.94 | 23.11 | 24.23 | 25.29 | 30.45 | 61
Lismore | Ballina 132kV | 132/66 | 35/45/60 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lismore | Dunoon | 132/11 | 10 | 10 |  | 11 | -0.853 | 4.59 | 4.88 | 5.15 | 5.41 | 5.65 | 8.61 | 34
Lismore | Ewingsdale | 132/11 | 30/45 | 30/45 |  | 49.5 | -0.686 | 10.82 | 11.45 | 12.05 | 12.62 | 13.17 | 19.09 | 16
Lismore | Kyogle | 66/11 | 8/10 | 8/10 |  | 11 | -1 | 4.5 | 4.73 | 4.96 | 5.17 | 5.37 | 7.6 | 14
Lismore | Lennox Head | 132/11 | 16 | 16 |  | 17.6 | -0.977 | 5.27 | 5.56 | 5.84 | 6.11 | 6.36 | 8.71 | 6
Lismore | Lismore 132/66kV | 132/66 | 80/120 | 80/120 | 80/120 | 264 | 0.974 | 29.69 | 29.69 | 29.69 | 29.69 | 29.69 | 0 | 74
Lismore | Lismore East | 66/11 | 15/19/23 | 15/20/25 |  | 25.3 | -0.994 | 10.35 | 10.96 | 11.54 | 12.09 | 12.62 | 17.07 | 32
Lismore | Lismore South | 66/11 | 15/19/25 | 15/19/23 | 20/25 | 52.8 | -0.462 | 3.87 | 4.09 | 4.3 | 4.5 | 4.69 | 7.88 | 16
Lismore | Lismore Uni | 66/11 | 20/30 | 20/30 |  | 33 | 0.701 | 9.91 | 10.49 | 11.04 | 11.57 | 12.07 | 16.2 | 39
Lismore | Mullumbimby | 132/11 | 16 | 10 |  | 11 | -0.933 | 6.89 | 7.26 | 7.61 | 7.94 | 8.26 | 12.34 | 25
Lismore | Suffolk Park | 132/11 | 30 |  |  | 0 | -0.992 | 7.92 | 8.42 | 8.89 | 9.33 | 9.75 | 13.8 | 15
Lismore | Woodburn | 66/11 | 8/10 | 8/10 |  | 11 | -0.962 | 5.29 | 5.6 | 5.9 | 6.18 | 6.44 | 8.14 | 22
Casino | Bonalbo | 33/11 | 3 | 2.5 |  | 2.75 | 0.9 | 0.51 | 0.53 | 0.55 | 0.57 | 0.59 | 0.97 | 22
Casino | Casino 132/66kV | 132/66 | 35/45/60 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Casino | Casino 66/11kV | 66/11 | 20/30 | 20/30 |  | 33 | 0.612 | 11.45 | 12.05 | 12.63 | 13.18 | 13.71 | 18.44 | 16
Casino | Casino 66/33kV | 66/33 | 8 | 3.5 |  | 3.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Casino | Mallanganee | 33/11 | 5/8 | 2.5 |  | 2.75 | 0.914 | 0.57 | 0.59 | 0.62 | 0.65 | 0.67 | 1.02 | 40
Casino | Rappville | 66/11 | 5/6.25 | 5 |  | 5.5 | -0.923 | 0.43 | 0.46 | 0.48 | 0.5 | 0.53 | 0.71 | 13
Casino | Urbenville | 33/11 | 5/8 | 2.5 |  | 2.75 | -0.042 | 0.51 | 0.54 | 0.57 | 0.59 | 0.62 | 0.75 | 8
Grafton | Grafton North | 66/11 | 24/30 | 15/20/25 |  | 27.5 | -0.737 | 8.33 | 8.82 | 9.28 | 9.72 | 10.15 | 12.23 | 33
Grafton | Grafton South | 66/11 | 15/19/25 | 15/19/24.5 |  | 26.95 | -0.868 | 8.45 | 8.89 | 9.32 | 9.72 | 10.11 | 13.44 | 28
Grafton | Koolkhan 11kV | 66/11 | 7.5/10 |  |  | 0 | -0.798 | 2.03 | 2.16 | 2.29 | 2.4 | 2.52 | 3.01 | 42
Grafton | Maclean 66/11kV | 66/11 | 10/16 | 10/16 |  | 17.6 | -0.837 | 7.72 | 8.14 | 8.54 | 8.91 | 9.28 | 12.08 | 35
Grafton | Maclean 66/33kV | 66/33 | 8/10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grafton | Nymboida | 66/11 | 0.6 | 0.6 |  | 0.66 | 0.95 | 0.21 | 0.22 | 0.23 | 0.24 | 0.25 | 0.36 | 12
Grafton | Redcliff | 33/11 | 0.5 | 0.5 |  | 0.55 | 0.591 | 0.19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.27 | 32
Grafton | Shannon Creek | 66/11 | 8 |  |  | 0 | -1 | 0.75 | 0.79 | 0.82 | 0.86 | 0.89 | 1.22 | 11
Grafton | Yamba | 66/11 | 20/30 | 15/19/23 |  | 25.3 | -0.963 | 8.39 | 8.93 | 9.43 | 9.91 | 10.37 | 11.94 | 55
Coffs Harbour | Boambee South 11kV | 132/66/11 | 60/30/30 |  |  | 33 | -0.998 | 6.77 | 7.19 | 7.58 | 7.95 | 8.31 | 9.98 | 33
Coffs Harbour | Boambee South 66kV | 132/66/11 |  | 60/30/30 |  | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | Coffs Harbour North | 66/11 | 15/19/23 | 15/20/25 | 15/19/23 | 50.6 | 0.978 | 11.83 | 12.62 | 13.37 | 14.07 | 14.75 | 17.83 | 54
Coffs Harbour | Coffs Harbour South | 66/11 | 20/30 | 20/30 |  | 33 | 0.553 | 8.02 | 8.56 | 9.08 | 9.56 | 10.02 | 11.03 | 13
Coffs Harbour | Dorrigo | 132/11, 66/11 | 7.5/10 | 10 |  | 11 | -0.512 | 1.72 | 1.81 | 1.9 | 1.99 | 2.07 | 2.84 | 49
Coffs Harbour | Moonee | 66/11 | 10/16 | 10/16 |  | 17.6 | -0.999 | 5.84 | 6.21 | 6.57 | 6.91 | 7.23 | 8.94 | 58
Coffs Harbour | Nana Glen | 66/11 | 5/6.25 | 8 |  | 6.88 | -0.957 | 1.94 | 2.05 | 2.15 | 2.24 | 2.33 | 3.28 | 25
Coffs Harbour | Sawtell | 66/11 | 15/19/24.5 | 15/19/25 |  | 26.95 | -0.391 | 6.11 | 6.54 | 6.94 | 7.32 | 7.68 | 8.28 | 58
Coffs Harbour | Ulong | 66/11 | 2.5 |  |  | 0 | 0.945 | 0.37 | 0.4 | 0.43 | 0.46 | 0.48 | 0.5 | 36
Coffs Harbour | Woolgoolga | 66/11 | 20/30 | 20/30 |  | 33 | -0.977 | 10.32 | 11.02 | 11.69 | 12.32 | 12.91 | 15.04 | 92
Nambucca Heads | Macksville | 132/11 | 24/30 | 24/30 |  | 33 | -0.992 | 7.15 | 7.63 | 8.09 | 8.52 | 8.93 | 10.9 | 36
Nambucca Heads | Nambucca Heads | 66/11 | 15/19/23 | 17/22/24.5 |  | 25.3 | -0.561 | 5.59 | 5.97 | 6.33 | 6.66 | 6.98 | 8.37 | 91
Nambucca Heads | Raleigh | 132/11 | 30 | 30 |  | 33 | -0.907 | 6.86 | 7.29 | 7.69 | 8.07 | 8.43 | 12.16 | 54
Kempsey | Crescent Head | 33/11 | 3/4 | 5 |  | 4.4 | -0.885 | 1.16 | 1.23 | 1.3 | 1.37 | 1.43 | 1.72 | 48
Kempsey | Munga | 33/11 | 2.5/3.25 | 3 |  | 3.3 | -0.928 | 0.95 | 1.01 | 1.06 | 1.12 | 1.17 | 1.53 | 10
Kempsey | North St | 33/11 | 16 |  |  | 0 | 0.852 | 4.59 | 4.85 | 5.1 | 5.33 | 5.56 | 7.92 | 48
Kempsey | Prince St | 33/11 | 10/15 | 10/15 |  | 16.5 | -0.602 | 4.52 | 4.84 | 5.14 | 5.41 | 5.68 | 6.83 | 34
Kempsey | Smithtown | 33/11 | 5/6.5 | 5 |  | 5.5 | 0.754 | 1.7 | 1.81 | 1.91 | 2.01 | 2.11 | 2.85 | 9
Kempsey | South West Rocks | 33/11 | 10/12.5 | 16 |  | 13.75 | -0.752 | 5.52 | 5.94 | 6.34 | 6.71 | 7.06 | 7.51 | 119
Port Macquarie | Boronia St | 33/11 | 20/30 | 20/30 |  | 33 | -0.447 | 9.37 | 9.92 | 10.44 | 10.94 | 11.42 | 14.5 | 30
Port Macquarie | Byabarra | 33/11 | 2.5/3.25 | 3 |  | 3.3 | -0.429 | 0.76 | 0.8 | 0.84 | 0.87 | 0.91 | 1.36 | 32
Port Macquarie | Clearwater Cr | 33/11 | 20/30 | 20/30 |  | 33 | -0.999 | 18.97 | 20.38 | 21.7 | 22.94 | 24.11 | 27.37 | 111
Port Macquarie | Koree Island | 33/11 | 5/8 | 3.5 |  | 3.85 | -0.999 | 1.84 | 1.96 | 2.08 | 2.19 | 2.29 | 3 | 19
Port Macquarie | Lake Cathie | 33/11 | 8 | 10/16 |  | 8.8 | -0.995 | 6.44 | 6.88 | 7.29 | 7.68 | 8.05 | 9.33 | 73
Port Macquarie | Owen St | 33/11 | 30 | 15/20 |  | 22 | 0.947 | 5.27 | 5.62 | 5.95 | 6.26 | 6.55 | 7.27 | 21
Port Macquarie | Rocks Ferry | 33/11 | 10/16 | 10/15 |  | 16.5 | 1 | 8.06 | 8.57 | 9.05 | 9.51 | 9.95 | 13.01 | 47
Port Macquarie | Telegraph Point | 33/11 | 3/4 | 3/4 |  | 4.4 | -0.951 | 1.16 | 1.24 | 1.31 | 1.38 | 1.45 | 2.21 | 28
Herons Creek | Herons Creek | 132/66 | 60 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Herons Creek | Johns River | 66/11 | 3 |  |  | 0 | 0.495 | 0.52 | 0.55 | 0.57 | 0.59 | 0.61 | 1.06 | 16
Herons Creek | Kew | 66/11 | 3/4 | 8 |  | 4.4 | -1 | 2.55 | 2.7 | 2.85 | 2.98 | 3.11 | 4.15 | 16
Herons Creek | Laurieton | 33/11, 66/11 | 15/20 | 15/20 |  | 22 | 1 | 6.16 | 6.51 | 6.84 | 7.16 | 7.47 | 8.69 | 77
Taree | Bohnock | 66/11 | 5/7 | 5/7 |  | 7.7 | -0.997 | 5.25 | 5.63 | 5.98 | 6.32 | 6.63 | 7.81 | 66
Taree | Bootawa | 33/11 | 8/11 | 5 |  | 5.5 | -0.635 | 1.09 | 1.16 | 1.23 | 1.29 | 1.35 | 1.89 | 18
Taree | Coopernook | 33/11 | 5/8 | 5/6.5 |  | 7.15 | -0.946 | 1.61 | 1.7 | 1.79 | 1.87 | 1.95 | 2.77 | 46
Taree | Forster | 66/11 | 15/20/25 | 15/20/25 |  | 27.5 | -0.94 | 9.31 | 10.01 | 10.67 | 11.29 | 11.87 | 12.76 | 85
Taree | Hallidays Point 11kV | 66/11 | 12.5/16 | 10/16 |  | 17.6 | -0.958 | 7.02 | 7.53 | 8.01 | 8.47 | 8.9 | 10.2 | 12
Taree | Harrington | 33/11 | 5/8 | 5/6.25 |  | 6.88 | -1 | 3.79 | 4.03 | 4.26 | 4.48 | 4.69 | 4.85 | 103
Taree | Kanangra Dr | 33/11 | 20/30 | 20/25 |  | 27.5 | 0.534 | 5.62 | 5.96 | 6.28 | 6.58 | 6.87 | 8.72 | 65
Taree | Tuncurry | 66/11 | 10/16 | 12.5/16 |  | 17.6 | -0.989 | 3.68 | 3.93 | 4.17 | 4.39 | 4.61 | 4.94 | 62
Taree | Whitbread St | 66/11 | 20 | 20/30 |  | 22 | 0.621 | 6.66 | 7.08 | 7.47 | 7.84 | 8.19 | 9.99 | 27
Taree | Wingham | 33/11 | 10/16 | 7.5/10 |  | 11 | 0.016 | 5.14 | 5.48 | 5.8 | 6.11 | 6.4 | 8.06 | 52
Stroud | Booral | 33/11 | 3 | 2.5 |  | 2.75 | -0.837 | 0.69 | 0.73 | 0.76 | 0.8 | 0.83 | 1.27 | 16
Stroud | Bulahdelah | 33/11 | 5/8 | 5/6.5 |  | 7.15 | -0.275 | 1.82 | 1.92 | 2.01 | 2.1 | 2.19 | 2.67 | 15
Stroud | Dungog | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.959 | 3.9 | 4.15 | 4.37 | 4.59 | 4.8 | 5.68 | 11
Stroud | Gloucester | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.859 | 4.66 | 4.98 | 5.27 | 5.55 | 5.81 | 6.51 | 32
Stroud | Gresford | 33/11 | 5/8 | 5/6.5 |  | 7.15 | -0.929 | 1.17 | 1.25 | 1.32 | 1.39 | 1.46 | 1.74 | 16
Stroud | Martins Creek | 33/11 | 5/8 | 5/8 |  | 8.8 | -0.947 | 1.68 | 1.77 | 1.86 | 1.94 | 2.02 | 2.95 | 17
Stroud | Pacific Palms | 33/11 | 5/8 | 5/8 |  | 8.8 | -0.944 | 2.5 | 2.66 | 2.81 | 2.95 | 3.09 | 3.96 | 76
Stroud | Stroud 132/33kV | 132/33 | 50/60 | 50/60 |  | 66 | -0.977 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.01 | 288
Stroud | Stroud 33/11kV | 33/11 | 5 | 5/8 |  | 5.5 | -0.97 | 1.4 | 1.48 | 1.55 | 1.62 | 1.69 | 2.13 | 10
Hawks Nest | Hawks Nest 132/33kV | 132/33 | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hawks Nest | Tea Gardens | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.973 | 5.87 | 6.24 | 6.59 | 6.92 | 7.23 | 7.75 | 28
Tenterfield | TransGrid 132/22kV Total Tenterfield 22kV Supply |  |  |  |  | 0 | -0.983 | 5.4 | 5.57 | 5.74 | 5.91 | 6.06 | 2.71 | 59
Tenterfield | Tenterfield 11kV | 22/11 | 2.5 | 4 |  | 2.75 | -0.919 | 1.47 | 1.55 | 1.62 | 1.7 | 1.77 | 1.9 | 51
Armidale | Galloway St | 66/11 | 12.5/16 | 10/12.5 |  | 13.75 | -0.873 | 11.57 | 11.98 | 12.37 | 12.73 | 13.08 | 9.41 | 92
Armidale | Hillgrove | 66/11 | 5/6.25 |  |  | 0 | 0.217 | 0.15 | 0.16 | 0.16 | 0.17 | 0.18 | 0.22 | 5
Armidale | Madgwick Dr | 66/11 | 10/12.5 | 10/16 |  | 13.75 | -0.895 | 6.44 | 6.89 | 7.31 | 7.7 | 8.08 | 6.43 | 48
Armidale | Miller St | 66/11 | 12.5/16 | 10/16 |  | 17.6 | -0.476 | 4.19 | 4.44 | 4.68 | 4.91 | 5.13 | 5.97 | 43
Armidale | Oaky | 66/11 | 3.5 | 3.5 |  | 3.85 | 0.95 | 0.15 | 0.16 | 0.17 | 0.18 | 0.18 | 0.21 | 18
Armidale | Uralla | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 2.61 | 2.78 | 2.94 | 3.09 | 3.24 | 3.62 | 38
Armidale | Walcha South 66/22kV | 66/22 | 8 | 8/10 |  | 8.8 | 0.969 | 0.76 | 0.79 | 0.81 | 0.83 | 0.85 | 1.13 | 14
Armidale | Walcha South 22/11kV | 22/11 | 3 | 3 |  | 3.3 | -0.405 | 0.85 | 0.9 | 0.94 | 0.99 | 1.03 | 1.25 | 54
Glen Innes | Emmaville 66/11kV | 66/11 | 3 |  |  | 0 | 0.95 | 0.79 | 0.84 | 0.88 | 0.91 | 0.95 | 1.19 | 29
Glen Innes | Emmaville 66/22kV | 66/22 | 2.5 |  |  | 0 | -0.726 | 0.11 | 0.11 | 0.12 | 0.12 | 0.12 | 0.13 | 29
Glen Innes | Glen Innes | 66/11 | 15/20 | 15/20 |  | 22 | -0.937 | 4.75 | 5.01 | 5.26 | 5.5 | 5.73 | 7.19 | 35
Glen Innes | Guyra | 66/11/22 | 5 | 5 |  | 5.5 | -0.217 | 2.47 | 2.61 | 2.74 | 2.86 | 2.98 | 3.22 | 63
Glen Innes | Pindari | 66/22 | 0.5 |  |  | 0 | 1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 8
Inverell | Ashford | 66/22 | 3 |  |  | 0 | 0.95 | 0.65 | 0.68 | 0.71 | 0.74 | 0.77 | 0.86 | 14
Inverell | Bingara | 66/22 | 3 | 7.5 |  | 3.3 | -0.664 | 1.42 | 1.5 | 1.58 | 1.65 | 1.72 | 2.15 | 14
Inverell | Borthwick St | 66/22 | 20/30 | 15/30 |  | 33 | -0.981 | 10.77 | 11.3 | 11.81 | 12.29 | 12.76 | 15.31 | 21
Inverell | Bundarra | 66/22 | 3 |  |  | 0 | -0.961 | 0.5 | 0.52 | 0.55 | 0.57 | 0.59 | 0.82 | 37
Inverell | Copeton | 66/22 | 3 | 1.5 |  | 1.65 | 0.999 | 0 | 0 | 0 | 0 | 0 | 0 | 78
Inverell | Texas 66/22kV | 66/22 | 5 | 5 |  | 5.5 | 0.148 | 0.82 | 0.85 | 0.88 | 0.9 | 0.93 | 1.42 | 31
Inverell | Texas 66/33kV | 66/33 | 7.5 | 5 |  | 5.5 | 0.976 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.59 | 10
Inverell | Wallangra | 66/22 | 1 |  |  | 0 | 1 | 0.06 | 0.07 | 0.07 | 0.07 | 0.07 | 0.12 | 4
Inverell | Warialda | 66/22 | 4 | 8 |  | 4.4 | -0.845 | 1.74 | 1.82 | 1.89 | 1.97 | 2.04 | 2.46 | 25
Inverell | Yallaroi | 66/22 | 3/4 |  |  | 0 | 0.95 | 0.54 | 0.56 | 0.58 | 0.59 | 0.61 | 0.95 | 5
Waggamba | Goondiwindi 22kV | 66/22 | 15 | 20/30 |  | 16.5 | 0.99 | 13.01 | 13.25 | 13.47 | 13.69 | 13.9 | 6.85 | 21
Waggamba | Goondiwindi 33kV | 66/33 | 5 |  |  | 0 | 0.543 | 1.52 | 1.56 | 1.6 | 1.63 | 1.67 | 2.72 | 17
Moree | Ashley | 66/22 | 8 |  |  | 0 | 0.282 | 0.29 | 0.3 | 0.3 | 0.31 | 0.32 | 0.56 | 4
Moree | Bellata | 66/11 | 2.8 | 2.5 |  | 2.75 | 0.842 | 0.27 | 0.28 | 0.28 | 0.29 | 0.29 | 0.54 | 25
Moree | Moree | 66/22 | 15/30 | 24/30 |  | 33 | -0.509 | 8.96 | 9.35 | 9.73 | 10.09 | 10.44 | 14.47 | 10
Moree | Mungindi | 66/22/33 | 8 |  |  | 0 | 0.95 | 0.72 | 0.76 | 0.79 | 0.83 | 0.86 | 1.33 | 7
Moree | Wathagar | 66/22 | 5 |  |  | 0 | 0.869 | 3.34 | 3.34 | 3.34 | 3.34 | 3.35 | 0.24 | 1197
Moree | Wenna | 66/22 | 7.5 |  |  | 0 | -0.929 | 5 | 5 | 5 | 5 | 5 | 0.05 | 584
Narrabri | Brewarrina | 66/22 | 6.5/8 |  |  | 0 | -0.158 | 0.73 | 0.77 | 0.8 | 0.84 | 0.87 | 1.33 | 6
Narrabri | Burren Junction | 66/22 | 5 | 5 |  | 5.5 | 0.659 | 0.42 | 0.43 | 0.44 | 0.46 | 0.47 | 0.69 | 22
Narrabri | Lightning Ridge | 66/22 | 6.5/8 | 5 |  | 5.5 | -0.952 | 1.71 | 1.83 | 1.96 | 2.07 | 2.18 | 2.57 | 11
Narrabri | Merrywinebone | 66/22 | 5 |  |  | 0 | 0.038 | 0.48 | 0.51 | 0.54 | 0.57 | 0.6 | 0.74 | 4
Narrabri | Narrabri | 66/22/11 | 18/30 | 18/30 |  | 33 | 0.651 | 6.08 | 6.34 | 6.59 | 6.83 | 7.07 | 10.15 | 18
Narrabri | Walgett | 66/22 | 10/16 | 10 |  | 11 | -0.395 | 1.87 | 2 | 2.11 | 2.22 | 2.33 | 3.32 | 14
Narrabri | Wee Waa | 66/22 | 8.8/10 | 16 |  | 11 | 0.951 | 1.75 | 1.83 | 1.91 | 1.99 | 2.06 | 2.89 | 11
Gunnedah | Boggabri | 66/11 | 5/6.5 | 10 |  | 7.15 | 0.707 | 1.15 | 1.2 | 1.25 | 1.3 | 1.34 | 1.75 | 15
Gunnedah | Gunnedah 22kV | 66/22/11 | 18/30 | 18/30 |  | 33 | -0.999 | 9.44 | 10.14 | 10.8 | 11.42 | 12.01 | 13.03 | 36
Gunnedah | Keepit Dam | 66/11 | 1 |  |  | 0 | 1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 8
Tamworth | Attunga | 66/11 | 5 | 8 |  | 5.5 | 0.95 | 1.22 | 1.28 | 1.33 | 1.38 | 1.44 | 1.73 | 11
Tamworth | Barraba | 66/11 | 5 | 5 |  | 5.5 | -0.998 | 1.3 | 1.38 | 1.45 | 1.51 | 1.58 | 1.96 | 20
Tamworth | Bendemeer | 66/11 | 3 | 1 |  | 1.1 | -0.059 | 0.42 | 0.44 | 0.46 | 0.49 | 0.51 | 0.63 | 13
Tamworth | Caroona | 33/11 | 2 | 3 |  | 2.2 | 0.889 | 0.09 | 0.1 | 0.1 | 0.11 | 0.11 | 0.17 | 3
Tamworth | Colly Blue | 33/11 | 1.5 | 3 |  | 1.65 | 1 | 0.26 | 0.27 | 0.28 | 0.3 | 0.31 | 0.41 | 15
Tamworth | Currabubula | 66/11 | 3 |  |  | 0 | 0.95 | 0.43 | 0.45 | 0.47 | 0.49 | 0.5 | 0.65 | 13
Tamworth | Goddard Lane | 66/11 | 20/30 | 20/30 |  | 33 | -0.981 | 4.2 | 4.46 | 4.72 | 4.96 | 5.18 | 3.17 | 7
Tamworth | Kootingal | 66/11 | 10/16 | 10/16 |  | 17.6 | -0.76 | 8.07 | 8.27 | 8.46 | 8.63 | 8.8 | 4.83 | 88
Tamworth | Manilla | 66/11 | 5/6.25 | 5/6.25 |  | 6.88 | 0.9 | 1.97 | 2.09 | 2.2 | 2.31 | 2.41 | 2.74 | 11
Tamworth | Murrurundi | 33/11 | 5/8 |  |  | 0 | 1 | 1.44 | 1.53 | 1.62 | 1.7 | 1.78 | 1.92 | 21
Tamworth | Nundle | 66/11 | 2.5 | 2.5 |  | 2.75 | -0.649 | 0.77 | 0.81 | 0.84 | 0.87 | 0.9 | 1.3 | 27
Tamworth | Oxley Vale | 66/11 | 20/30 | 20/30 |  | 33 | -0.999 | 9.91 | 10.58 | 11.22 | 11.82 | 12.39 | 13 | 16
Tamworth | Quirindi 66/11kV | 66/33/11 | 10/13.3 | 10/13.3 |  | 14.63 | -0.24 | 2.74 | 2.89 | 3.04 | 3.17 | 3.31 | 3.66 | 30
Tamworth | Quirindi 66/33kV | 66/33/11 | 8/10 | 8/10 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tamworth | Spring Ridge | 33/11 | 1 |  |  | 0 | 0.95 | 0.08 | 0.09 | 0.09 | 0.09 | 0.1 | 0.18 | 8
Tamworth | Tamworth East | 66/11 | 20/30 | 18/23 | 18/23 | 50.6 | 1 | 8.82 | 9.37 | 9.89 | 10.38 | 10.85 | 12.94 | 34
Tamworth | Tamworth South | 66/11 | 20/30 | 20/30 |  | 33 | -0.03 | 10.4 | 11.04 | 11.65 | 12.22 | 12.78 | 15 | 68
Tamworth | Upper Manilla | 66/11 | 1.5 |  |  | 0 | 0.799 | 0.05 | 0.05 | 0.06 | 0.06 | 0.06 | 0.12 | 16
Tamworth | Werris Creek | 66/11 | 8 | 5/6.25 |  | 6.88 | -0.07 | 5.49 | 5.55 | 5.6 | 5.65 | 5.7 | 1.4 | 440
Beryl | Coonabarabran | 66/22 | 10/13 | 10/13 |  | 14.3 | -0.938 | 4.07 | 4.26 | 4.45 | 4.62 | 4.79 | 6.72 | 16
Beryl | Dunedoo | 66/22 | 7.5/10 | 7.5/10 |  | 11 | -0.786 | 2.84 | 2.97 | 3.1 | 3.23 | 3.35 | 4.24 | 64
Beryl | Gulgong | 66/22 | 5 |  |  | 0 | -1 | 1.48 | 1.58 | 1.67 | 1.76 | 1.84 | 2.33 | 26
Beryl | Mudgee | 132/22, 66/22 | 18/30 | 30 |  | 33 | -0.995 | 11.74 | 12.45 | 13.12 | 13.76 | 14.38 | 18.38 | 9
Beryl | Ulan Town | 66/22 | 3 | 2.5 |  | 2.75 | 0.886 | 1.11 | 1.17 | 1.22 | 1.27 | 1.32 | 1.71 | 34
Wellington | Mumbil | 66/11 | 2.5 | 2.8 |  | 2.75 | 0.372 | 0.54 | 0.59 | 0.63 | 0.67 | 0.7 | 0.79 | 25
Wellington | Wellington 11kV | 132/11, 66/11 | 8/11 | 15 |  | 12.1 | -0.087 | 3.48 | 3.73 | 3.96 | 4.18 | 4.39 | 5.79 | 6
Dubbo | Coonamble | 66/22 | 10 | 10 |  | 11 | -0.697 | 2.52 | 2.66 | 2.79 | 2.91 | 3.03 | 3.74 | 5
Dubbo | Dubbo 132/66kV | 132/66 | 30/45 | 30/45 | 30/45 | 99 | 0.878 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 0 | 2
Dubbo | Dubbo Phillip St | 66/11 | 20/30 | 20/30 |  | 33 | 0.814 | 4.44 | 4.7 | 4.94 | 5.17 | 5.39 | 6.63 | 7
Dubbo | Dubbo South | 132/11 | 24/30 | 24/30 |  | 33 | -0.997 | 24.9 | 25.61 | 26.28 | 26.92 | 27.53 | 16.22 | 165
Dubbo | Dubbo West | 132/11 | 15/23 | 15/23 |  | 25.3 | -1 | 8.2 | 8.68 | 9.14 | 9.57 | 9.99 | 12.51 | 21
Dubbo | Eulomogo | 66/11 | 15/30 | 20/30 |  | 33 | -0.73 | 13.68 | 14.44 | 15.15 | 15.83 | 16.47 | 16.95 | 17
Dubbo | Geurie | 66/11 | 5 |  |  | 0 | -0.894 | 0.78 | 0.84 | 0.89 | 0.95 | 0.99 | 1.19 | 25
Dubbo | Gilgandra | 66/11 | 8/12 | 8/12 |  | 13.2 | -0.885 | 2.98 | 3.14 | 3.29 | 3.44 | 3.58 | 4.77 | 30
Dubbo | Gulargambone | 66/22 | 3 |  |  | 0 | 0.95 | 0.65 | 0.68 | 0.71 | 0.74 | 0.77 | 1.02 | 20
Dubbo | Narromine | 132/22 | 17/24 | 24 |  | 26.4 | -0.101 | 19.38 | 19.63 | 19.86 | 20.09 | 20.31 | 7.9 | 125
Dubbo | Nevertire | 132/22, 66/22 | 17/24 | 10 |  | 11 | 0.328 | 2.12 | 2.23 | 2.33 | 2.43 | 2.52 | 3.54 | 9
Dubbo | Yarrandale | 66/11 | 18/25 | 20/30 |  | 27.5 | 0.531 | 1.39 | 1.47 | 1.53 | 1.6 | 1.66 | 2.39 | 4
Nyngan | Bourke 22kV | 66/22 | 8.8/10 | 8.8/10 |  | 11 | -0.473 | 1.47 | 1.52 | 1.57 | 1.62 | 1.67 | 2.46 | 6
Nyngan | Bourke 33kV | 66/33 | 5/8 |  |  | 0 | 0.242 | 0.48 | 0.49 | 0.5 | 0.51 | 0.53 | 0.83 | 11
Nyngan | Byrock | 66/22 | 1 | 1 |  | 1.1 | 1 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 7
Nyngan | Cobar CSA | 132/11 | 15/18 | 30/45 |  | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Elura | 132/11 | 15 | 15 |  | 16.5 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Peak | 132/11 | 15/20 | 15/20 |  | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Cobar Town | 66/22 | 8/11 | 10 |  | 11 | 0.95 | 3.49 | 3.7 | 3.91 | 4.1 | 4.29 | 4.94 | 21
Nyngan | Girilambone | 66/11 | 10/12.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan | Nyngan 132kV | 132/66 | 18/30 | 30/45 |  | 33 | 0.881 | 2.48 | 2.48 | 2.48 | 2.48 | 2.48 | 0 | 2428
Nyngan | Nyngan Town | 66/22 | 10 | 10 |  | 11 | -0.714 | 4.65 | 4.76 | 4.85 | 4.95 | 5.04 | 2.75 | 17
Broken Hill | TransGrid 220/22kV Total Broken Hill 22kV Supply |  |  |  |  | 0 | -0.995 | 38.4 | 39.81 | 41.13 | 42.39 | 43.59 | 26.2 | 28
Broken Hill | Wilcannia 33kV |  |  |  |  | 0 | -0.027 | 0.21 | 0.21 | 0.21 | 0.22 | 0.22 | 0.33 | 6
Broken Hill | Menindee | 66/22 | 4/5 | 4/5 |  | 5.5 | -0.993 | 0.72 | 0.77 | 0.81 | 0.85 | 0.88 | 1.03 | 21
Broken Hill | Mt Gipps 33kV | 66/33 | 1.5 | 1.5 |  | 1.65 | 0.329 | 0.53 | 0.55 | 0.57 | 0.58 | 0.6 | 0.95 | 9
Broken Hill | Mt Gipps 6.6kV | 66/6.6 | 1.5 | 1.5/2 |  | 1.65 | 0.677 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.13 | 7
Broken Hill | Pinnacles Place | 22/66 | 15 | 15 |  | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Broken Hill | Sunset Strip 22kV | 66/22 | 5 |  |  | 0 | -0.974 | 0.33 | 0.37 | 0.4 | 0.43 | 0.46 | 0.35 | 13
Broken Hill | Sunset Strip 33kV | 66/33 | 4 | 4 |  | 4.4 | 0.069 | 0.17 | 0.17 | 0.17 | 0.18 | 0.18 | 0.26 | 5
Broken Hill | Wilcannia 6.6kV | 33/6.6 | 3.5 | 3.5 |  | 3.85 | -0.904 | 0.4 | 0.43 | 0.46 | 0.48 | 0.51 | 0.68 | 2
Orange | Orange Industrial | 66/11 | 15 | 10 |  | 11 | -0.998 | 9.14 | 9.72 | 10.26 | 10.78 | 11.27 | 11.74 | 30
Orange | Orange North | 66/11 | 20/30 | 20/30 |  | 33 | 0.94 | 6.25 | 6.67 | 7.08 | 7.46 | 7.82 | 7.81 | 16
Orange | Orange South | 66/11 | 20/30 | 20/30 |  | 33 | -0.976 | 10.54 | 11.31 | 12.02 | 12.7 | 13.35 | 13.59 | 18
Orange | Orange West | 66/11 | 30 | 30 |  | 33 | -0.998 | 9.1 | 9.72 | 10.3 | 10.84 | 11.36 | 12.38 | 44
Molong | Cumnock | 66/11 | 2.5 | 2.5 |  | 2.75 | -0.932 | 0.88 | 0.92 | 0.95 | 0.99 | 1.02 | 1.43 | 27
Molong | Manildra | 132/11 | 18/24 | 18/24 |  | 26.4 | 0.936 | 44.7 | 44.76 | 44.81 | 44.86 | 44.91 | 2.21 | 5
Molong | Molong 11kV | 66/11 | 5/7.5 | 3/4 |  | 4.4 | 0.986 | 1.98 | 2.11 | 2.24 | 2.36 | 2.47 | 2.95 | 4
Bathurst | Blayney | 66/11 | 20 | 14/20 |  | 22 | 0.901 | 4.1 | 4.4 | 4.68 | 4.95 | 5.2 | 5.71 | 8
Bathurst | Mandurama | 66/11 | 2.5 | 3/4 |  | 2.75 | -0.871 | 1.28 | 1.35 | 1.43 | 1.49 | 1.56 | 1.85 | 40
Bathurst | Raglan | 66/11 | 18/30 | 18/30 |  | 33 | -0.843 | 9.27 | 9.91 | 10.51 | 11.08 | 11.62 | 13.28 | 54
Bathurst | Russell Street | 66/11 | 20/30 | 15/30 | 20/30 | 66 | 0.786 | 8.45 | 9.08 | 9.68 | 10.23 | 10.76 | 11.24 | 20
Bathurst | Stewart | 66/11 | 13/20 | 15/18/25 |  | 22 | -1 | 11.28 | 12.06 | 12.8 | 13.49 | 14.15 | 15.11 | 22
Oberon | Burraga | 33/11 | 2.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oberon | Oberon 132kV | 132/11 | 25/36/45 | 25/36/45 |  | 49.5 | 0.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oberon | Oberon Town | 66/11 | 10/15 | 10/15 |  | 16.5 | 0.156 | 2.83 | 3 | 3.17 | 3.33 | 3.48 | 4.04 | 46
Parkes | Parkes Town | 66/11 | 30 | 20/30 |  | 33 | -0.988 | 8.8 | 9.29 | 9.75 | 10.19 | 10.62 | 12.68 | 18
Parkes | Peak Hill | 66/11 | 8 | 5 | 5 | 11 | -0.927 | 6.08 | 6.14 | 6.2 | 6.25 | 6.3 | 1.73 | 615
Parkes | Trundle | 66/22 | 8 | 5 |  | 5.5 | 0.99 | 6.54 | 6.61 | 6.67 | 6.74 | 6.8 | 2.37 | 517
Forbes | Condobolin | 66/22 | 16 | 8.8/10 |  | 11 | -0.611 | 3.51 | 3.66 | 3.81 | 3.95 | 4.09 | 4.79 | 8
Forbes | Forbes Town | 66/11 | 18/30 | 15/30 |  | 33 | -0.826 | 5.64 | 5.97 | 6.29 | 6.59 | 6.88 | 9.04 | 10
Forbes | Lake Cargelligo | 66/22 | 8 | 7 |  | 7.7 | -0.647 | 2.02 | 2.1 | 2.17 | 2.24 | 2.31 | 3.05 | 18
Forbes | Paytens Bridge | 66/11 | 5 | 5/6.25 |  | 5.5 | -0.123 | 1.05 | 1.11 | 1.17 | 1.22 | 1.27 | 1.3 | 2
Forbes | West Jemalong | 66/11 | 3/4 | 3/4 |  | 4.4 | 1 | 0.37 | 0.4 | 0.42 | 0.44 | 0.47 | 0.51 | 4
Moruya North | Batemans Bay | 132/11 | 30/45 | 30/45 |  | 49.5 | -0.994 | 10.35 | 11.06 | 11.72 | 12.35 | 12.94 | 14.46 | 43
Moruya North | Bodalla | 33/11 | 3/4 | 3 |  | 3.3 | -0.931 | 1.04 | 1.1 | 1.17 | 1.23 | 1.29 | 1.37 | 18
Moruya North | Moruya North | 132/33 | 40 | 30/45 |  | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moruya North | Moruya Town | 33/11 | 10/16 | 10/16 |  | 17.6 | -0.901 | 4.64 | 4.96 | 5.26 | 5.54 | 5.81 | 6.78 | 49
Moruya North | Mossy Point | 33/11 | 10/12.5 | 12.5 |  | 13.75 | -0.984 | 6.1 | 6.55 | 6.96 | 7.36 | 7.73 | 8.36 | 76
Moruya North | Narooma | 33/11 | 10/16 | 10/12.5 |  | 13.75 | -0.699 | 4.21 | 4.5 | 4.78 | 5.04 | 5.29 | 5.55 | 36
Moruya North | Tuross | 33/11 | 5/8 |  |  | 0 | -0.96 | 2.2 | 2.36 | 2.51 | 2.65 | 2.78 | 2.82 | 49
Cooma | Adaminaby 11kV | 66/33/11 | 8/10 |  | 5 | 5.5 | -0.952 | 0.53 | 0.57 | 0.6 | 0.63 | 0.66 | 0.75 | 61
Cooma | Adaminaby 33kV | 66/33/11 |  | 5 |  | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooma | Cooma 66/11kV | 66/11 | 15/20 | 15/20 |  | 22 | -0.445 | 5.44 | 5.69 | 5.93 | 6.17 | 6.39 | 7.3 | 33
Cooma | Eucumbene | 66/11 | 3 |  |  | 0 | -0.903 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09 | 0.08 | 25
Cooma | Jindabyne 11kV | 66/33/11 | 15/30 | 15/30 |  | 33 | 0.344 | 3.77 | 3.98 | 4.18 | 4.36 | 4.54 | 4.12 | 46
Cooma | Jindabyne 33kV | 66/33/11 | 15 |  |  | 0 | -1 | 0.19 | 0.21 | 0.22 | 0.24 | 0.25 | 0.3 | 15
Cooma | Jindabyne East | 66/11 | 8/10 | 8/10 |  | 11 | -0.976 | 2.33 | 2.51 | 2.67 | 2.83 | 2.97 | 2.89 | 50
Cooma | Providence Portal | 33/11 | 0.5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Munyang | Blue Cow | 33/11 | 5/8 |  |  | 0 | 0.9 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 5
Munyang | Bullocks Flat | 33/11 | 5/6.25 |  |  | 0 | 0.955 | 0.2 | 0.22 | 0.23 | 0.25 | 0.26 | 0.19 | 32
Munyang | Bullocks Portal | 33/11 | 5/6.25 |  |  | 0 | 1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 9
Munyang | Perisher | 33/11 | 8/10 | 8/10 |  | 11 | 0.95 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14 | 0.14 | 36
Munyang | Snowy Adit 11kV | 132/66/11 | 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Munyang | Snowy Adit 66kV | 132/66/11 | 30 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Munyang | Thredbo | 33/11 | 10/16 | 10/16 |  | 17.6 | 0.984 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.03 | 1
Bega | Bega 132kV | 132/66 | 35/60 | 35/60 |  | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Bermagui | 33/11 | 5 | 5 |  | 5.5 | -0.928 | 2.19 | 2.35 | 2.5 | 2.64 | 2.77 | 3.23 | 113
Bega | Brogo | 33/11 | 3 |  |  | 0 | 0.711 | 0.4 | 0.43 | 0.45 | 0.48 | 0.5 | 0.66 | 44
Bega | Cobargo | 33/11 | 3 | 2.5 |  | 2.75 | -0.964 | 1.4 | 1.48 | 1.56 | 1.64 | 1.71 | 2.15 | 20
Bega | Eden South | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.109 | 2.36 | 2.51 | 2.66 | 2.79 | 2.93 | 5.98 | 43
Bega | Edrom | 66/11 | 5 | 5 |  | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Maher Street 66/33kV | 66/33 | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bega | Maher Street 66/11kV | 66/11 | 24/30 | 24/30 |  | 33 | 0.187 | 6.91 | 7.29 | 7.65 | 7.99 | 8.32 | 10.65 | 36
Bega | Pambula | 66/11 | 10/13/16 | 10/13/16 |  | 17.6 | -0.931 | 8.48 | 9.07 | 9.62 | 10.14 | 10.63 | 12.51 | 142
Bega | Quira | 66/11 | 5 |  |  | 0 | 0.009 | 0.77 | 0.83 | 0.89 | 0.94 | 0.99 | 1.12 | 39
Steeple Flat | Bombala | 66/22 | 10/16 | 10/13 |  | 14.3 | 0.354 | 1.09 | 1.17 | 1.24 | 1.31 | 1.37 | 1.69 | 78
Steeple Flat | Steeple Flat 132/66kV | 132/66 | 30 |  |  | 0 | 0.816 | 4.61 | 4.61 | 4.61 | 4.61 | 4.61 | 0 | 238
Steeple Flat | Steeple Flat 22kV | 11/22 | 5 |  |  | 0 | 0.329 | 0.31 | 0.33 | 0.35 | 0.37 | 0.39 | 0.45 | 23
Tumut | Adelong | 66/11 | 3 | 2.5 |  | 2.75 | -0.974 | 1.03 | 1.08 | 1.13 | 1.18 | 1.23 | 1.52 | 6
Tumut | Batlow | 66/11 | 5 | 5 |  | 5.5 | -0.707 | 0.96 | 1.02 | 1.07 | 1.12 | 1.17 | 1.37 | 13
Tumut | Gundagai South | 66/11 | 8 | 8 |  | 8.8 | -0.447 | 2.26 | 2.37 | 2.48 | 2.58 | 2.68 | 3.92 | 25
Tumut | Nangus | 66/11 | 1 | 2.8 |  | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 0
Tumut | Parsons Creek | 66/11 | 3 |  |  | 0 | 0.394 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.09 | 3
Tumut | Talbingo | 66/11 | 3.5 |  |  | 0 | -0.301 | 0.82 | 0.85 | 0.89 | 0.93 | 0.96 | 0.41 | 3
Tumut | Tumbarumba | 66/22 | 10/12.5 | 8 |  | 8.8 | 0.619 | 2.58 | 2.69 | 2.8 | 2.91 | 3.01 | 3.63 | 65
Tumut | Tumut | 66/11 | 30 | 18/30 |  | 33 | 0.891 | 5.06 | 5.36 | 5.64 | 5.91 | 6.16 | 7.5 | 34
Queanbeyan | Bungendore | 66/11 | 7.5/10 | 7.5/10 |  | 11 | -1 | 6.9 | 7.35 | 7.77 | 8.17 | 8.55 | 9.87 | 55
Queanbeyan | Captains Flat | 66/22 | 8/11 | 5 |  | 5.5 | -0.841 | 2.54 | 2.71 | 2.88 | 3.03 | 3.18 | 3.77 | 71
Queanbeyan | Googong Dam | 66/11 | 8/10 | 7.5/10 |  | 11 | 0.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queanbeyan | Googong Town | 132/11 | 30 | 30 |  | 33 | -0.994 | 10.94 | 11.79 | 12.58 | 13.32 | 14.03 | 14.31 | 78
Queanbeyan | Oaks Estate | 66/11 | 20/30 | 20/30 |  | 33 | -0.997 | 7.32 | 7.85 | 8.35 | 8.82 | 9.27 | 9.49 | 28
Queanbeyan | Queanbeyan South | 66/11 | 20/25/30 | 20/25/30 |  | 33 | -0.999 | 14.75 | 15.85 | 16.87 | 17.83 | 18.74 | 19.97 | 83
Queanbeyan | South Jerrabomberra | 132/11 | 30/40/50 | 30/40/50 |  | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queanbeyan | Sutton | 66/11 | 8 | 6.5/8 |  | 8.8 | -0.991 | 3.03 | 3.22 | 3.4 | 3.57 | 3.74 | 5.21 | 58
Goulburn | Brisbane Grove | 33/22 | 2.5 | 2.5 |  | 2.75 | -0.629 | 1.65 | 1.76 | 1.86 | 1.96 | 2.05 | 2.76 | 58
Goulburn | Clinton Street | 66/11 | 15/19 | 20/23/30 |  | 20.9 | 0.908 | 6.37 | 6.81 | 7.22 | 7.62 | 7.99 | 8.8 | 37
Goulburn | Crookwell | 66/11 | 7.5/10 | 7.5/10 |  | 11 | -0.541 | 2.92 | 3.09 | 3.24 | 3.39 | 3.53 | 4.76 | 67
Goulburn | Goulburn 132/33kV | 132/33 | 15/22.5/30 | 30/36 |  | 33 | -0.52 | 3.64 | 3.88 | 4.12 | 4.34 | 4.55 | 4.44 | 4
Goulburn | Goulburn 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 1 | 7.68 | 7.68 | 7.68 | 7.68 | 7.68 | 0 | 112
Goulburn | Goulburn North | 66/11 | 15 | 12.5/16 |  | 16.5 | -0.97 | 6.44 | 6.79 | 7.12 | 7.44 | 7.74 | 8.67 | 71
Goulburn | Marulan North | 66/22 | 12.5/15 | 12.5/15 |  | 16.5 | 0.983 | 2.2 | 2.37 | 2.52 | 2.67 | 2.8 | 3.07 | 38
Goulburn | Marulan South | 66/33 | 10/16 |  |  | 0 | 0.969 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 1
Goulburn | Woodlawn | 66/11 | 10/14 | 24/30 |  | 15.4 | 0.656 | 4.48 | 4.54 | 4.6 | 4.65 | 4.71 | 1.58 | 363
Cowra | Bendick Murrell | 66/11 | 2.8 |  |  | 0 | -0.863 | 1.13 | 1.18 | 1.23 | 1.28 | 1.33 | 1.48 | 5
Cowra | Canowindra | 66/11 | 5 | 8 |  | 5.5 | -0.721 | 2.61 | 2.79 | 2.96 | 3.12 | 3.27 | 3.95 | 77
Cowra | Cowra | 66/11 | 15/30 | 15/30 |  | 33 | -0.84 | 8.68 | 9.25 | 9.78 | 10.28 | 10.76 | 11.81 | 24
Cowra | Grenfell | 66/11 | 8 | 5 |  | 5.5 | 0.95 | 2.9 | 3.1 | 3.28 | 3.45 | 3.62 | 4.39 | 28
Cowra | Monteagle | 66/11 | 1 |  |  | 0 | -0.534 | 0.43 | 0.44 | 0.46 | 0.47 | 0.49 | 0.68 | 23
Harden - Murrumburrah | Boorowa | 66/11 | 8 | 5 |  | 5.5 | -0.955 | 2.07 | 2.17 | 2.27 | 2.37 | 2.46 | 3.22 | 9
Harden - Murrumburrah | Cootamundra | 66/11 | 15/19 | 15/19 |  | 20.9 | -0.899 | 13.22 | 13.82 | 14.38 | 14.91 | 15.42 | 8 | 4
Harden - Murrumburrah | Jugiong | 66/11 | 5.9/6.5 | 5.9/6.5 |  | 7.15 | 0.917 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31 | 0.41 | 12
Harden - Murrumburrah | Murrumburrah | 66/11 | 8/10 | 8/10 |  | 11 | -0.859 | 2.61 | 2.78 | 2.93 | 3.07 | 3.21 | 3.99 | 4
Harden - Murrumburrah | Young | 66/11 | 24/30 | 18/30 |  | 33 | -0.725 | 7.43 | 7.87 | 8.28 | 8.68 | 9.06 | 11.03 | 8
Yass | Gunning | 22/11 | 2.5 | 2.5 |  | 2.75 | 0.986 | 0.86 | 0.91 | 0.95 | 0.99 | 1.03 | 1.36 | 14
Yass | Marilba | 66/11 | 3 |  |  | 0 | 0.963 | 0.93 | 0.99 | 1.05 | 1.1 | 1.15 | 1.37 | 53
Yass | Murrumbateman | 132/22 | 10/12.5 |  |  | 0 | -0.992 | 5.89 | 6.28 | 6.66 | 7.01 | 7.35 | 9.77 | 73
Yass | Yass | 66/22 | 10/13 | 10/13 |  | 14.3 | -0.995 | 7.21 | 7.65 | 8.07 | 8.47 | 8.85 | 9.54 | 48
Temora | Anona | 66/22 | 3 | 2.5 |  | 2.75 | -0.593 | 0.61 | 0.65 | 0.68 | 0.71 | 0.74 | 1.02 | 52
Temora | Ardlethan | 66/11 | 2.5 | 3 |  | 2.75 | -0.904 | 0.4 | 0.43 | 0.45 | 0.47 | 0.49 | 0.65 | 15
Temora | Ariah Park | 66/11 | 3 | 3 |  | 3.3 | -0.984 | 0.48 | 0.52 | 0.55 | 0.58 | 0.61 | 0.77 | 27
Temora | Junee Reefs | 66/11 | 3 |  |  | 0 | -0.931 | 0.14 | 0.14 | 0.15 | 0.15 | 0.15 | 0.17 | 5
Temora | Temora 132/66kV | 132/66 | 35/60 | 35/60 |  | 66 | 0.621 | 2.88 | 2.88 | 2.88 | 2.88 | 2.88 | 0 | 34
Temora | Temora 66/11kV | 66/11 | 6.75/10 | 10/12.5 |  | 11 | -0.376 | 6.65 | 6.92 | 7.18 | 7.42 | 7.65 | 6.19 | 10
Temora | West Wyalong | 66/22 | 8/10 | 10/12.5 |  | 11 | -0.995 | 4.09 | 4.3 | 4.51 | 4.71 | 4.9 | 5.67 | 5
Wagga North | Bethungra | 66/11 | 3 | 3 |  | 3.3 | 0.988 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24 | 0.3 | 9
Wagga North | Bomen | 66/11 | 20/30 | 20/30 |  | 33 | 0.837 | 2.27 | 2.29 | 2.3 | 2.31 | 2.32 | 0.34 | 12
Wagga North | Cartwrights Hill 11kV | 66/11 | 6.75/8 | 6.75/8 |  | 8.8 | -0.992 | 4.24 | 4.52 | 4.79 | 5.04 | 5.28 | 5.32 | 21
Wagga North | Cartwrights Hill 33kV | 11/33 | 5 | 4 |  | 4.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wagga North | Coolamon | 66/11 | 8 | 8 |  | 8.8 | -0.847 | 2.65 | 2.82 | 2.98 | 3.14 | 3.29 | 4.55 | 30
Wagga North | Euberta | 33/11 | 4 | 3 |  | 3.3 | 0.331 | 0.41 | 0.43 | 0.46 | 0.48 | 0.5 | 0.81 | 12
Wagga North | Forest Hill | 66/11 | 12.5/16 | 10/14 |  | 15.4 | 0.386 | 2.05 | 2.19 | 2.32 | 2.44 | 2.55 | 2.68 | 18
Wagga North | Ganmurra | 33/11 | 2.5 |  |  | 0 | 0.723 | 0.18 | 0.19 | 0.2 | 0.21 | 0.22 | 0.26 | 19
Wagga North | Junee 11kV | 66/11 | 10/18 | 10/15 |  | 16.5 | -0.889 | 2.71 | 2.84 | 2.96 | 3.08 | 3.19 | 4.08 | 5
Wagga North | Junee 66kV | 132/66 | 30 |  |  | 0 | 0.777 | 31.57 | 31.57 | 31.57 | 31.57 | 31.57 | 0 | 21
Wagga North | Mates Gully | 33/11 | 2 |  |  | 0 | 0.697 | 0.28 | 0.29 | 0.31 | 0.32 | 0.33 | 0.42 | 4
Wagga North | Oura 11/33kV | 11/33 | 4 | 2 |  | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wagga North | Oura 66/11kV | 66/11 | 5/6.9 | 5/6.9 |  | 7.59 | 0.791 | 0.34 | 0.36 | 0.38 | 0.4 | 0.42 | 0.61 | 11
Wagga North | Tarcutta | 33/11 | 1 | 3 |  | 1.1 | 0.721 | 0.45 | 0.47 | 0.49 | 0.51 | 0.53 | 0.8 | 17
Wagga (Copland St) | Ashmont | 66/11 | 20/30 | 20/30 |  | 33 | -0.725 | 7.73 | 8.31 | 8.84 | 9.35 | 9.83 | 10.44 | 13
Wagga (Copland St) | Bourkelands | 66/11 | 10/13.3 | 10/13.3 |  | 14.63 | -1 | 7.52 | 8.05 | 8.55 | 9.02 | 9.47 | 10.28 | 54
Wagga (Copland St) | Bulgary | 66/22 | 2.5 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4
Wagga (Copland St) | Hammond Ave | 66/11 | 24/30 | 24/30 |  | 33 | 0.831 | 3.66 | 3.84 | 4.02 | 4.19 | 4.36 | 4.9 | 6
Wagga (Copland St) | Henty | 66/11 | 5 | 5 |  | 5.5 | -0.891 | 1.3 | 1.35 | 1.41 | 1.46 | 1.51 | 2.12 | 46
Wagga (Copland St) | Kooringal | 66/11 | 18/25 | 18/25 |  | 27.5 | -0.978 | 9.06 | 9.68 | 10.26 | 10.81 | 11.34 | 12.96 | 23
Wagga (Copland St) | Lockhart | 66/22 | 8 | 5 |  | 5.5 | -0.716 | 1.59 | 1.66 | 1.73 | 1.8 | 1.86 | 2.5 | 28
Wagga (Copland St) | Morrow St | 66/11 | 20 | 20 |  | 22 | 0.983 | 1.58 | 1.68 | 1.77 | 1.85 | 1.93 | 2.53 | 6
Wagga (Copland St) | Uranquinty | 66/22 | 10/16 | 10/16 |  | 17.6 | 0.179 | 2.31 | 2.46 | 2.6 | 2.73 | 2.85 | 3.55 | 33
Morven | Culcairn | 66/11 | 5/7 | 8 |  | 7.7 | -0.929 | 2.49 | 2.6 | 2.71 | 2.81 | 2.91 | 3.85 | 15
Morven | Holbrook | 66/22 | 5/7 | 5/7 |  | 7.7 | -0.973 | 1.87 | 1.96 | 2.05 | 2.13 | 2.21 | 3.16 | 65
Morven | Morven | 132/66 | 30 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Albury | Corowa | 132/22 | 30 | 27/30 |  | 33 | 0.355 | 39.72 | 39.98 | 40.23 | 40.46 | 40.69 | 9.52 | 11
Albury | Jelbart | 132/22 | 30/44 | 30/44 |  | 48.4 | 0.878 | 9.58 | 10.24 | 10.85 | 11.44 | 12 | 18.31 | 37
Albury | Mulwala | 132/22 | 30 | 30 |  | 33 | 0.58 | 9.62 | 9.89 | 10.15 | 10.39 | 10.63 | 6.96 | 43
Albury | Union Rd | 132/22 | 30 | 30/40 | 30/44 | 77 | -0.987 | 33.2 | 35.48 | 37.62 | 39.64 | 41.56 | 49.36 | 102
Finley | Finley Town | 66/22 | 24/30 | 24/30 |  | 33 | -0.811 | 8.05 | 8.34 | 8.62 | 8.88 | 9.14 | 10.4 | 35
Finley | Jerilderie | 66/22 | 8.8/10 | 8.8/10 |  | 11 | 0.73 | 6.04 | 6.12 | 6.19 | 6.26 | 6.32 | 2.21 | 26
Deniliquin | Barham | 66/22 | 10/16 | 10 |  | 11 | -0.759 | 2.76 | 2.86 | 2.96 | 3.06 | 3.15 | 3.98 | 8
Deniliquin | Deniliquin | 66/22 | 18/30 | 18/30 |  | 33 | -0.928 | 8.79 | 9.32 | 9.83 | 10.31 | 10.77 | 12.31 | 27
Deniliquin | Koraleigh | 66/22 | 8/11 | 5 |  | 5.5 | 1 | 1.38 | 1.43 | 1.49 | 1.53 | 1.58 | 2.85 | 15
Deniliquin | Moama | 66/22 | 24/30 | 24/30 |  | 33 | -0.939 | 10.63 | 11 | 11.35 | 11.68 | 12 | 9.13 | 47
Deniliquin | Moulamein | 66/22 | 8/11 | 5 |  | 5.5 | -0.483 | 0.69 | 0.7 | 0.72 | 0.73 | 0.74 | 1.04 | 31
Deniliquin | Murgha | 66/22 | 1 |  |  | 0 | 0.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coleambally | Coleambally 132kV | 132/33 | 17.5/25 | 25 |  | 27.5 | 0.917 | 5.38 | 5.39 | 5.4 | 5.41 | 5.42 | 0.42 | 55
Coleambally | Coleambally 33/11kV | 33/11 | 7.5 | 7.5 |  | 8.25 | 0.49 | 0.52 | 0.54 | 0.56 | 0.58 | 0.59 | 0.86 | 17
Coleambally | Darlington Point | 33/11 | 10/12.5 | 10/14 |  | 13.75 | -0.236 | 0.96 | 1.01 | 1.06 | 1.11 | 1.15 | 1.14 | 8
Coleambally | Egansford | 33/11 | 2.5 | 5 |  | 2.75 | 1 | 0.09 | 0.1 | 0.1 | 0.11 | 0.11 | 0.12 | 5
Coleambally | Ringwood Road | 33/11 | 5 |  |  | 0 | 0.707 | 0.31 | 0.31 | 0.32 | 0.33 | 0.33 | 0.51 | 14
Darlington Point | Carrathool | 33/11 | 1.5 | 1.5 |  | 1.65 | 0.788 | 0.25 | 0.26 | 0.27 | 0.29 | 0.3 | 0.22 | 4
Darlington Point | Hay 132kV | 132/33 | 24/30 | 30/36 |  | 33 | 0.943 | 0.81 | 0.82 | 0.84 | 0.85 | 0.86 | 1.11 | 14
Darlington Point | Hay Town | 33/11 | 8/11 | 8/10 |  | 11 | -0.936 | 2.46 | 2.6 | 2.74 | 2.86 | 2.98 | 3.66 | 21
Darlington Point | Hillston | 132/33 | 30 | 12/16 |  | 17.6 | 0.975 | 3.01 | 3.18 | 3.34 | 3.49 | 3.64 | 3.32 | 6
Darlington Point | Ivanhoe | 33/11 | 1 | 1 |  | 1.1 | 0.439 | 0.28 | 0.3 | 0.32 | 0.34 | 0.36 | 0.38 | 15
Griffith | Beelbangera | 33/11 | 10/12.5 | 10/12.5 |  | 13.75 | -0.994 | 4.8 | 5.1 | 5.39 | 5.66 | 5.92 | 6.4 | 92
Griffith | Griffith | 33/11 | 40/50 | 40/50 |  | 55 | -0.605 | 8.78 | 9.21 | 9.63 | 10.03 | 10.41 | 10.41 | 5
Griffith | Hanwood | 33/11 | 15/17/25 | 15/17/25 |  | 27.5 | 1 | 1.9 | 1.95 | 2.01 | 2.06 | 2.11 | 1.94 | 2
Griffith | Nericon | 33/11 | 5/8 |  |  | 0 | 0.874 | 0.41 | 0.42 | 0.43 | 0.44 | 0.45 | 0.54 | 6
Griffith | Tharbogang | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | -0.995 | 6.15 | 6.46 | 6.76 | 7.04 | 7.31 | 6.53 | 8
Griffith | Warrawidgee | 33/11 | 2.5 | 3 |  | 2.75 | 0.389 | 0.29 | 0.29 | 0.29 | 0.3 | 0.3 | 0.23 | 4
Griffith | Widgelli | 33/11 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Griffith | Willbriggie | 33/11 | 5/8 |  |  | 0 | 0.997 | 0.31 | 0.33 | 0.36 | 0.38 | 0.4 | 0.33 | 6
Griffith | Yenda | 33/11 | 7.5/9.5 | 7.5/9.5 |  | 10.45 | 0.962 | 1.61 | 1.69 | 1.76 | 1.82 | 1.89 | 1.79 | 12
Yanco | Kywong | 66/11 | 3 |  |  | 0 | 0.861 | 0.11 | 0.12 | 0.12 | 0.13 | 0.14 | 0.15 | 6
Yanco | Leeton | 33/11 | 15/20/25 | 15/20/25 |  | 27.5 | 0.629 | 6.78 | 7.15 | 7.49 | 7.83 | 8.14 | 9.13 | 13
Yanco | Murrami | 33/11 | 5 | 5 |  | 5.5 | -0.825 | 0.32 | 0.32 | 0.33 | 0.34 | 0.34 | 0.45 | 17
Yanco | Narrandera | 66/11 | 10/16 | 10/16 |  | 17.6 | 0.594 | 6.51 | 6.69 | 6.87 | 7.03 | 7.19 | 5.93 | 18
Yanco | Whitton | 33/11 | 5/6.25 | 5/6.25 |  | 6.88 | -0.071 | 0.79 | 0.83 | 0.87 | 0.9 | 0.94 | 0.93 | 8
Yanco | Yanco 33/11kV | 33/11 | 5 |  |  | 0 | -0.91 | 1.19 | 1.26 | 1.32 | 1.38 | 1.43 | 1.71 | 30
Yanco | Yanco 33/66kV | 33/66 | 15 |  |  | 0 | 0.667 | 3.86 | 3.91 | 3.96 | 4 | 4.04 | 0.96 | 152
Buronga | Powercor Robinvale 22kV Euston Distribution Supply |  |  |  |  | 0 | 0.983 | 1.38 | 1.4 | 1.42 | 1.44 | 1.46 | 1.33 | 21
Buronga | TransGrid 220/22kV Total Balranald 22kV Supply |  |  |  |  | 0 | 0.258 | 1.62 | 1.63 | 1.65 | 1.67 | 1.68 | 1.34 | 51
Buronga | Buronga Town | 66/22 | 20/30 | 20/30 |  | 33 | 0.944 | 4.13 | 4.36 | 4.58 | 4.79 | 5 | 5.79 | 86
Buronga | Dareton | 66/22 | 24/30 | 24/30 |  | 33 | 0.954 | 5.83 | 6.03 | 6.22 | 6.4 | 6.57 | 4.55 | 11
Buronga | Ellerslie | 66/22 | 8 |  |  | 0 | 0.918 | 0.5 | 0.51 | 0.53 | 0.55 | 0.57 | 0.65 | 20
Buronga | Ginkgo | 66/22 | 12.5/16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Buronga | Snapper | 66/22 | 10/16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Lines Export
Supply Area | Feeder # | Feeder Voltage kV | Feeder Origin | Feeder Destination
[5 empty] | Line Rating | Line Forecast MW
[5 empty] | Summer MVA | 2026 | 2027 | 2028 | 2029 | 2030
Casino | 96L | 132 | Transgrid Casino 132kV 96L Tee | Casino ZS | 140 | 12.54 | 13.22 | 13.86 | 14.47 | 15.05
Casino | 6501 | 66 | Casino ZS | Rappville Tee | 16 | 0.43 | 0.46 | 0.48 | 0.5 | 0.53
Casino | 8401 | 33 | Casino ZS | Mallanganee ZS | 4 | 1.43 | 1.49 | 1.57 | 1.63 | 1.69
Casino | 8402 | 33 | Mallanganee ZS | Bonalbo ZS | 4 | 1.02 | 1.07 | 1.12 | 1.16 | 1.21
Casino | 8403 | 33 | Bonalbo ZS | Urbenville ZS | 4 | 0.51 | 0.54 | 0.57 | 0.59 | 0.62
Coffs Harbour | 96C/2(D) | 132 | TransGrid 96C Armidale Coffs Harbour Dorrigo Tee | Dorrigo ZS | 41 | 1.72 | 1.81 | 1.9 | 1.99 | 2.07
Coffs Harbour | 702 | 66 | Boambee South 132/66kV STS | Sawtell ZS | 61 | 6.11 | 6.54 | 6.94 | 7.32 | 7.68
Coffs Harbour | 705 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 9.39 | 10.02 | 10.61 | 11.17 | 11.7
Coffs Harbour | 706 | 66 | TransGrid Coffs Harbour 132/66 kV STS | South Coffs ZS | 52 | 10.7 | 11.41 | 12.08 | 12.72 | 13.32
Coffs Harbour | 7501 | 66 | Nana Glen ZS | Woolgoolga ZS | 29 | 3.5 | 3.74 | 3.96 | 4.17 | 4.36
Coffs Harbour | 7502 | 66 | Nana Glen ZS | Ulong Tee | 9 | 0.37 | 0.4 | 0.43 | 0.46 | 0.48
Coffs Harbour | 7502/1 | 66 | Ulong Tee | Ulong ZS | 9 | 0.37 | 0.4 | 0.43 | 0.46 | 0.48
Coffs Harbour | 7502/2 | 66 | Ulong Tee | Dorrigo ZS | 9 | 0 | 0 | 0 | 0 | 0
Coffs Harbour | 7509 | 66 | Moonee ZS | Woolgoolga ZS | 30 | 10.32 | 11.02 | 11.69 | 12.32 | 12.91
Coffs Harbour | 7510 | 66 | North Coffs ZS | Moonee ZS | 61 | 4.55 | 4.85 | 5.14 | 5.41 | 5.66
Coffs Harbour | 703:NGN | 66 | TransGrid Coffs Harbour 132/66 kV STS | Nana Glen ZS | 62 | 5.74 | 6.12 | 6.48 | 6.82 | 7.15
Coffs Harbour | 711:CHN | 66 | TransGrid Coffs Harbour 132/66 kV STS | North Coffs ZS | 62 | 11.55 | 12.33 | 13.05 | 13.74 | 14.39
Coffs Harbour | 87C | 66 | North Coffs ZS | South Coffs ZS | 68 | 7.23 | 7.71 | 8.17 | 8.6 | 9.01
Grafton | 825 | 66 | TransGrid Koolkhan 132/66kV STS | Koolkhan ZS | 62 | 12.85 | 13.59 | 14.29 | 14.96 | 15.59
Grafton | 826 | 66 | TransGrid Koolkhan 132/66kV STS | Grafton North ZS | 61 | 10.49 | 11.09 | 11.66 | 12.2 | 12.72
Grafton | 6503 | 66 | Grafton North ZS | South Grafton ZS | 24 | 6.85 | 7.24 | 7.62 | 7.97 | 8.31
Grafton | 6504 | 66 | Five Mile Sw Stn | South Grafton ZS | 61 | 2.97 | 3.14 | 3.3 | 3.45 | 3.6
Grafton | 6505 | 66 | Koolkhan SS | Grafton ZS | 52 | 11.41 | 12.06 | 12.68 | 13.27 | 13.84
Grafton | 6506 | 66 | Shannon Creek ZS | Nymboida ZS | 14 | 0.18 | 0.19 | 0.2 | 0.21 | 0.21
Grafton | 6508 | 66 | Maclean ZS | Yamba ZS | 28 | 8.39 | 8.93 | 9.43 | 9.91 | 10.37
Grafton | 6509 | 66 | Shannon Creek ZS | Five Mile Sw Stn | 14 | 0.81 | 0.86 | 0.9 | 0.95 | 0.99
Grafton | 6510 | 66 | Grafton North ZS | Five Mile Sw Stn | 28 | 3.71 | 3.92 | 4.12 | 4.31 | 4.5
Grafton | 896:MLN | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 21 | 6.11 | 6.46 | 6.79 | 7.11 | 7.41
Grafton | 8G1 | 66 | TransGrid Koolkhan 132/66kV STS | Maclean ZS | 68 | 7.84 | 8.29 | 8.72 | 9.12 | 9.51
Grafton | 6402 | 33 | Maclean ZS | Yamba Tee | 8 | 0.32 | 0.34 | 0.35 | 0.37 | 0.39
Grafton | 6403 | 33 | Yamba Tee | Redcliff ZS | 3 | 0.32 | 0.34 | 0.35 | 0.37 | 0.39
Grafton | 6404 | 33 | Yamba Tee | Yamba ZS | 10 | 0 | 0 | 0 | 0 | 0
Hawks Nest | 7Y1 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 3.05 | 3.24 | 3.42 | 3.59 | 3.75
Hawks Nest | 7Y2 | 33 | Hawks Nest 132/33kV STS | Tea Gardens ZS | 7 | 2.79 | 2.97 | 3.14 | 3.29 | 3.44
Hawks Nest | 7V1 | 33 | Ausgrid Salt Ash ZS | Tee with 7Y1 | 7 | 0 | 0 | 0 | 0 | 0
Herons Creek | 866:KEW | 66 | Herons Creek 132/66kV STS | Kew ZS | 16 | 9.06 | 9.57 | 10.06 | 10.52 | 10.97
Herons Creek | 871 | 66 | Kew ZS | Laurieton ZS | 36 | 6.16 | 6.51 | 6.84 | 7.16 | 7.47
Herons Creek | 862/1 | 66 | Kew ZS | Johns River ZS | 16 | 0.52 | 0.55 | 0.57 | 0.59 | 0.61
Herons Creek | 862/2 | 66 | TransGrid Taree 132/66/33kV STS | Johns River ZS | 16 | 0 | 0 | 0 | 0 | 0
Kempsey | 7R1 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 30 | 4.21 | 4.49 | 4.76 | 5.01 | 5.25
Kempsey | 7R2/1 | 33 | TransGrid Kempsey 132/33kV STS | North St Tee | 26 | 4.87 | 5.2 | 5.51 | 5.79 | 6.07
Kempsey | 7R2/2 | 33 | North St Tee | Smithtown ZS | 19 | 2.44 | 2.6 | 2.75 | 2.9 | 3.04
Kempsey | 7R2/3 | 33 | North St Tee | North St ZS | 10 | 2.4 | 2.56 | 2.71 | 2.85 | 2.99
Kempsey | 7R3 | 33 | TransGrid Kempsey 132/33kV STS | Prince St ZS | 26 | 4.23 | 4.51 | 4.78 | 5.03 | 5.27
Kempsey | 7R4 | 33 | TransGrid Kempsey 132/33kV STS | Munga ZS | 3 | 0.95 | 1.01 | 1.06 | 1.12 | 1.17
Kempsey | 7R5 | 33 | TransGrid Kempsey 132/33kV STS | North St ZS | 19 | 3.69 | 3.94 | 4.17 | 4.39 | 4.6
Kempsey | 7R6/1 | 33 | Prince St ZS | South West Rocks Tee | 15 | 3.08 | 3.29 | 3.48 | 3.66 | 3.84
Kempsey | 7R6/2 | 33 | South West Rocks Tee | South West Rocks ZS | 19 | 1.56 | 1.66 | 1.76 | 1.85 | 1.94
Kempsey | 7R6/3 | 33 | South West Rocks Tee | Smithtown ZS | 19 | 1.45 | 1.55 | 1.64 | 1.73 | 1.81
Kempsey | 7R7 | 33 | Prince St ZS | Crescent Head ZS | 5 | 1.16 | 1.23 | 1.3 | 1.37 | 1.43
Kempsey | 7R8 | 33 | Smithtown ZS | South West Rocks ZS | 30 | 1.84 | 1.97 | 2.08 | 2.19 | 2.3
Lismore | 9U8 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 183 | 44.21 | 46.31 | 48.29 | 50.18 | 51.99
Lismore | 9U9 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 40.91 | 42.85 | 44.69 | 46.44 | 48.11
Lismore | 9W1 | 132 | TransGrid Lismore 330/132 STS | Lismore 132/66kV STS | 128 | 37.86 | 39.66 | 41.35 | 42.98 | 44.52
Lismore | 9G2 | 132 | Ballina ZS | Lennox Head ZS | 124 | 9.77 | 10.23 | 10.67 | 11.09 | 11.49
Lismore | 9G3 | 132 | Lennox Head ZS | Suffolk Park ZS | 124 | 13.07 | 13.69 | 14.27 | 14.83 | 15.37
Lismore | 9G4 | 132 | Suffolk Park ZS | Ewingsdale ZS | 124 | 18.2 | 19.06 | 19.88 | 20.66 | 21.4
Lismore | 9G5 | 132 | Ewingsdale ZS | Mullumbimby ZS | 122 | 31.75 | 33.26 | 34.68 | 36.04 | 37.34
Lismore | 9U6 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 58.62 | 61.4 | 64.03 | 66.54 | 68.94
Lismore | 9U6/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 47.63 | 49.89 | 52.03 | 54.07 | 56.01
Lismore | 9U7 | 132 | Lismore 132/66kV STS | Dunoon ZS | 107 | 61.06 | 63.96 | 66.7 | 69.32 | 71.81
Lismore | 9U7/1 | 132 | Dunoon ZS | Mullumbimby ZS | 107 | 50.07 | 52.45 | 54.69 | 56.84 | 58.88
Lismore | 892 | 66 | Lismore 132/66kV STS | Woodburn ZS | 11 | 5.29 | 5.6 | 5.9 | 6.18 | 6.44
Lismore | 893 | 66 | Lismore 132/66kV STS | Casino ZS | 34 | 0 | 0 | 0 | 0 | 0
Lismore | 894:LME | 66 | Lismore 132/66kV STS | Kyogle ZS | 11 | 4.5 | 4.73 | 4.96 | 5.17 | 5.37
Lismore | 0897:LME | 66 | Lismore 132/66kV STS | Alstonville ZS | 62 | 15.51 | 16.25 | 16.94 | 17.61 | 18.24
Lismore | 8502 | 66 | Lismore East ZS | Alstonville ZS | 62 | 8.18 | 8.57 | 8.94 | 9.29 | 9.62
Lismore | 8503 | 66 | Ballina ZS | Alstonville ZS | 62 | 7.21 | 7.55 | 7.87 | 8.18 | 8.47
Lismore | 8507 | 66 | Alstonville ZS | Ballina ZS | 61 | 8.3 | 8.7 | 9.07 | 9.43 | 9.77
Lismore | 8510 | 66 | Lismore Sw Stn | East Lismore ZS | 61 | 18.68 | 19.57 | 20.41 | 21.21 | 21.97
Lismore | 8511 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 16.36 | 17.14 | 17.88 | 18.58 | 19.25
Lismore | 8512 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 4.96 | 5.25 | 5.52 | 5.79 | 6.04
Lismore | 8513 | 66 | Lismore Sw Stn | Lismore University ZS | 54 | 4.96 | 5.25 | 5.52 | 5.79 | 6.04
Lismore | 8514 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 1.94 | 2.05 | 2.15 | 2.25 | 2.35
Lismore | 8515 | 66 | Lismore 132/66kV STS | South Lismore ZS | 68 | 1.84 | 1.95 | 2.05 | 2.15 | 2.25
Lismore | 8516 | 66 | Lismore 132/66kV STS | Lismore Sw Stn | 62 | 16.24 | 17.01 | 17.74 | 18.44 | 19.1
Nambucca Heads | 751 | 66 | TransGrid Nambucca 132/66 kV STS | Nambucca ZS | 15 | 5.59 | 5.97 | 6.33 | 6.66 | 6.98
Port Macquarie | 70Y | 33 | Rocks Ferry ZS | Telegraph Point ZS | 8 | 1.16 | 1.24 | 1.31 | 1.38 | 1.45
Port Macquarie | 701 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 22 | 7.42 | 7.92 | 8.39 | 8.84 | 9.26
Port Macquarie | 703:BPM | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 6.15 | 6.57 | 6.96 | 7.33 | 7.68
Port Macquarie | 707 | 33 | TransGrid Port Macquarie 132/33kV STS | Boronia Street ZS | 26 | 6.97 | 7.43 | 7.88 | 8.29 | 8.69
Port Macquarie | 708 | 33 | TransGrid Port Macquarie 132/33kV STS | Owen Street ZS | 26 | 8.09 | 8.63 | 9.14 | 9.63 | 10.09
Port Macquarie | 710 | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 31 | 8.8 | 9.39 | 9.95 | 10.47 | 10.98
Port Macquarie | 711:CPM | 33 | TransGrid Port Macquarie 132/33kV STS | Clearwater ZS | 20 | 8.75 | 9.33 | 9.89 | 10.41 | 10.91
Port Macquarie | 712 | 33 | TransGrid Port Macquarie 132/33kV STS | Rocks Ferry ZS | 12 | 4.93 | 5.26 | 5.58 | 5.87 | 6.15
Port Macquarie | 715 | 33 | Clearwater ZS | Owen Street ZS | 31 | 3.66 | 3.91 | 4.14 | 4.36 | 4.57
Port Macquarie | 719/1 | 33 | Clearwater ZS | Lake Cathie ZS | 20 | 6.44 | 6.88 | 7.29 | 7.68 | 8.05
Port Macquarie | 719/2 | 33 | Lake Cathie ZS | Laurieton ZS | 12 | 0 | 0 | 0 | 0 | 0
Port Macquarie | 765 | 33 | Rocks Ferry ZS | Koree ZS | 9 | 3.31 | 3.53 | 3.74 | 3.94 | 4.12
Port Macquarie | 784 | 33 | Koree ZS | Byabarra ZS | 9 | 0.86 | 0.92 | 0.98 | 1.03 | 1.08
Stroud | 9C9/3 | 33 | Stroud 132/33kV STS | Dungog ZS | 27 | 3.62 | 3.84 | 4.05 | 4.25 | 4.44
Stroud | 9C9/2 | 33 | Dungog ZS | Martins Creek ZS | 21 | 2.85 | 3.02 | 3.18 | 3.33 | 3.48
Stroud | STR4B3/1 | 33 | Stroud 132/33kV STS | Booral ZS | 7 | 2.39 | 2.54 | 2.68 | 2.81 | 2.94
Stroud | STR4B3/2 | 33 | Booral ZS | Bulahdelah ZS | 7 | 1.72 | 1.82 | 1.92 | 2.01 | 2.11
Stroud | STR4B4 | 33 | Stroud 132/33kV STS | Dungog ZS | 4 | 1.25 | 1.33 | 1.4 | 1.47 | 1.54
Stroud | STR4B5/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 3.4 | 3.61 | 3.8 | 3.99 | 4.17
Stroud | STR4B5/2 | 33 | Wards River Sw Stn | Stratford Tee | 19 | 1.78 | 1.89 | 1.99 | 2.09 | 2.18
Stroud | STR4B5/2a | 33 | Stratford Tee | Stratford Coal ZS | 7 | 0 | 0 | 0 | 0 | 0
Stroud | STR4B5/3 | 33 | Stratford Tee | Gloucester ZS | 19 | 1.58 | 1.69 | 1.79 | 1.89 | 1.98
Stroud | STR4B6/1 | 33 | Stroud 132/33kV STS | Wards River Sw Stn | 17 | 3.92 | 4.16 | 4.38 | 4.6 | 4.81
Stroud | STR4B6/2 | 33 | Wards River Sw Stn | Gloucester ZS | 17 | 3.08 | 3.29 | 3.48 | 3.66 | 3.83
Stroud | STR4B7 | 33 | Stroud 132/33kV STS | Dungog ZS | 7 | 1.88 | 2 | 2.1 | 2.2 | 2.3
Stroud | STR4B8 | 33 | Stroud 132/33kV STS | Bulahdelah ZS | 7 | 2.17 | 2.3 | 2.43 | 2.54 | 2.66
Stroud | 3801 | 33 | Bulahdelah ZS | Pacific Palms ZS | 7 | 2.5 | 2.66 | 2.81 | 2.95 | 3.09
Stroud | 3803 | 33 | Bulahdelah ZS | Bungwahl Sw Stn | 7 | 0 | 0 | 0 | 0 | 0
Stroud | BLH4B4 | 33 | Bulahdelah ZS | Hawks Nest 132/33kV STS | 7 | 0.12 | 0.13 | 0.14 | 0.14 | 0.15
Stroud | 7J1 | 33 | Ausgrid Recloser 33175 (Patterson) | Martins Creek Tee | 8 | 0 | 0 | 0 | 0 | 0
Stroud | 7J1/2 | 33 | Martins Creek Tee | Martins Creek ZS | 4 | 1.17 | 1.25 | 1.32 | 1.39 | 1.46
Stroud | 7J1/3 | 33 | Martins Creek Tee | Gresford ZS | 4 | 1.17 | 1.25 | 1.32 | 1.39 | 1.46
Taree | 861 | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 6.04 | 6.46 | 6.86 | 7.24 | 7.6
Taree | 863:WTE | 66 | TransGrid Taree 132/66/33kV STS | Whitbread ZS | 62 | 6.25 | 6.7 | 7.11 | 7.5 | 7.87
Taree | 867 | 66 | TransGrid Taree 132/66/33kV STS | Hallidays Point ZS | 34 | 8.48 | 9.08 | 9.64 | 10.18 | 10.68
Taree | 867/1 | 66 | Hallidays Point Tee | Tuncurry ZS | 39 | 8.48 | 9.08 | 9.64 | 10.18 | 10.68
Taree | 868/1 | 66 | TransGrid Taree 132/66/33kV STS | Bohnock Tee | 36 | 9.94 | 10.64 | 11.3 | 11.92 | 12.51
Taree | 868/2 | 66 | Bohnock Tee | Bohnock ZS | 16 | 5.25 | 5.63 | 5.98 | 6.32 | 6.63
Taree | 868/3 | 66 | Bohnock Tee | Hallidays Point ZS | 38 | 7.28 | 7.79 | 8.27 | 8.73 | 9.16
Taree | 872 | 66 | Tuncurry ZS | Forster ZS | 30 | 4.27 | 4.57 | 4.86 | 5.13 | 5.38
Taree | 86C | 66 | Tuncurry ZS | Forster ZS | 42 | 3.75 | 4.01 | 4.26 | 4.49 | 4.72
Taree | 86R | 66 | Hallidays Point ZS | Tuncurry ZS | 38 | 7.12 | 7.62 | 8.1 | 8.54 | 8.97
Taree | 7G2/1 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Tee | 22 | 2.36 | 2.5 | 2.64 | 2.78 | 2.9
Taree | 7G2/2 | 33 | Kanangra Tee | Coopernook ZS | 7 | 2.01 | 2.14 | 2.26 | 2.37 | 2.48
Taree | 7G2/3 | 33 | Coopernook ZS | Harrington ZS | 8 | 3.79 | 4.03 | 4.26 | 4.48 | 4.69
Taree | 7G4 | 33 | Bootawa ZS | Wingham ZS | 18 | 0.94 | 0.99 | 1.05 | 1.1 | 1.15
Taree | 7G5 | 33 | TransGrid Taree 132/66/33kV STS | Kanangra Dr ZS | 17 | 3.47 | 3.69 | 3.89 | 4.09 | 4.27
Taree | 7G1 | 33 | TransGrid Taree 132/66/33kV STS | Bootawa ZS | 17 | 2.53 | 2.69 | 2.84 | 2.98 | 3.12
Taree | 7G3 | 33 | TransGrid Taree 132/66/33kV STS | Wingham ZS | 18 | 2.66 | 2.83 | 2.99 | 3.14 | 3.28
Terranora | 757 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 100 | 100 | 100 | 100 | 100
Terranora | 758 | 110 | Powerlink Mudgeeraba 275/110kV STS | Terranora 110/66kV STS | 106 | 101 | 101 | 101 | 101 | 101
Terranora | 9501 | 66 | Terranora 110/66kV STS | Cudgen ZS | 59 | 9.74 | 10.31 | 10.84 | 11.35 | 11.84
Terranora | 9502 | 66 | Terranora 110/66kV STS | Murwillumbah ZS | 61 | 7 | 7.4 | 7.78 | 8.14 | 8.49
Terranora | 9503 | 66 | Terranora 110/66kV STS | Banora Pt ZS | 59 | 18.34 | 19.42 | 20.44 | 21.41 | 22.34
Terranora | 9504 | 66 | Terranora 110/66kV STS | Condong Sw Stn | 61 | 6.3 | 6.66 | 7 | 7.33 | 7.64
Terranora | 9505 | 66 | Cudgen ZS | Banora Point ZS | 53 | 0.76 | 0.8 | 0.85 | 0.89 | 0.92
Terranora | 9508 | 66 | Terranora 110/66kV STS | Tweed Heads ZS | 41 | 3.81 | 4.05 | 4.28 | 4.49 | 4.7
Terranora | 9510 | 66 | Banora Point ZS | Tweed Heads South ZS | 43 | 11.43 | 12.11 | 12.75 | 13.36 | 13.94
Terranora | 9514 | 66 | Condong Sw Stn | Murwillumbah ZS | 61 | 11.9 | 12.58 | 13.23 | 13.84 | 14.42
Terranora | 9516 | 66 | Tweed Head South ZS | Tweed Heads ZS | 43 | 0.91 | 0.97 | 1.02 | 1.07 | 1.12
Terranora | 9406 | 33 | Cudgen ZS | Casuarina Sw Stn | 17 | 11.67 | 12.33 | 12.97 | 13.57 | 14.14
Terranora | 9407 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 0 | 0 | 0 | 0 | 0
Terranora | 9409 | 33 | Casuarina Sw Stn | Hastings Pt ZS | 20 | 11.67 | 12.33 | 12.97 | 13.57 | 14.14
Armidale | 661/1 | 66 | TransGrid Armidale 330/132/66kV STS | Hillgrove Tee | 20 | 0.73 | 0.77 | 0.81 | 0.84 | 0.87
Armidale | 661/2 | 66 | Hillgrove Tee | Hillgrove ZS | 16 | 0.31 | 0.33 | 0.35 | 0.36 | 0.37
Armidale | 661/3 | 66 | Hillgrove Tee | Oaky ZS | 20 | 0.45 | 0.47 | 0.49 | 0.51 | 0.53
Armidale | 662/1 | 66 | TransGrid Armidale 330/132/66kV STS | Uralla Tee | 12 | 4.22 | 4.47 | 4.69 | 4.91 | 5.12
Armidale | 662/2 | 66 | Uralla Tee | Uralla ZS | 9 | 2.61 | 2.78 | 2.94 | 3.09 | 3.24
Armidale | 662/4 | 66 | Uralla Tee | Walcha South ZS | 9 | 1.61 | 1.69 | 1.75 | 1.82 | 1.88
Armidale | 664 | 66 | TransGrid Armidale 330/132/66kV STS | Galloway St ZS | 28 | 12.1 | 12.71 | 13.3 | 13.85 | 14.38
Armidale | 665 | 66 | TransGrid Armidale 330/132/66kV STS | Madgwick Dr ZS | 21 | 7.78 | 8.17 | 8.55 | 8.9 | 9.24
Armidale | 66C | 66 | Miller St ZS | Madgwick Dr ZS | 21 | 1.55 | 1.62 | 1.7 | 1.77 | 1.84
Armidale | 66F | 66 | Galloway St ZS | Miller St ZS | 15 | 5.55 | 5.83 | 6.1 | 6.36 | 6.6
Bathurst | 81H | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 62 | 4.74 | 5.07 | 5.38 | 5.67 | 5.94
Bathurst | 81G | 66 | TransGrid Panorama 132/66kV STS | Stewart ZS | 64 | 6.77 | 7.24 | 7.68 | 8.09 | 8.49
Bathurst | 81F | 66 | TransGrid Panorama 132/66kV STS | Russell St ZS | 64 | 12.05 | 12.91 | 13.73 | 14.49 | 15.22
Bathurst | 81J | 66 | Raglan ZS | Russell St ZS | 64 | 2.3 | 2.47 | 2.62 | 2.77 | 2.91
Bathurst | 81L | 66 | TransGrid Panorama 132/66kV STS | Raglan ZS | 64 | 7.44 | 7.98 | 8.48 | 8.95 | 9.4
Bathurst | 81C | 66 | TransGrid Panorama 132/66kV STS | Blayney ZS | 25 | 5.65 | 6.04 | 6.42 | 6.76 | 7.1
Bathurst | 66:MAN | 66 | Blayney ZS | Mandurama ZS | 9 | 1.28 | 1.35 | 1.43 | 1.49 | 1.56
Beryl | 94M/4 | 132 | TransGrid 94M Mudgee Tee | Mudgee ZS | 128 | 11.74 | 12.45 | 13.12 | 13.76 | 14.38
Beryl | 851/1 | 66 | TransGrid Beryl 132/66kV STS | Gulgong ZS | 28 | 1.48 | 1.58 | 1.67 | 1.76 | 1.84
Beryl | 851/2 | 66 | Gulgong ZS | Mudgee ZS | 28 | 0 | 0 | 0 | 0 | 0
Beryl | 852 | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 15 | 0 | 0 | 0 | 0 | 0
Beryl | 86J | 66 | TransGrid Beryl 132/66kV STS | Dunedoo ZS | 61 | 6.91 | 7.23 | 7.55 | 7.85 | 8.14
Beryl | 85A | 66 | Dunedoo ZS | Coonabarabran ZS | 11 | 4.87 | 5.06 | 5.25 | 5.42 | 5.59
Beryl | 80L | 66 | Ulan Sw Stn | Ulan Town ZS | 15 | 1.11 | 1.17 | 1.22 | 1.27 | 1.32
Beryl | 80R | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 64 | 0 | 0 | 0 | 0 | 0
Beryl | 80U | 66 | TransGrid Beryl 132/66kV STS | Ulan Sw Stn | 61 | 0 | 0 | 0 | 0 | 0
Beryl | 80T | 66 | Ulan Sw Stn | Moolarben No1 Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Beryl | 80W | 66 | Moolarben No1 Mine ZS | Moolarben No2 Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Beryl | 80X | 66 | Moolarben No2 Mine ZS | Wilpinjong Mine ZS | 43 | 0 | 0 | 0 | 0 | 0
Broken Hill | X4 | 220 | TransGrid Broken Hill 220/22kV STS | Perilya Mine | 427 | 0 | 0 | 0 | 0 | 0
Broken Hill | 5B1:PPL | 66 | Pinnacles Place ZS | Mt Gipps ZS | 19 | 0 | 0 | 0 | 0 | 0
Broken Hill | 5B1:MTG | 66 | Mt Gipps ZS | Sunset Strip ZS | 19 | -0.67 | -0.69 | -0.71 | -0.72 | -0.74
Broken Hill | 5B1:SUN | 66 | Sunset Strip ZS | Menindee ZS | 6 | 0.72 | 0.77 | 0.81 | 0.85 | 0.88
Dubbo | 94J/3 | 132 | 94J Tee | Dubbo South ZS | 106 | 76.49 | 77.4 | 78.28 | 79.11 | 79.91
Dubbo | 943/2 | 132 | Dubbo South ZS | Narromine South Sw Stn | 106 | 54.38 | 55.03 | 55.65 | 56.24 | 56.81
Dubbo | 94W/1 | 132 | Dubbo 132/66kV STS | Nevertire Tee | 128 | 100.38 | 100.27 | 100.17 | 100.07 | 99.98
Dubbo | 94W/2 | 132 | Nevertire Tee | Nevertire ZS | 124 | 2.12 | 2.23 | 2.33 | 2.43 | 2.52
Dubbo | 94W/3 | 132 | Nevertire Tee | Nevertire Sw Stn | 128 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
Dubbo | 9GX | 132 | Nevertire Sw Stn | Nyngan 132/66kV STS | 128 | 1.98 | 1.98 | 1.98 | 1.98 | 1.98
Dubbo | 9GP | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 19.38 | 19.63 | 19.86 | 20.09 | 20.31
Dubbo | 9GR | 132 | Narromine South Sw Stn | Narromine ZS | 124 | 0 | 0 | 0 | 0 | 0
Dubbo | 9GT | 132 | Dubbo West ZS | Narromine South Sw Stn | 140 | 21.86 | 22.11 | 22.34 | 22.57 | 22.79
Dubbo | 9GU | 132 | Narromine South Sw Stn | Nyngan 132/66kV STS | 106 | 5.46 | 5.46 | 5.46 | 5.46 | 5.46
Dubbo | 9GW | 132 | Dubbo 132/66kV STS | Dubbo West ZS | 140 | 59.16 | 59.87 | 60.54 | 61.19 | 61.8
Dubbo | 812 | 66 | Yarrandale ZS | Gilgandra ZS | 15 | 0 | 0 | 0 | 0 | 0
Dubbo | 815 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 2.22 | 2.35 | 2.47 | 2.59 | 2.7
Dubbo | 816 | 66 | Dubbo 132/66kV STS | Phillip St ZS | 43 | 2.22 | 2.35 | 2.47 | 2.59 | 2.7
Dubbo | 813:EUL | 66 | Eulomogo ZS | Geurie Tee | 12 | 0.78 | 0.84 | 0.89 | 0.95 | 0.99
Dubbo | 813/1:GUE | 66 | Geurie Tee | Geurie ZS | 16 | 0.78 | 0.84 | 0.89 | 0.95 | 0.99
Dubbo | 814/1 | 66 | Gilgandra ZS | Gulargambone ZS | 11 | 3.27 | 3.44 | 3.6 | 3.75 | 3.9
Dubbo | 814/2 | 66 | Gulargambone ZS | Coonamble ZS | 11 | 2.52 | 2.66 | 2.79 | 2.91 | 3.03
Dubbo | 81M | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 6.84 | 7.22 | 7.58 | 7.92 | 8.24
Dubbo | 81P | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 61 | 3.48 | 3.67 | 3.83 | 4 | 4.16
Dubbo | 81R | 66 | Dubbo 132/66kV STS | Eulomogo ZS | 20 | 6.84 | 7.22 | 7.58 | 7.92 | 8.24
Dubbo | 81X | 66 | Dubbo 132/66kV STS | Yarrandale ZS | 28 | 4.26 | 4.48 | 4.69 | 4.89 | 5.08
Dubbo | 81T | 66 | Yarrandale ZS | Gilgandra ZS | 43 | 6.35 | 6.68 | 6.99 | 7.29 | 7.58
Forbes | 858 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 5.64 | 5.97 | 6.29 | 6.59 | 6.88
Forbes | 859 | 66 | TransGrid Forbes 132/66kV STS | Forbes Town ZS | 28 | 0 | 0 | 0 | 0 | 0
Forbes | 893/5 | 66 | TransGrid Forbes 132/66kV STS | Payten's Bridge ZS | 12 | 1.05 | 1.11 | 1.17 | 1.22 | 1.27
Forbes | 894:CDN | 66 | Condobolin ZS | Lake Cargelligo ZS | 15 | 2.02 | 2.1 | 2.17 | 2.24 | 2.31
Forbes | 896:WJL | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 20 | 18 | 18 | 18 | 18 | 18
Forbes | 897:CDN | 66 | West Jemalong ZS | Condobolin ZS | 20 | 21.31 | 21.52 | 21.72 | 21.92 | 22.11
Forbes | 89H | 66 | TransGrid Forbes 132/66kV STS | West Jemalong ZS | 43 | 30 | 30 | 30 | 30 | 30
Glen Innes | 886 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 70 | 4.94 | 5.14 | 5.33 | 5.51 | 5.68
Glen Innes | 887 | 66 | TransGrid Glen Innes 132/66kV STS | Glen Innes ZS | 19 | 5.88 | 6.12 | 6.34 | 6.56 | 6.76
Glen Innes | 6NY | 66 | Glen Innes ZS | Guyra ZS | 11 | 2.47 | 2.61 | 2.74 | 2.86 | 2.98
Glen Innes | 6NE | 66 | Glen Innes ZS | Emmaville ZS | 17 | 0.99 | 1.04 | 1.07 | 1.11 | 1.14
Glen Innes | 6AE/A | 66 | Pindari ZS | Ashford ZS | 17 | 0 | 0 | 0 | 0 | 0
Glen Innes | 6AE/E | 66 | Emmaville ZS | Pindari ZS | 17 | 0.35 | 0.36 | 0.37 | 0.39 | 0.4
Gunnedah | 877 | 66 | TransGrid Gunnedah 132/66kV STS | Keepit Dam ZS | 10 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Gunnedah | 88G/1 | 66 | Gunnedah ZS | Emerald Hill Sw Stn | 24 | 13.15 | 13.2 | 13.25 | 13.3 | 13.34
Gunnedah | 88G/2 | 66 | Emerald Hill Sw Stn | Boggabri ZS | 24 | 1.15 | 1.2 | 1.25 | 1.3 | 1.34
Gunnedah | 88K | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 11.3 | 11.67 | 12.03 | 12.36 | 12.68
Gunnedah | 88L | 66 | TransGrid Gunnedah 132/66kV STS | Gunnedah ZS | 61 | 11.3 | 11.67 | 12.03 | 12.36 | 12.68
Inverell | 734 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 16.97 | 17.35 | 17.71 | 18.05 | 18.39
Inverell | 735 | 66 | TransGrid Inverell 132/66kV STS | Borthwick St ZS | 64 | 17.25 | 17.62 | 17.99 | 18.35 | 18.68
Inverell | 6AB | 66 | Borthwick St ZS | Ashford ZS | 17 | 6.19 | 6.33 | 6.46 | 6.59 | 6.71
Inverell | 6AF/A | 66 | Ashford ZS | Wallangra ZS | 11 | 0.86 | 0.87 | 0.89 | 0.91 | 0.93
Inverell | 6AF/F | 66 | Wallangra ZS | Coolatai Sw Stn | 11 | 0.72 | 0.73 | 0.75 | 0.76 | 0.78
Inverell | 6AX | 66 | Ashford ZS | Texas ZS | 9 | 5.17 | 5.28 | 5.39 | 5.5 | 5.6
Inverell | 6BC | 66 | Borthwick St ZS | Copeton ZS | 21 | 0.79 | 0.8 | 0.82 | 0.84 | 0.85
Inverell | 6BD | 66 | Borthwick St ZS | Bundarra ZS | 14 | 0.89 | 0.91 | 0.93 | 0.95 | 0.96
Inverell | 6BW | 66 | Borthwick St ZS | Warialda ZS | 15 | 6.81 | 6.96 | 7.1 | 7.24 | 7.38
Inverell | 6FH | 66 | Coolatai Sw Stn | Yallaroi ZS | 20 | 2.16 | 2.2 | 2.25 | 2.29 | 2.34
Inverell | 6FW | 66 | Warialda ZS | Coolatai Sw Stn | 11 | 1.64 | 1.68 | 1.71 | 1.75 | 1.78
Inverell | 6HG | 66 | Yallaroi ZS | Goondiwindi ZS | 20 | 0 | 0 | 0 | 0 | 0
Inverell | 6WK | 66 | Warialda ZS | Bingara ZS | 11 | 2.63 | 2.69 | 2.75 | 2.8 | 2.85
Molong | 8C1 | 66 | TransGrid Molong 132/66kV STS | Cumnock / Orange West Tee | 61 | 0.88 | 0.92 | 0.95 | 0.99 | 1.02
Molong | 8C1/3 | 66 | Cumnock / Orange West Tee | Cumnock ZS | 9 | 0.88 | 0.92 | 0.95 | 0.99 | 1.02
Molong | 8C1/4 | 66 | Cumnock / Orange West Tee | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0
Moree | 876 | 66 | TransGrid Moree 132/66kV STS | Moree Solar Farm | 70 | -0.27 | -0.28 | -0.28 | -0.29 | -0.29
Moree | 87J | 66 | Moree Solar Farm | Bellata ZS | 25 | 0.27 | 0.28 | 0.28 | 0.29 | 0.29
Moree | 721 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 4.48 | 4.68 | 4.87 | 5.05 | 5.22
Moree | 722 | 66 | TransGrid Moree 132/66kV STS | Moree ZS | 64 | 4.75 | 4.96 | 5.16 | 5.35 | 5.53
Moree | 881/1 | 66 | TransGrid Moree 132/66kV STS | Ashley Tee | 15 | 1.21 | 1.26 | 1.29 | 1.34 | 1.38
Moree | 881/2 | 66 | Ashley Tee | Ashley ZS | 10 | 0.29 | 0.3 | 0.3 | 0.31 | 0.32
Moree | 6PU | 66 | Ashley Tee | Mungindi ZS | 10 | 0.72 | 0.76 | 0.79 | 0.83 | 0.86
Moree | 723:WTR/1 | 66 | TransGrid Moree 132/66kV STS | Wathagar ZS | 12 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Moree | 723:WTR/2 | 66 | Wathagar ZS | Wenna ZS | 15 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Narrabri | 879 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 18 | 0.95 | 1 | 1.04 | 1.09 | 1.13
Narrabri | 882 | 66 | TransGrid Narrabri 132/66kV STS | Wee Waa ZS | 64 | 1.86 | 1.94 | 2.02 | 2.11 | 2.19
Narrabri | 885 | 66 | Burren Junction ZS | Merrywinebone ZS | 15 | 0.48 | 0.51 | 0.54 | 0.57 | 0.6
Narrabri | 833:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 3.04 | 3.17 | 3.3 | 3.42 | 3.54
Narrabri | 834:NBI | 66 | TransGrid Narrabri 132/66kV STS | Narrabri ZS | 38 | 3.04 | 3.17 | 3.3 | 3.42 | 3.54
Narrabri | 861/1 | 66 | TransGrid Narrabri 132/66kV STS | Wilga Park ZS | 64 | 2.29 | 2.93 | 3.54 | 4.13 | 4.69
Narrabri | 861/2 | 66 | Wilga Park ZS | Walgett ZS | 64 | 4.53 | 4.83 | 5.11 | 5.39 | 5.65
Narrabri | 88F | 66 | Narrabri Sw Stn | Boggabri ZS | 24 | 0 | 0 | 0 | 0 | 0
Narrabri | 878/3 | 66 | TransGrid Narrabri 132/66kV STS | Narrabri Sw Stn | 61 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7
Narrabri | 88C | 66 | Narrabri Sw Stn | Narrabri Coal | 53 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5
Narrabri | 880/1 | 66 | Wee Waa ZS | Burren Junction ZS | 13 | 0.81 | 0.85 | 0.88 | 0.93 | 0.96
Narrabri | 880/2 | 66 | Burren Junction ZS | Walgett ZS | 13 | 0 | 0 | 0 | 0 | 0
Narrabri | 890:BRE | 66 | Walgett ZS | Brewarrina ZS | 15 | 0.73 | 0.77 | 0.8 | 0.84 | 0.87
Narrabri | 895:LGR | 66 | Walgett ZS | Lightning Ridge ZS | 15 | 1.71 | 1.83 | 1.96 | 2.07 | 2.18
Nyngan | 9UT | 132 | Nyngan 132/66kV STS | Nyngan Solar Farm | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 9UW | 132 | Nyngan Solar Farm | Scrubby Valley Sw Stn | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 946/2 | 132 | Scrubby Valley Sw Stn | Cobar CSA ZS | 106 | 0 | 0 | 0 | 0 | 0
Nyngan | 946/3 | 132 | Scrubby Valley Sw Stn | Cobar Peak ZS | 102 | 0 | 0 | 0 | 0 | 0
Nyngan | 94R | 132 | Cobar CSA ZS | Cobar Elura ZS | 128 | 0 | 0 | 0 | 0 | 0
Nyngan | 811 | 66 | Nyngan 132/66kV STS | Cobar Town ZS | 10 | 4.49 | 4.7 | 4.91 | 5.1 | 5.29
Nyngan | 854 | 66 | Nyngan 132/66kV STS | Nyngan Town ZS | 15 | 4.65 | 4.76 | 4.85 | 4.95 | 5.04
Nyngan | 820/1:NYN | 66 | Nyngan Town ZS | Nevertire Tee | 15 | 0 | 0 | 0 | 0 | 0
Nyngan | 820:NVE | 66 | Nyngan 132/66kV STS | Nevertire ZS | 11 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/1 | 66 | Nyngan 132/66kV STS | Girilambone Tee | 28 | 1.67 | 1.71 | 1.75 | 1.8 | 1.85
Nyngan | 855/1a | 66 | Girilambone Tee | Girilambone ZS | 24 | 0 | 0 | 0 | 0 | 0
Nyngan | 855/2 | 66 | Girilambone Tee | Byrock Tee | 28 | 2.09 | 2.14 | 2.19 | 2.25 | 2.31
Nyngan | 855/3 | 66 | Byrock Tee | Bourke ZS | 28 | 1.76 | 1.81 | 1.86 | 1.92 | 1.98
Nyngan | 855/3a | 66 | Byrock Tee | Byrock ZS | 15 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Nyngan | 855/4 | 66 | Girilambone ZS | Tritton Mine ZS | 24 | 0 | 0 | 0 | 0 | 0
Oberon | 94C | 132 | TransGrid Wallerawang 330/132/66kV STS | Oberon 132 ZS | 128 | 0 | 0 | 0 | 0 | 0
Oberon | 856 | 66 | TransGrid Wallerawang 330/132/66kV STS | Oberon Town ZS | 28 | 2.93 | 3.1 | 3.27 | 3.43 | 3.58
Oberon | 81B | 33 | Oberon Town ZS | Burraga ZS | 8 | 0 | 0 | 0 | 0 | 0
Orange | 94G | 132 | TransGrid Orange North 132kV Sw Stn | Cadia ZS | 142 | 68.66 | 68.66 | 68.66 | 68.66 | 68.66
Orange | 9MC | 132 | TransGrid Orange North 132kV Sw Stn | Flyers Creek Sw Stn | 142 | 72.86 | 72.86 | 72.86 | 72.86 | 72.86
Orange | 9MR | 132 | Flyers Creek Sw Stn | Cadia ZS | 180 | 112.1 | 112.1 | 112.1 | 112.1 | 112.1
Orange | 807 | 66 | TransGrid Orange 132/66kV STS | Orange West & South Tee | 61 | 9.1 | 9.72 | 10.3 | 10.84 | 11.36
Orange | 807/2 | 66 | Orange West & South Tee | Orange South ZS | 63 | 0 | 0 | 0 | 0 | 0
Orange | 807/3 | 66 | Orange West & South Tee | Orange West ZS | 62 | 9.1 | 9.72 | 10.3 | 10.84 | 11.36
Orange | 818/1 | 66 | TransGrid Orange 132/66kV STS | Blayney ZS | 11 | 0 | 0 | 0 | 0 | 0
Orange | 8C2 | 66 | TransGrid Orange 132/66kV STS | Orange West ZS | 9 | 0 | 0 | 0 | 0 | 0
Orange | 8F1 | 66 | TransGrid Orange 132/66kV STS | Orange South ZS | 63 | 11.07 | 11.88 | 12.62 | 13.34 | 14.02
Orange | 8M1 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 11 | 9.14 | 9.72 | 10.26 | 10.78 | 11.27
Orange | 8M2 | 66 | TransGrid Orange 132/66kV STS | Orange Industrial ZS | 21 | 0 | 0 | 0 | 0 | 0
Parkes | 9MX | 132 | TransGrid Parkes 132/66kV STS | Quorn Park Sw Stn | 87 | 0 | 0 | 0 | 0 | 0
Parkes | 300 | 132 | Quorn Park Sw Stn | North Parkes Mine ZS | 87 | 0 | 0 | 0 | 0 | 0
Parkes | 898 | 66 | TransGrid Parkes 132/66kV STS | Trundle ZS | 10 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
Parkes | 899 | 66 | Parkes Town ZS | Peak Hill ZS | 12 | 4.86 | 4.91 | 4.96 | 5 | 5.04
Parkes | 89G | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 61 | 7.44 | 7.72 | 7.98 | 8.22 | 8.46
Parkes | 89L | 66 | TransGrid Parkes 132/66kV STS | Parkes Town ZS | 39 | 6.7 | 6.94 | 7.18 | 7.4 | 7.61
Parkes | 89M | 66 | Peak Hill ZS | Tomingley Mine ZS | 32 | 0 | 0 | 0 | 0 | 0
Tamworth | 801 | 66 | Transgrid Tamworth 132/66kV STS | Oxley Vale ZS | 63 | 7.43 | 7.94 | 8.42 | 8.87 | 9.29
Tamworth | 803 | 66 | Transgrid Tamworth 132/66kV STS | South Tamworth ZS | 70 | 12.88 | 13.69 | 14.46 | 15.18 | 15.88
Tamworth | 804 | 66 | Transgrid Tamworth 132/66kV STS | Nundle ZS | 8 | 0.77 | 0.81 | 0.84 | 0.87 | 0.9
Tamworth | 806 | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 38 | 4.56 | 4.83 | 5.09 | 5.33 | 5.57
Tamworth | 873 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 4.32 | 4.59 | 4.85 | 5.09 | 5.32
Tamworth | 874 | 66 | Transgrid Tamworth 132/66kV STS | East Tamworth ZS | 53 | 4.5 | 4.78 | 5.04 | 5.29 | 5.53
Tamworth | 803/2 | 66 | South Tamworth ZS | Oxley Vale ZS | 63 | 2.48 | 2.65 | 2.81 | 2.96 | 3.1
Tamworth | 806/1 | 66 | Goddard Lane ZS | Attunga ZS | 18 | 4.41 | 4.66 | 4.89 | 5.1 | 5.33
Tamworth | 806/2 | 66 | Attunga ZS | Manilla ZS | 18 | 3.19 | 3.38 | 3.56 | 3.72 | 3.89
Tamworth | 806/3 | 66 | Manilla ZS | Upper Manilla ZS | 18 | 1.22 | 1.29 | 1.36 | 1.41 | 1.48
Tamworth | 806/4 | 66 | Upper Manilla ZS | Barraba ZS | 15 | 1.3 | 1.38 | 1.45 | 1.51 | 1.58
Tamworth | 80C | 66 | Transgrid Tamworth 132/66kV STS | Goddard Lane ZS | 61 | 4.04 | 4.28 | 4.52 | 4.73 | 4.94
Tamworth | 813:CLA | 66 | Transgrid Tamworth 132/66kV STS | Currububula ZS | 28 | 8.41 | 8.64 | 8.85 | 9.05 | 9.24
Tamworth | 813/1:QDI | 66 | Currububula ZS | Werris Creek ZS | 28 | 7.98 | 8.19 | 8.38 | 8.56 | 8.74
Tamworth | 813/2:QDI | 66 | Werris Creek ZS | Quirindi ZS | 28 | 2.74 | 2.89 | 3.04 | 3.17 | 3.31
Tamworth | 870/1:KTL | 66 | Transgrid Tamworth 132/66kV STS | Kootingal Tee | 14 | 8.49 | 8.71 | 8.92 | 9.12 | 9.31
Tamworth | 870/2:KTL | 66 | Kootingal Tee | Kootingal ZS | 12 | 8.07 | 8.27 | 8.46 | 8.63 | 8.8
Tamworth | 870/3:KTL | 66 | Kootingal Tee | Bendemeer ZS | 13 | 0.42 | 0.44 | 0.46 | 0.49 | 0.51
Tamworth | 798 | 33 | Quirindi ZS | Murrurundi ZS | 4 | 1.44 | 1.53 | 1.62 | 1.7 | 1.78
Tamworth | 799/1 | 33 | Quirindi ZS | Caroona Tee | 6 | 0.63 | 0.66 | 0.67 | 0.7 | 0.72
Tamworth | 799/2 | 33 | Caroona Tee | Caroona ZS | 4 | 0.09 | 0.1 | 0.1 | 0.11 | 0.11
Tamworth | 799/3 | 33 | Caroona Tee | Spring Ridge ZS | 3 | 0.08 | 0.09 | 0.09 | 0.09 | 0.1
Tamworth | 799/4 | 33 | Spring Ridge ZS | Colly Blue ZS | 3 | 0.26 | 0.27 | 0.28 | 0.3 | 0.31
Wellington | 945/3 | 132 | TransGrid Line 945 Wellington 132kV Tee | Wellington 132kV ZS | 124 | 3.48 | 3.73 | 3.96 | 4.18 | 4.39
Wellington | 947/1 | 132 | TransGrid Line 947 Burrendong Tee | Burrendong Hydro | 36 | 0 | 0 | 0 | 0 | 0
Wellington | 94F | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 155.06 | 156.92 | 158.69 | 160.38 | 162
Wellington | 94J | 132 | TransGrid Wellington 330/132kV STS | Dubbo 132/66kV STS | 173 | 143.71 | 145.44 | 147.08 | 148.64 | 150.13
Wellington | 805 | 66 | Wellington 132kV ZS | Mumbil ZS | 11 | 0.54 | 0.59 | 0.63 | 0.67 | 0.7
Wellington | 813:WGN | 66 | Wellington 132kV ZS | Geurie Tee | 12 | 0 | 0 | 0 | 0 | 0
Albury | 997/1 | 132 | Union Rd ZS | Corowa ZS | 128 | -39.47 | -39.9 | -40.3 | -40.68 | -41.06
Albury | 997/2 | 132 | Corowa ZS | Mulwala ZS | 128 | -7.7 | -7.91 | -8.12 | -8.31 | -8.5
Albury | 99E | 132 | Union Rd ZS | Jelbart ZS | 148 | 4.79 | 5.12 | 5.43 | 5.72 | 6
Albury | 99G | 132 | Union Rd ZS | Jelbart ZS | 148 | 4.79 | 5.12 | 5.43 | 5.72 | 6
Bega | 84G | 66 | Bega 132/66kV STS | Eden South ZS | 61 | 2.97 | 3.17 | 3.36 | 3.53 | 3.7
Bega | 84H | 66 | Eden South ZS | Edrom ZS | 38 | 0 | 0 | 0 | 0 | 0
Bega | 84M | 66 | Bega 132/66kV STS | Maher St ZS | 61 | 3.71 | 3.9 | 4.08 | 4.25 | 4.41
Bega | 89A | 66 | Bega 132/66 | Pambula ZS | 38 | 7.63 | 8.16 | 8.66 | 9.13 | 9.57
Bega | 84P | 66 | Bega 132/66kV STS | Maher St ZS | 38 | 3.71 | 3.9 | 4.08 | 4.25 | 4.41
Bega | 89F | 66 | Pambula ZS | Eden South ZS | 30 | 0.99 | 1.05 | 1.12 | 1.17 | 1.23
Bega | 84R/1 | 66 | Maher St ZS | Quira ZS | 6 | 0 | 0 | 0 | 0 | 0
Bega | 7802/1 | 33 | Maher St ZS | Brogo ZS | 12 | 0 | 0 | 0 | 0 | 0
Bega | 7802/2 | 33 | Brogo ZS | Cobargo ZS | 10 | 3.59 | 3.83 | 4.06 | 4.28 | 4.48
Bega | 7814 | 33 | Cobargo ZS | Bermagui ZS | 5 | 2.19 | 2.35 | 2.5 | 2.64 | 2.77
Buronga | 87G | 66 | Dareton ZS | Ellerslie ZS | 67 | 0.45 | 0.46 | 0.48 | 0.5 | 0.51
Buronga | 87H/1 | 66 | Ellerslie ZS | Ginkgo Snapper Tee | 45 | 0 | 0 | 0 | 0 | 0
Buronga | 87H/2 | 66 | Ginkgo Snapper Tee | Ginkgo ZS | 20 | 0 | 0 | 0 | 0 | 0
Buronga | 87H/3 | 66 | Ginkgo Snapper Tee | Snapper ZS | 12 | 0 | 0 | 0 | 0 | 0
Buronga | 83U | 66 | Powercor Mildura ZS (NSW Border) | Buronga ZS | 22 | 6.59 | 6.59 | 6.59 | 6.59 | 6.59
Buronga | 83W | 66 | Buronga ZS | Dareton ZS | 22 | 0 | 0 | 0 | 0 | 0
Buronga | Merbein - Dareton Line | 66 | Powercor Mildura ZS (NSW Border) | Dareton ZS | 49 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48
Coleambally | CLY1526/1 | 33 | Coleambally 132/33kV STS | Coleambally Tee | 10 | 0.57 | 0.59 | 0.62 | 0.64 | 0.65
Coleambally | CLY1526/2 | 33 | Coleambally Tee | Coleambally ZS | 10 | 0.52 | 0.54 | 0.56 | 0.58 | 0.59
Coleambally | CLY1526/3 | 33 | Coleambally Tee | Egansford ZS | 8 | 0.1 | 0.11 | 0.11 | 0.12 | 0.12
Coleambally | CLY1530/1 | 33 | Coleambally 132/33kV STS | Ringwood Rd ZS | 8 | 1.17 | 1.21 | 1.27 | 1.32 | 1.36
Coleambally | CLY1530/2 | 33 | Ringwood Rd ZS | Darlington Point ZS | 8 | 0.96 | 1.01 | 1.06 | 1.11 | 1.15
Cooma | 974 | 132 | TransGrid Cooma 132/66kV STS | Bega 132/66kV STS | 128 | 10.39 | 11.09 | 11.75 | 12.37 | 12.96
Cooma | 97R/1 | 132 | TransGrid Cooma 132/66kV STS | Steeple Flat 132/66kV STS | 163 | -23.22 | -24.1 | -24.94 | -25.73 | -26.48
Cooma | 82D | 66 | TransGrid Cooma 132/66kV STS | Jindabyne East ZS | 20 | 4.42 | 4.7 | 4.96 | 5.21 | 5.44
Cooma | 84J | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 70 | 2.72 | 2.85 | 2.97 | 3.09 | 3.2
Cooma | 84L | 66 | TransGrid Cooma 132/66kV STS | Cooma 66/11kV ZS | 64 | 2.72 | 2.85 | 2.97 | 3.09 | 3.2
Cooma | 82J/1 | 66 | Snowy Adit 132/66/11kV ZS | Snowy Lookout Sw Stn | 12 | 0 | 0 | 0 | 0 | 0
Cooma | 82J/2 | 66 | Snowy Lookout Sw Stn | Jindabyne ZS | 12 | 0 | 0 | 0 | 0 | 0
Cooma | 82R | 66 | Jindabyne East ZS | Jindabyne ZS | 20 | 1.89 | 1.99 | 2.09 | 2.18 | 2.27
Cooma | 888/1 | 66 | TransGrid Cooma 132/66kV STS | Rhine Falls Sw Stn | 16 | 0.9 | 0.95 | 0.98 | 1.01 | 1.05
Cooma | 888/3 | 66 | Rhine Falls Sw Stn | Adaminaby ZS | 16 | 0.63 | 0.67 | 0.7 | 0.73 | 0.76
Cooma | 888/4 | 66 | Rhine Falls Sw Stn | Eucumbene Tee | 15 | 0.17 | 0.18 | 0.18 | 0.18 | 0.19
Cooma | 888/6 | 66 | Eucumbene Tee | Eucumbene ZS | 15 | 0.07 | 0.08 | 0.08 | 0.08 | 0.09
Cooma | 888/7 | 66 | Eucumbene Tee | Snowy Adit 132/66/11kV ZS | 20 | 0 | 0 | 0 | 0 | 0
Cooma | 849/1 | 33 | Adaminaby ZS | Providence Portal ZS | 7 | 0 | 0 | 0 | 0 | 0
Cowra | 865 | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 4.34 | 4.63 | 4.89 | 5.14 | 5.38
Cowra | 863:CWD | 66 | TransGrid Cowra 132/66kV STS | Canowindra ZS | 9 | 2.61 | 2.79 | 2.96 | 3.12 | 3.27
Cowra | 866:COW | 66 | TransGrid Cowra 132/66kV STS | Cowra Town ZS | 15 | 4.34 | 4.63 | 4.89 | 5.14 | 5.38
Cowra | 891/1 | 66 | TransGrid Cowra 132/66kV STS | Wyangala Dam Tee | 20 | 21.76 | 21.73 | 21.7 | 21.67 | 21.64
Cowra | 891/2 | 66 | Wyangala Dam Tee | Wyangala Dam | 19 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5
Cowra | 891/5 | 66 | Monteagle Tee | Monteagle ZS | 13 | 0.43 | 0.44 | 0.46 | 0.47 | 0.49
Cowra | 891/6 | 66 | Monteagle Tee | Young ZS | 19 | 0 | 0 | 0 | 0 | 0
Cowra | 891/7 | 66 | Bendick Murrell Tee | Bendick Murrell ZS | 19 | 1.13 | 1.18 | 1.23 | 1.28 | 1.33
Cowra | 891:BMU/1 | 66 | Wyangala Dam Tee | Bendick Murrell Tee | 19 | 1.48 | 1.54 | 1.61 | 1.66 | 1.73
Cowra | 891:BMU/2 | 66 | Bendick Murrell Tee | Monteagle Tee | 19 | 0.43 | 0.44 | 0.46 | 0.47 | 0.49
Cowra | 893/1 | 66 | TransGrid Cowra 132/66kV STS | Grenfell Tee | 12 | 2.9 | 3.1 | 3.28 | 3.45 | 3.62
Cowra | 893/4 | 66 | Grenfell Tee | Payten's Bridge ZS | 12 | 0 | 0 | 0 | 0 | 0
Cowra | 893/6 | 66 | Grenfell Tee | Grenfell ZS | 12 | 2.9 | 3.1 | 3.28 | 3.45 | 3.62
Darlington Point | 99N | 132 | TransGrid Darlington Point 330/132kV STS | Hillston ZS | 128 | 52.97 | 53.16 | 53.34 | 53.52 | 53.68
Darlington Point | 99R | 132 | TransGrid Darlington Point 330/132kV STS | Hay 132 ZS | 128 | 2.01 | 2.02 | 2.04 | 2.05 | 2.06
Darlington Point | HAT 22 | 33 | Hay 132 ZS | Hay ZS | 8 | 2.03 | 2.15 | 2.26 | 2.36 | 2.45
Darlington Point | HAT 32 | 33 | Hay 132 ZS | Hay ZS | 8 | 0.51 | 0.54 | 0.56 | 0.59 | 0.61
Darlington Point | HAT 42 | 33 | Hay 132 ZS | Carrathool ZS | 7 | 0.82 | 0.83 | 0.86 | 0.89 | 0.9
Darlington Point | HIL1117 | 33 | Hillston ZS | Ivanhoe ZS | 8 | 1.48 | 1.57 | 1.66 | 1.74 | 1.82
Deniliquin | 844 | 66 | TransGrid Deniliquin 132/66kV STS | Barham ZS | 11 | 2.58 | 2.71 | 2.82 | 2.93 | 3.04
Deniliquin | 845 | 66 | TransGrid Deniliquin 132/66kV STS | Deniliquin ZS | 38 | 9.83 | 10.29 | 10.73 | 11.15 | 11.55
Deniliquin | 822/1 | 66 | TransGrid Deniliquin 132/66kV STS | Murgha ZS | 11 | 3.38 | 3.54 | 3.69 | 3.83 | 3.97
Deniliquin | 822/2 | 66 | Murgha ZS | Moulamein ZS | 11 | 2.83 | 2.96 | 3.09 | 3.21 | 3.32
Deniliquin | 84Y | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 66 | 3.8 | 3.98 | 4.15 | 4.31 | 4.47
Deniliquin | MM61 | 66 | Moulamein ZS | Koraleigh ZS | 15 | 1.88 | 1.97 | 2.05 | 2.13 | 2.21
Deniliquin | No.6 Moama | 66 | TransGrid Deniliquin 132/66kV STS | Moama ZS | 34 | 2.65 | 2.77 | 2.89 | 3.01 | 3.12
Finley | 9R4 | 132 | TransGrid Finley 132/66kV STS | Mulwala ZS | 140 | 0 | 0 | 0 | 0 | 0
Finley | 84A | 66 | TransGrid Finley 132/66kV STS | Jerilderie ZS | 15 | 6.04 | 6.12 | 6.19 | 6.26 | 6.32
Finley | 84B | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 2.82 | 2.92 | 3.02 | 3.11 | 3.2
Finley | 84C | 66 | TransGrid Finley 132/66kV STS | Finley ZS | 61 | 5.23 | 5.42 | 5.6 | 5.77 | 5.94
Goulburn | 972 | 132 | TransGrid Marulan 330/132kV STS | Goulburn 132/66/33kV STS | 180 | 121.8 | 123.23 | 124.57 | 125.84 | 127.05
Goulburn | 9UR | 132 | TransGrid Marulan 330/132kV STS | Taralga Wind Farm | 140 | 0 | 0 | 0 | 0 | 0
Goulburn | 843 | 66 | Clinton St ZS | Goulburn North ZS | 46 | 2.17 | 2.32 | 2.45 | 2.59 | 2.72
Goulburn | 82K/2 | 66 | Woodlawn ZS | Bungendore ZS | 28 | 0 | 0 | 0 | 0 | 0
Goulburn | 840:GOU | 66 | Goulburn 132/66/33kV STS | Goulburn North ZS | 61 | 6.12 | 6.45 | 6.76 | 7.07 | 7.35
Goulburn | 841:GBN | 66 | Goulburn North ZS | Crookwell ZS | 9 | 2.92 | 3.09 | 3.24 | 3.39 | 3.53
Goulburn | 850:GOU | 66 | Goulburn 132/66/33kV STS | Woodlawn ZS | 28 | 4.48 | 4.54 | 4.6 | 4.65 | 4.71
Goulburn | 86M/1 | 66 | Goulburn 132/66/33kV STS | Marulan North Tee | 25 | 2 | 2.15 | 2.29 | 2.42 | 2.54
Goulburn | 86M/2 | 66 | Marulan North Tee | Marulan South ZS | 25 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Goulburn | 86L | 66 | Marulan North Tee | Marulan North ZS | 12 | 2.2 | 2.37 | 2.52 | 2.67 | 2.8
Goulburn | 870:GOU | 66 | Goulburn 132/66/33kV STS | Clinton St ZS | 34 | 11.73 | 12.44 | 13.11 | 13.76 | 14.37
Goulburn | GOU12 | 33 | Goulburn 132/66/33kV STS | Brisbane Grove ZS | 7 | 1.65 | 1.76 | 1.86 | 1.96 | 2.05
Griffith | 79C/1 | 33 | TransGrid Griffith 132/33kV STS | Widgelli / Willbriggie Tee | 10 | 3.4 | 3.48 | 3.56 | 3.63 | 3.7
Griffith | 79C/2 | 33 | Widgelli / Willbriggie Tee | Widgelli ZS | 10 | 0.66 | 0.67 | 0.69 | 0.7 | 0.72
Griffith | 79C/3 | 33 | Widgelli / Willbriggie Tee | Willbriggie Tee | 10 | 2.74 | 2.8 | 2.87 | 2.93 | 2.98
Griffith | 79C/4 | 33 | Willbriggie Tee | Willbriggie ZS | 10 | 2.43 | 2.49 | 2.55 | 2.6 | 2.65
Griffith | 79C/5 | 33 | Willbriggie Tee | 79C / 79P Tee | 10 | 0.3 | 0.31 | 0.32 | 0.33 | 0.33
Griffith | 79F | 33 | TransGrid Griffith 132/33kV STS | Yenda ZS | 22 | 6.64 | 6.8 | 6.95 | 7.1 | 7.24
Griffith | 79G | 33 | Beelbangera ZS | Griffith ZS | 10 | 0 | 0 | 0 | 0 | 0
Griffith | 79J | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 51 | 0 | 0 | 0 | 0 | 0
Griffith | 79L | 33 | TransGrid Griffith 132/33kV STS | Beelbangera ZS | 22 | 7.4 | 7.58 | 7.75 | 7.91 | 8.07
Griffith | 79M | 33 | TransGrid Griffith 132/33kV STS | Hanwood ZS | 22 | 1.9 | 1.95 | 2.01 | 2.06 | 2.11
Griffith | 79P | 33 | TransGrid Griffith 132/33kV STS | Warrawidgee Tee | 22 | 5.22 | 5.35 | 5.47 | 5.58 | 5.69
Griffith | 79W/1 | 33 | Warrawidgee Tee | Warrawidgee ZS | 6 | 1.22 | 1.25 | 1.27 | 1.3 | 1.33
Griffith | 79W/2 | 33 | Warrawidgee Tee | Nericon Tee | 21 | 3.65 | 3.74 | 3.82 | 3.9 | 3.98
Griffith | 79W/3 | 33 | Nericon Tee | Nericon ZS | 20 | 1.62 | 1.66 | 1.7 | 1.73 | 1.77
Griffith | 79R | 33 | TransGrid Griffith 132/33kV STS | Tharbogang ZS | 31 | 6.15 | 6.46 | 6.76 | 7.04 | 7.31
Griffith | 79U | 33 | TransGrid Griffith 132/33kV STS | Griffith ZS | 53 | 8.78 | 9.21 | 9.63 | 10.03 | 10.41
Harden - Murrumburrah | 836 | 66 | TransGrid Murrumburrah 132/66kV STS | Cootamundra ZS | 20 | 13.22 | 13.82 | 14.38 | 14.91 | 15.42
Harden - Murrumburrah | 837 | 66 | TransGrid Murrumburrah 132/66kV STS | Jugiong ZS | 12 | 0.27 | 0.28 | 0.29 | 0.3 | 0.31
Harden - Murrumburrah | 847 | 66 | TransGrid Murrumburrah 132/66kV STS | Boorowa ZS | 10 | 4.07 | 4.17 | 4.27 | 4.37 | 4.46
Harden - Murrumburrah | 823/3 | 66 | Bogalara Sw Stn | Marilba ZS | 12 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 830/1:PCR | 66 | Bogalara Sw Stn | Parsons Creek ZS | 11 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 838/3 | 66 | Jugiong ZS | Bogalara Sw Stn | 12 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 83A | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 2.61 | 2.78 | 2.93 | 3.07 | 3.21
Harden - Murrumburrah | 83D | 66 | TransGrid Murrumburrah 132/66kV STS | Murrumburrah ZS | 15 | 0 | 0 | 0 | 0 | 0
Harden - Murrumburrah | 890:YOU | 66 | TransGrid Murrumburrah 132/66kV STS | Young ZS | 24 | 7.43 | 7.87 | 8.28 | 8.68 | 9.06
Moruya North | 98H | 132 | Endeavour Energy Evans Lane Sw Stn | Moruya North 132/33kV STS | 180 | 14.84 | 15.88 | 16.85 | 17.77 | 18.64
Moruya North | 98M | 132 | Endeavour Energy Evans Lane Sw Stn | Batemans Bay ZS | 50 | 13.13 | 14.04 | 14.9 | 15.72 | 16.49
Moruya North | 98T | 132 | Batemans Bay ZS | Moruya North 132/33kV STS | 61 | 2.85 | 3.05 | 3.24 | 3.42 | 3.58
Moruya North | 7703 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 30 | 5.2 | 5.56 | 5.9 | 6.22 | 6.52
Moruya North | 7704 | 33 | Moruya North 132/33kV STS | Moruya Town ZS | 26 | 6.65 | 7.11 | 7.55 | 7.95 | 8.34
Moruya North | 7706 | 33 | Moruya North 132/33kV STS | Mossy Point ZS | 25 | 6.41 | 6.88 | 7.31 | 7.73 | 8.12
Moruya North | 7712 | 33 | Bodalla Tee | Bodalla ZS | 10 | 1.09 | 1.16 | 1.23 | 1.29 | 1.35
Moruya North | 7713 | 33 | Bodalla Tee | Narooma ZS | 21 | 0 | 0 | 0 | 0 | 0
Moruya North | 7817 | 33 | Narooma Tee | Cobargo ZS | 10 | 0 | 0 | 0 | 0 | 0
Moruya North | 7711/1 | 33 | Moruya Town ZS | Tuross Tee | 17 | 3.08 | 3.29 | 3.5 | 3.69 | 3.87
Moruya North | 7711/2 | 33 | Tuross Tee | Tuross ZS | 7 | 2.31 | 2.48 | 2.64 | 2.78 | 2.92
Moruya North | 7711/3 | 33 | Tuross Tee | Bodalla Tee | 21 | 1.12 | 1.19 | 1.26 | 1.33 | 1.39
Moruya North | 7715/1 | 33 | Moruya Town ZS | Narooma Tee | 30 | 4.63 | 4.95 | 5.26 | 5.54 | 5.82
Moruya North | 7715/2 | 33 | Narooma Tee | Narooma ZS | 10 | 4.42 | 4.73 | 5.02 | 5.29 | 5.55
Morven | 996/1 | 132 | TransGrid 132kV Line 996 Tee | Morven 132/66kV STS | 45 | 0 | 0 | 0 | 0 | 0
Morven | 83M/3 | 66 | Morven 132/66kV STS | Culcairn ZS | 15 | 2.49 | 2.6 | 2.71 | 2.81 | 2.91
Morven | 83M/4 | 66 | Morven 132/66kV STS | Holbrook ZS | 15 | 1.87 | 1.96 | 2.05 | 2.13 | 2.21
Munyang | 56 | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.22 | 0.24 | 0.25 | 0.26 | 0.27
Munyang | 57A | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.06 | 0.07 | 0.07 | 0.08 | 0.08
Munyang | 57B | 33 | Smiggin Sw Stn | Perisher ZS | 20 | 0.04 | 0.04 | 0.05 | 0.05 | 0.06
Munyang | No.1 Perisher | 33 | TransGrid Munyang 132/33kV STS | Smiggin Sw Stn | 38 | 0.22 | 0.24 | 0.25 | 0.26 | 0.27
Munyang | No.2 Perisher/1 | 33 | TransGrid Munyang 132/33kV STS | Blue Cow Tee | 38 | 0.11 | 0.12 | 0.13 | 0.14 | 0.15
Munyang | No.2 Perisher/2 | 33 | Blue Cow Tee | Smiggin Sw Stn | 38 | 0.1 | 0.11 | 0.12 | 0.13 | 0.14
Munyang | 60/2 | 33 | Bullocks Portal ZS | Bullocks Flat ZS | 19 | 0.2 | 0.21 | 0.22 | 0.23 | 0.24
Munyang | 58 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Munyang | 59 | 33 | Bullocks Flat ZS | Thredbo ZS | 6 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Munyang | Bullocks Portal Line | 33 | Perisher ZS | Bullocks Portal ZS | 20 | 0.22 | 0.24 | 0.25 | 0.26 | 0.27
Queanbeyan | 97Y | 132 | TransGrid Williamsdale 330/132kV STS | Googong Town ZS | 91 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 975 | 132 | TransGrid Queanbeyan 132/66kV STS | South Jerrabomberra ZS | 140 | 10.94 | 11.79 | 12.58 | 13.32 | 14.03
Queanbeyan | 9MU | 132 | South Jerrabomberra ZS | Googong Town ZS | 91 | 10.94 | 11.79 | 12.58 | 13.32 | 14.03
Queanbeyan | 82A | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 8.85 | 9.51 | 10.12 | 10.7 | 11.24
Queanbeyan | 82B | 66 | TransGrid Queanbeyan 132/66kV STS | Queanbeyan South ZS | 30 | 6.64 | 7.13 | 7.59 | 8.02 | 8.43
Queanbeyan | 82F | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 49 | 7.32 | 7.85 | 8.35 | 8.82 | 9.27
Queanbeyan | 82G | 66 | TransGrid Queanbeyan 132/66kV STS | Captains Flat ZS | 12 | 2.84 | 3.01 | 3.18 | 3.33 | 3.48
Queanbeyan | 82K | 66 | TransGrid Queanbeyan 132/66kV STS | Sutton / Bungendore Tee | 28 | 10.33 | 10.97 | 11.57 | 12.14 | 12.69
Queanbeyan | 82K/1 | 66 | Sutton / Bungendore Tee | Bungendore ZS | 28 | 7.2 | 7.65 | 8.07 | 8.47 | 8.85
Queanbeyan | 82K/3 | 66 | Sutton / Bungendore Tee | Sutton ZS | 28 | 3.13 | 3.32 | 3.5 | 3.67 | 3.84
Queanbeyan | 82M | 66 | TransGrid Queanbeyan 132/66kV STS | Oaks Estate ZS | 20 | 0 | 0 | 0 | 0 | 0
Queanbeyan | 830:QSH | 66 | Queanbeyan South ZS | Googong Dam ZS | 15 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Steeple Flat | 97C | 132 | Steeple Flat 132/66kV STS | Boco Rock Wind Farm | 184 | 0 | 0 | 0 | 0 | 0
Steeple Flat | 97R/2 | 132 | Steeple Flat 132/66kV STS | Bega 132/66kV STS | 163 | 10.67 | 11.39 | 12.06 | 12.7 | 13.3
Steeple Flat | 84R/5 | 66 | Steeple Flat 132/66kV STS | Brown Mountain Hydro | 70 | 0 | 0 | 0 | 0 | 0
Steeple Flat | 810/4 | 66 | Steeple Flat 132/66kV STS | Bombala ZS | 21 | 1.09 | 1.17 | 1.24 | 1.31 | 1.37
Steeple Flat | 84R/3 | 66 | Brown Mountain Hydro | Quira ZS | 70 | 0.77 | 0.83 | 0.89 | 0.94 | 0.99
Temora | 901 | 132 | Temora 132/66 STS | Wyalong Switching Station | 108 | 82 | 82 | 82 | 82 | 82
Temora | 9JW | 132 | Wyalong Switching Station | West Wyalong Switching Station | 108 | 73 | 73 | 73 | 73 | 73
Temora | 9JX | 132 | West Wyalong Switching Station | Lake Cowal | 108 | 0 | 0 | 0 | 0 | 0
Temora | 4 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 0 | 0 | 0 | 0 | 0
Temora | 5 | 66 | Temora 132/66 STS | Ariah Park Tee | 21 | 90.32 | 90.64 | 90.95 | 91.23 | 91.51
Temora | 6 | 66 | Temora 132/66 STS | Temora Town ZS | 15 | 6.65 | 6.92 | 7.18 | 7.42 | 7.65
Temora | 20-60 | 66 | Ariah Park Tee | West Wyalong ZS | 21 | 75.27 | 75.54 | 75.79 | 76.03 | 76.26
Temora | 60-70 | 66 | West Wyalong ZS | Anona ZS | 7 | 0.61 | 0.65 | 0.68 | 0.71 | 0.74
Temora | 80-140/1 | 66 | Ariah Park Tee | Ariah Park ZS | 15 | 15.05 | 15.11 | 15.16 | 15.21 | 15.25
Temora | 80-140/2 | 66 | Ariah Park ZS | Ardlethan ZS | 11 | 0.4 | 0.43 | 0.45 | 0.47 | 0.49
Temora | 835/J | 66 | Junee Reefs ZS | Junee ZS | 12 | 0 | 0 | 0 | 0 | 0
Temora | 835/T | 66 | Temora 132/66 STS | Junee Reefs ZS | 12 | 0.14 | 0.14 | 0.15 | 0.15 | 0.15
Tumut | 827 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 5.06 | 5.36 | 5.64 | 5.91 | 6.16
Tumut | 828 | 66 | TransGrid Tumut 132/66kV STS | Gundagai South ZS | 11 | 2.3 | 2.41 | 2.52 | 2.62 | 2.72
Tumut | 829 | 66 | TransGrid Tumut 132/66kV STS | Tumut ZS | 28 | 0 | 0 | 0 | 0 | 0
Tumut | 831 | 66 | Gundagai South ZS | Nangus ZS | 11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Tumut | 848 | 66 | Adelong Tee | Adelong ZS | 12 | 1.03 | 1.08 | 1.13 | 1.18 | 1.23
Tumut | 830/2:GUN | 66 | Gundagai South ZS | Parsons Creek ZS | 11 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14
Tumut | 848/1 | 66 | Adelong Tee | Batlow ZS | 21 | 3.36 | 3.52 | 3.68 | 3.83 | 3.97
Tumut | 848/2 | 66 | Batlow ZS | Tumbarumba ZS | 22 | 2.58 | 2.69 | 2.8 | 2.91 | 3.01
Tumut | 848/3 | 66 | TransGrid Tumut 132/66kV STS | Adelong Tee | 21 | 4.19 | 4.39 | 4.58 | 4.77 | 4.96
Tumut | 850:TAL | 66 | TransGrid Tumut 132/66kV STS | Talbingo ZS | 18 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
Wagga (Copland St) | 83L | 66 | Hammond Ave ZS | Bomen ZS | 54 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Uranquinty ZS | 64 | 3.61 | 3.81 | 4.01 | 4.19 | 4.36
Wagga (Copland St) | 840/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bulgary ZS | 15 | 1.59 | 1.66 | 1.73 | 1.8 | 1.86
Wagga (Copland St) | 840/2 | 66 | Bulgary ZS | Lockhart ZS | 15 | 1.59 | 1.66 | 1.73 | 1.8 | 1.86
Wagga (Copland St) | 840/3 | 66 | Lockhart Tee | Kywong ZS | 16 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 83M/1 | 66 | Uranquinty ZS | Henty ZS | 15 | 1.3 | 1.35 | 1.41 | 1.46 | 1.51
Wagga (Copland St) | 83M/2 | 66 | Henty ZS | Culcairn ZS | 15 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8W9 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Ashmont ZS | 34 | 8.38 | 8.99 | 9.55 | 10.08 | 10.58
Wagga (Copland St) | 8WF/1 | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Bourkelands Tee | 34 | 7.52 | 8.05 | 8.55 | 9.02 | 9.47
Wagga (Copland St) | 8WF/2 | 66 | Bourkelands Tee | Kooringal ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WF/3 | 66 | Bourkelands Tee | Bourkelands ZS | 42 | 7.52 | 8.05 | 8.55 | 9.02 | 9.47
Wagga (Copland St) | 8WM | 66 | Hammond Ave ZS | Morrow St ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WO | 66 | Ashmont ZS | Bourkelands ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WP | 66 | Morrow St ZS | Cartwrights Hill ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga (Copland St) | 8WR | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 1.9 | 2 | 2.09 | 2.18 | 2.27
Wagga (Copland St) | 8WT | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Hammond Ave ZS | 52 | 1.79 | 1.88 | 1.97 | 2.05 | 2.14
Wagga (Copland St) | 8WG | 66 | TransGrid Wagga 132/66kV STS (Copland St) | Kooringal ZS | 34 | 9.06 | 9.68 | 10.26 | 10.81 | 11.34
Wagga North | 99U | 132 | TransGrid Wagga North 132/66kV STS | Sebastopol Sw Stn | 128 | 75 | 75 | 75 | 75 | 75
Wagga North | 9J6 | 132 | Sebastopol Sw Stn | Temora 132/66 STS | 128 | 110.4 | 110.79 | 111.16 | 111.51 | 111.85
Wagga North | 9J5/1 | 132 | TransGrid Wagga North 132/66kV STS | Junee 132/66/11kV ZS | 140 | 140.5 | 141 | 141.47 | 141.92 | 142.35
Wagga North | 9J5/2 | 132 | Junee 132/66/11kV ZS | Temora 132/66 STS | 140 | 109.67 | 110.11 | 110.53 | 110.93 | 111.32
Wagga North | 30-90 | 66 | Junee ZS | Coolamon ZS | 6 | 2.95 | 3.12 | 3.28 | 3.44 | 3.59
Wagga North | 834:JUN | 66 | Junee ZS | Bethungra ZS | 11 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54
Wagga North | 83C/1 | 66 | TransGrid Wagga North 132/66kV STS | Oura ZS | 24 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52
Wagga North | 83C/2 | 66 | Oura ZS | Forest Hill ZS | 34 | 0 | 0 | 0 | 0 | 0
Wagga North | 83G | 66 | TransGrid Wagga North 132/66kV STS | Bomen ZS | 34 | 5.86 | 6.13 | 6.38 | 6.62 | 6.84
Wagga North | 83J | 66 | Bomen ZS | Cartwrights Hill ZS | 34 | 4.44 | 4.72 | 4.99 | 5.24 | 5.48
Wagga North | 850:BET | 66 | Bethungra ZS | Cootamundra ZS | 12 | 0 | 0 | 0 | 0 | 0
Wagga North | 7CH/1 | 33 | Cartwrights Hill ZS | Euberta ZS | 4 | 0.64 | 0.67 | 0.71 | 0.74 | 0.77
Wagga North | 7CH/2 | 33 | Euberta ZS | Ganmurra ZS | 4 | 0.23 | 0.24 | 0.25 | 0.26 | 0.27
Wagga North | Oura-Mates Gully | 33 | Oura ZS | Mates Gully ZS | 3 | 0.83 | 0.86 | 0.9 | 0.93 | 0.96
Wagga North | Mates Gully-Tarcutta | 33 | Mates Gully ZS | Tarcutta ZS | 4 | 0.45 | 0.47 | 0.49 | 0.51 | 0.53
Wagga North | 8WJ | 66 | TransGrid Wagga North 132/66kV STS | Forest Hill ZS | 11 | 2.25 | 2.39 | 2.52 | 2.64 | 2.75
Yanco | 840/4 | 66 | Narrandra ZS | Kywong ZS | 16 | 0.11 | 0.12 | 0.12 | 0.13 | 0.14
Yanco | 841:YNC | 66 | TransGrid Yanco 132/33/66kV STS | Narrandera ZS | 15 | 6.36 | 6.54 | 6.71 | 6.87 | 7.04
Yanco | 7L3 | 33 | TransGrid Yanco 132/33/66kV STS | Cudgel ZS | 8 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Yanco | 7L6/1 | 33 | TransGrid Yanco 132/33/66kV STS | Whitton / Murrami Tee | 15 | 2.11 | 2.15 | 2.2 | 2.24 | 2.28
Yanco | 7L6/2 | 33 | Whitton / Murrami Tee | Whitton ZS | 8 | 0.79 | 0.83 | 0.87 | 0.9 | 0.94
Yanco | 7L6/3 | 33 | Whitton / Murrami Tee | Murrami ZS | 6 | 0.32 | 0.32 | 0.33 | 0.34 | 0.34
Yanco | 7L5/1 | 33 | TransGrid Yanco 132/33/66kV STS | Yanco ZS | 8 | 4.44 | 4.69 | 4.92 | 5.14 | 5.34
Yanco | 7L5/2 | 33 | Yanco ZS | Leeton ZS | 6 | 3.25 | 3.43 | 3.6 | 3.76 | 3.91
Yanco | 7L4 | 33 | TransGrid Yanco 132/33/66kV STS | Leeton ZS | 31 | 3.53 | 3.72 | 3.89 | 4.07 | 4.23
Yass | 971(1) | 132 | TransGrid Yass 330/132/66kV STS | Cullerin Range Wind Farm | 106 | 0 | 0 | 0 | 0 | 0
Yass | 971(2) | 132 | Cullerin Range Wind Farm | Gunning Wind Farm | 140 | 0 | 0 | 0 | 0 | 0
Yass | 971(3) | 132 | Cullerin Range Wind Farm | Goulburn 132/66/33kV STS | 106 | 0 | 0 | 0 | 0 | 0
Yass | 976/2 (M) | 132 | TransGrid 132kV Line 976/2(Y) / Murrumbateman Tee | Murrumbateman ZS | 42 | 5.89 | 6.28 | 6.66 | 7.01 | 7.35
Yass | 824 | 66 | TransGrid Yass 330/132/66kV STS | Yass ZS | 12 | 8.14 | 8.64 | 9.12 | 9.57 | 10
Yass | 823/5 | 66 | Yass ZS | Marilba ZS | 12 | 0.93 | 0.99 | 1.05 | 1.1 | 1.15

## BSP Export
Connection Point | Forecast PF | Summer Forecast (POE50 MW)
|  | 25/26 | 26/27 | 27/28 | 28/29 | 29/30
Albury (Corowa) | 0.355 | 39.72 | 39.98 | 40.23 | 40.46 | 40.69
Albury (Mulwala) | 0.58 | 9.62 | 9.89 | 10.15 | 10.39 | 10.63
Albury (Union Rd + Jelbart) | -0.82 | 41.49 | 44.17 | 46.69 | 49.08 | 51.36
Armidale | -0.999 | 26.19 | 27.52 | 28.78 | 29.98 | 31.12
Balranald | 0.258 | 0.82 | 0.83 | 0.85 | 0.87 | 0.88
Beryl | 0.961 | 99.64 | 100.15 | 100.63 | 101.1 | 101.54
Boambee South | -0.808 | 12.88 | 13.72 | 14.52 | 15.27 | 15.99
Broken Hill 22kV | -0.995 | 21.03 | 22.44 | 23.76 | 25.02 | 26.22
Casino | 0.375 | 13.34 | 14.06 | 14.74 | 15.39 | 16.01
Coffs Harbour | -0.281 | 37.27 | 39.76 | 42.1 | 44.31 | 46.42
Coleambally | 0.91 | 6.92 | 7.01 | 7.1 | 7.19 | 7.27
Cooma 132kV | -0.938 | 23.15 | 24.7 | 26.16 | 27.54 | 28.86
Cooma 66kV | -0.366 | 5.99 | 6.32 | 6.62 | 6.92 | 7.2
Cowra | 0.828 | 31.87 | 32.88 | 33.83 | 34.74 | 35.6
Darlington Point | 0.807 | 91.33 | 91.66 | 91.97 | 92.27 | 92.55
Deniliquin | 0.879 | 22.08 | 23.12 | 24.11 | 25.06 | 25.96
Dorrigo | -0.512 | 1.72 | 1.81 | 1.9 | 1.99 | 2.07
Dunoon | -0.853 | 4.59 | 4.88 | 5.15 | 5.41 | 5.65
Evans Lane | 1 | 0 | 0 | 0 | 0 | 0
Finley 132kV | 1 | 0 | 0 | 0 | 0 | 0
Finley 66kV | -0.746 | 1.47 | 1.54 | 1.6 | 1.66 | 1.72
Forbes | 0.764 | 61.76 | 62.38 | 62.97 | 63.54 | 64.08
Glen Innes | -0.679 | 10.81 | 11.25 | 11.66 | 12.05 | 12.43
Griffith | 0.912 | 50.69 | 51.9 | 53.06 | 54.18 | 55.24
Gunnedah 66kV | -0.998 | 16.97 | 17.71 | 18.41 | 19.07 | 19.69
Hawks Nest | 1 | 0 | 0 | 0 | 0 | 0
Herons Ck | -0.974 | 9.06 | 9.57 | 10.06 | 10.52 | 10.97
Inverell | 0.451 | 34.22 | 34.97 | 35.7 | 36.4 | 37.07
Kempsey 33kV | -0.672 | 17.91 | 19.11 | 20.24 | 21.3 | 22.32
Koolkhan | -0.696 | 35.31 | 37.33 | 39.26 | 41.09 | 42.84
Lismore 132kV | 0.278 | 66.7 | 69.17 | 71.51 | 73.75 | 75.89
Macksville | -0.99 | 7.15 | 7.63 | 8.09 | 8.52 | 8.93
Manildra | 0.78 | 44.7 | 44.76 | 44.81 | 44.86 | 44.91
Marulan | 0.518 | 135.33 | 136.92 | 138.41 | 139.82 | 141.17
Merbein | 0.334 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48
Mildura | 0.986 | 6.59 | 6.59 | 6.59 | 6.59 | 6.59
Molong | -0.462 | 31.45 | 31.62 | 31.78 | 31.93 | 32.08
Moree | 0.979 | 69.52 | 69.97 | 70.4 | 70.81 | 71.22
Morven | -0.976 | 4.27 | 4.47 | 4.66 | 4.84 | 5.02
Mudgee | -0.995 | 11.74 | 12.45 | 13.12 | 13.76 | 14.38
Mullumbimby | 1 | 50.83 | 53.87 | 56.74 | 59.47 | 62.08
Munyang | 0.483 | 0.35 | 0.38 | 0.41 | 0.44 | 0.47
Murrumbateman | -0.992 | 5.89 | 6.28 | 6.66 | 7.01 | 7.35
Murrumburrah | 1 | 23.37 | 24.52 | 25.61 | 26.64 | 27.63
Nambucca | -0.561 | 5.59 | 5.97 | 6.33 | 6.66 | 6.98
Narrabri | 0.861 | 32.29 | 32.93 | 33.54 | 34.13 | 34.69
Orange 132kV | 0.999 | 140.12 | 140.12 | 140.12 | 140.12 | 140.12
Orange 66kV | -0.986 | 34.75 | 37.13 | 39.36 | 41.48 | 43.49
Panorama | -0.953 | 37.64 | 40.05 | 42.3 | 44.44 | 46.46
Parkes 132kV | 1 | 0 | 0 | 0 | 0 | 0
Parkes 66kV | 0.979 | 124.49 | 125.11 | 125.69 | 126.25 | 126.78
Port Macquarie | -0.951 | 50.85 | 54.27 | 57.49 | 60.54 | 63.45
Queanbeyan 132kV | -0.955 | 10.94 | 11.79 | 12.58 | 13.32 | 14.03
Queanbeyan 66kV | -0.934 | 33.82 | 36.22 | 38.46 | 40.59 | 42.6
Raleigh | -0.907 | 6.86 | 7.29 | 7.69 | 8.07 | 8.43
Robinvale | 0.983 | 1.38 | 1.4 | 1.42 | 1.44 | 1.46
Snowy Adit | 1 | 0 | 0 | 0 | 0 | 0
Stroud | -0.992 | 17.34 | 18.4 | 19.4 | 20.35 | 21.27
Tamworth | 0.993 | 53.29 | 56.16 | 58.88 | 61.45 | 63.91
Taree 33kV | 0.012 | 11.01 | 11.7 | 12.35 | 12.97 | 13.56
Taree 66kV | -0.963 | 30.96 | 33.15 | 35.2 | 37.14 | 38.98
Tenterfield | -0.983 | 3.47 | 3.64 | 3.81 | 3.98 | 4.13
Terranora | -1 | 92 | 96.06 | 99.91 | 103.58 | 107.09
Tumut | 0.981 | 23.91 | 24.55 | 25.15 | 25.73 | 26.29
Upper Tumut | 1 | 0 | 0 | 0 | 0 | 0
Wagga 66kV | -0.939 | 33.86 | 36.12 | 38.24 | 40.25 | 42.17
Wagga North 132kV | 0.908 | 250.9 | 251.79 | 252.63 | 253.43 | 254.2
Wagga North 66kV | 0.524 | 10.12 | 10.85 | 11.54 | 12.19 | 12.8
Waggamba | 1 | 0 | 0 | 0 | 0 | 0
Wallerawang 132kV | 1 | 0 | 0 | 0 | 0 | 0
Wallerawang 66kV | 0.835 | 2.83 | 3 | 3.17 | 3.33 | 3.48
Wellington 132kV | 0.866 | 298.77 | 302.36 | 305.77 | 309.02 | 312.13
Yanco | 0.858 | 27.95 | 28.65 | 29.31 | 29.94 | 30.55
Yass 132kV | 0.875 | 77.27 | 77.27 | 77.27 | 77.27 | 77.27
Yass 66kV | -0.996 | 8.87 | 9.41 | 9.93 | 10.42 | 10.88

## System Limitations
Feeder - Terranora - MWN3B2 Norco
Feeder - Lismore - AVE3B2 Alstonville 2
Feeder - Lismore - EWE3B1 Brunswick No.1
Feeder - Lismore - MUL3B3 Mullumbimby West
Feeder - Lismore - MUL3B3 Mullumbimby West
Feeder - Lismore - WBN3B4 Broadwater
Feeder - Lismore - WBN3B3 Coraki
Feeder - Casino - CSO3B3 Leeville
Feeder - Grafton - SGN3B1 Armidale Rd
Feeder - Grafton - SGN3B1 Armidale Rd
Feeder - Grafton - MLN3B4 Townsend
Feeder - Grafton - MLN3B5 Woodford Dale-Leigh
Feeder - Grafton - YAM3B4 Yamba West
Feeder - Coffs Harbour - NGN3B2 Coramba
Feeder - Coffs Harbour - WGA3B6 Corindi
Feeder - Kempsey - MGA3B1 Turners Flat
Feeder - Kempsey - PSK3B4 Industrial
Feeder - Port Macquarie - LKC7781 Cathie Sth
Feeder - Port Macquarie - OPM3B1 Granite St
Feeder - Taree - BNK24787 Old Bar No.2
Feeder - Taree - HGN3B1 Crowdy Head
Feeder - Taree - WGM3B5 Hillside
Feeder - Stroud - BLH3B3 Bulahdelah Nth/Markwell/Newells Ck
Feeder - Hawks Nest - TEA3B4 Tea Gardens
Feeder - Hawks Nest - TEA3B3 Mineral Deposits
Feeder - Armidale - GLS3B2 Rockvale
Feeder - Armidale - GLS3B7 City Central
Feeder - Armidale - GLS3B1 Gara
Feeder - Armidale - HGE3B1 Grafton Rd
Feeder - Armidale - HGE3B1 Grafton Rd
Feeder - Armidale - UNI3B2 Tilbuster/Puddledock
Feeder - Armidale - WLS3B1 Walcha East
Feeder - Armidale - WLS8B5 Uralla/Walcha Rd/Wollun
Feeder - Inverell - BGA2K13 Horton Valley
Feeder - Inverell - BTS8B11 Inverell West
Feeder - Inverell - TXS3X06 Yelarbon
Feeder - Inverell - TXS3X06 Yelarbon
Feeder - Waggamba - GDI8B6 Goondiwindi Town Sth
Feeder - Moree - MRE8B4 Western Rural
Feeder - Moree - WTR8B2 Poison Gate
Feeder - Gunnedah - BBI1101 M11 Ghoolendaadi
Feeder - Tamworth - ATA3B1 Attunga
Feeder - Tamworth - NDL3B2 Woolomin
Feeder - Tamworth - ETH3B14 King George Ave
Feeder - Tamworth - ETH3B11 Coles/White
Feeder - Tamworth - ETH3B7 TCC/Calala
Feeder - Tamworth - STH3B9 Winton
Feeder - Tamworth - WCK516 Dewhurst/Gordon
Feeder - Beryl - DNO132 Dunedoo No.1
Feeder - Beryl - CBB8B1 Tambar Springs
Feeder - Wellington - WGN72 Yeoval
Feeder - Wellington - WGN72 Yeoval
Feeder - Dubbo - DBS3B8 Margaret Cres
Feeder - Dubbo - GID22 Rural Nth/Sth/West
Feeder - Dubbo - GID12 Gilgandra Town No.1
Feeder - Dubbo - GGB112 Gulargambone
Feeder - Dubbo - NME8B3 Trangie Rural
Feeder - Nyngan - BKE4B2 M82 Wanaaring
Feeder - Broken Hill - MTG4B1 Tibooburra Backbone Line
Feeder - Broken Hill - MTG4B1 Tibooburra Backbone Line
Feeder - Broken Hill - BHL42 Railwaytown
Feeder - Orange - ORS3B5 Lords Place
Feeder - Orange - ORS3B3 Email (Electrolux)
Feeder - Orange - ORS3B7 Anson St Sth
Feeder - Bathurst - BNY3B4 Millthorpe
Feeder - Bathurst - BNY3B4 Millthorpe
Feeder - Bathurst - MUA5006 West
Feeder - Bathurst - RAG3B5 OConnell
Feeder - Bathurst - RAG3B5 OConnell
Feeder - Bathurst - RAG3B6 Limekilns
Feeder - Bathurst - BTH92 Lagoon/Trunkey
Feeder - Bathurst - BTH82 Lloyds Rd
Feeder - Bathurst - BTH72 City Central
Feeder - Bathurst - BTH92 Lagoon/Trunkey
Feeder - Bathurst - SWT12 Stewarts Mt
Feeder - Bathurst - SWT42 Simplot
Feeder - Parkes - PKH32 Peak Hill
Feeder - Parkes - TDL8B2 Tullamore/Tottenham
Feeder - Moruya North - MYT3B2 Kiora
Feeder - Bega - ESH3B5 Boydtown
Feeder - Steeple Flat - BOM8B2 Nimmitabel
Feeder - Goulburn - MRN8B3 Marulan Town
Feeder - Goulburn - WOO3B2 Rural Fdr 2
Feeder - Cowra - CWD13 Cargo
Feeder - Yass - YAS6242 Yass Town Sth
Feeder - Wagga (Copland St) - KOO3B1 Plumpton Rd
Feeder - Wagga (Copland St) - KOO3B6 Lake Albert
Feeder - Morven - HOL1890 Wantagong/Woomargama
Feeder - Albury - CRA32 Corowa Town No.2
Feeder - Albury - CRA42 Corurgan
Feeder - Albury - MWA8B4 North St and Rural
Feeder - Finley - FIN52 Tocumwal
Feeder - Deniliquin - MOA8B2 Moama West
Feeder - Darlington Point - HAT42 Hay 132 - Carrathool
Feeder - Darlington Point - HIL1401 Upper Lachlan
Feeder - Griffith - GFH3B6 Illilliwa
Feeder - Griffith - THA2223 West End
Feeder - Yanco - YAN2319 Euroley Rd

## Comments
A 30MW biomass generator is located at Condong and is connected to the Terranora 110/66kV sub-transmission substation at 66kV via feeders 9504, 9514 and 9502.
A 30MW biomass generator is located at Broadwater and is connected to the Lismore 132/66kV sub-transmission substation at 66kV via feeder 0892.
The Nymboida hydro generation has reached end of life so has been decommissioned.
The 5MW hydro generation at Oaky is presently decommissioned after failure of the dam wall.
A 5MW solar generator is connected to Galloway St zone substation on the 11kV network.
A 2.7MW solar generator is connected to Madgwick Drive zone substation on the 11kV network.
A 5.5MW hydro generator is located at Pindari Dam and is connected to the Transgrid Glen Innes 132/66kV sub-transmission substation at 66kV via feeders 6AE, 6NE, 886 and 887.
A 23MW hydro generator is located at Copeton Dam and is connected to the Transgrid Inverell 132/66kV sub-transmission substation at 66kV via feeders 6BC, 734 and 735.
A 56MW solar generator is located at Moree Solar Farm and is connected to Transgrid’s Moree 132/66kV sub-transmission substation at 66kV via feeder 876.
A 5MW solar generator is located at Wenna on the 22kV network.
A 5MW solar generator is located at Wathagar on the 22kV network.
A 5MW solar generator is located at Ashley on the 22kV network.
A 10MW and 6MW gas generator located at Wilga Park is connected to the Transgrid Narrabri 132/66kV sub-transmission substation at 66kV via feeder 861.
A 7MW hydro generator is located at Lake Keepit and is connected to the Transgrid Gunnedah 132/66kV sub-transmission substation at 66kV via feeder 877.
A 4.99MW solar generator is connected to Kootingal zone substation on the 11kV network.
A 4.99MW solar generator is connected to Werris Creek zone substation on the 11kV network.
A 4.95MW solar generator is connected to Manilla zone substation on the 11kV network.
A 1.76MW solar generator is connected to Goddard Lane zone substation on the 11kV network.
A 9.2MW solar generator is located at Narromine on the 22kV network, and a 14.5MW solar generator is connected at Dubbo South on the 11kV network.
A 105MW solar generator is located at Nevertire and is connected to the Dubbo 132/66kV sub-transmission substation at 132kV via the feeder 94W.
A 5MW solar generator is located at Nyngan Town on the 22kV network.
A 4.6MW solar generator is connected to Eulomogo zone substation on the 11kV network.
A 102MW solar generator is located at Nyngan Solar Farm and is connected to the Nyngan 132/66kV sub-transmission substation at 132kV via the feeder 9UT.
A 53MW solar generator is located at Broken Hill and is connected to the Transgrid Broken Hill 220/22kV sub-transmission substation at 22kV.
There have been changes to the water pump network with a new water supply now coming from Wentworth. It is unclear what the long-term configuration will be for the existing water pump infrastructure and whether it will affect peak loads.
A 145MW wind generator is located at Flyers Creek Wind Farm and is connected to Transgrid’s Orange North 132kV Switching Station through the Flyers Creek Switching Station via feeders 9MT and 9MC.
A 46.7MW solar generator is located at Manildra on the 11kV network.
A 10MW wind generator is located at Blayney wind farm and is connected to the Transgrid Panorama 132/66kV sub-transmission substation at 66kV via feeders 66:MAN and 81C.
A 4.99MW solar generator is located at Peak Hill on the 11kV network, and a 4.99MW solar generator is located at Trundle on the 22kV network.
A 50MW solar generator is located at West Jemalong and is connected to the Transgrid Forbes 132/66kV sub-transmission substation at 66kV via the feeder 89R.
A 3MW solar thermal generator is located at Lake Cargelligo on the 22kV network, and a 1.1MW solar thermal generator is located at West Jemalong on the 11kV network.
A 5MW hydro generator is located at Brown Mountain Hydro and is connected to Steeple Flat 132/66kV sub-transmission substation at 66kV via feeder 810.
A 114MW wind generator is located at Boco Rock wind farm and is connected to the Steeple Flat 132/66kV sub-transmission substation which is connected to Transgrid’s Cooma 132/66kV sub-transmission substation at 132kV via the feeder 97R.
A 1MW hydro generator is located at Jindabyne Dam and is connected to the Jindabyne zone substation 11kV busbar via feeder JIN22.
Lines 849/2 and 849/3 sustained bushfire damage so are not currently in service. More information is contained in 4.3 Urgent and Unforeseen Investments.
A 15MW hydro generator is located at Jounama Dam and is connected to the Transgrid Tumut 132/66kV sub-transmission substation at 66kV via feeder 850:TAL.
A 7MW biomass generator is located at Woodlawn Bioreactor and is connected to the Woodlawn 66/11kV zone substation at 11kV via feeder WOO8642.
A 5MW wind generator is located at Crookwell wind farm and is connected to the Goulburn 132/66kV sub-transmission substation at 66kV via feeders 841:GBN and 840:GOU.
A 107MW wind generator is located at Taralga wind farm and is connected to the Transgrid Marulan 330/132kV sub-transmission substation at 132kV via feeder 9UR.
A 24MW hydro generator is located at Wyangala Dam and is connected to the Transgrid Cowra 132/66kV sub-transmission substation at 66kV via feeder 891.
A 4.5MW solar generator is located at Cootamundra on the 11kV network.
A 30MW wind generator is located at Cullerin Range wind farm and is connected to the Transgrid Yass 330/132/66kV sub-transmission substation at 132kV via feeder 971.
A 47MW wind generator is located at Gunning wind farm and is also connected to the Transgrid Yass 330/132/66kV sub-transmission substation at 132kV via feeder 971.
There are multiple load transfer points in the Yass area to other zone substations that can be utilised with the loss of a single Yass transformer.
A 90MW solar generator is located at Sebastopol and is connected to the Transgrid Wagga North 132/66kV sub-transmission substation at 132kV via feeder 99U.
A 90MW solar generator is located at West Wyalong and is connected to the Temora 132/66kV sub-transmission substation at 132kV via feeder 9JW.
A 53MW solar generator is located at Wyalong and is connected to the Temora 132/66kV sub-transmission substation at 132kV via feeder 901.
A 30MW solar generator is located at Junee on the 11kV network.
A 4.99MW solar generator is located at Temora on the 11kV network.
A 2.2MW generator is connected to Bomen zone substation on the 11kV network.
A 30MW solar thermal generator is located at Corowa on the 22kV network.
A 5MW solar generator and 4.85MW combined solar generator and BESS is located at Mulwala on the 22kV network.
A 2.5MW hydro generator is located at The Drop and is connected to the Finley 66/22kV zone substation at 22kV via feeder FIN42.
An 85MW solar generator is located at Hillston and is connected to the Hillston 132/66kV sub-transmission substation at 132kV via feeder 9JY.
A 5MW solar generator is located near Egansford and is connected to the Coleambally 132/33kV sub-transmission substation at 33kV via feeder CLY4B4.
A 4.55MW solar generator is connected to Coleambally 132/33kV sub-transmission substation at 33kV.
Two 4.99MW solar generators are located near Hay and are connected to the Hay 132/33kV sub-transmission substation at 33kV via feeder HAT32.
Two 5MW solar generators are located near Leeton and are connected to the Yanco 132/33kV sub-transmission substation at 33kV via feeder 7L2.
A 4.76MW solar generator is connected to Narrandera zone substation on the 11kV network.
A 1.48MW solar generator is connected to Narrandera zone substation on the 11kV network.
A 3.3MW solar generator is located at Dareton on the 22kV network.