## AER_NOM_annual_data
asset_name | asset_code | exclude_from_capacity_layers | network | network_element | use_5yr_forecast | voltage_highside | voltage_lowside | investment_description | reliability_criteria | latitude | longitude | latitude_end | longitude_end | res_cust_affected_no | res_cust_affected_percent | primary_driver | augmentation_invest | replacement_invest | connections_invest | other_invest | total_invest | cost_accuracy_plus | cost_accuracy_minus | annual_deferral | deferrable_invest | opex | project_timing | commitment_timing | summer_critical | winter_critical | spring_critical | autumn_critical | summer_nameplate_cap_mva | summer_secure_cap_mva | summer_acc_cap_yr_minus2_mva | summer_acc_cap_yr_minus1_mva | summer_acc_cap_yr0_mva | summer_acc_cap_yr1_mva | summer_acc_cap_yr2_mva | summer_acc_cap_yr3_mva | summer_acc_cap_yr4_mva | summer_acc_cap_yr5_mva | summer_acc_cap_yr6_mva | summer_acc_cap_yr7_mva | summer_acc_cap_yr8_mva | summer_acc_cap_yr9_mva | summer_acc_cap_yr10_mva | summer_load_yr1_poe50_mva | summer_load_yr2_poe50_mva | summer_load_yr3_poe50_mva | summer_load_yr4_poe50_mva | summer_load_yr5_poe50_mva | summer_load_yr6_poe50_mva | summer_load_yr7_poe50_mva | summer_load_yr8_poe50_mva | summer_load_yr9_poe50_mva | summer_load_yr10_poe50_mva | summer_load_yr1_poe10_mva | summer_load_yr2_poe10_mva | summer_load_yr3_poe10_mva | summer_load_yr4_poe10_mva | summer_load_yr5_poe10_mva | summer_load_yr6_poe10_mva | summer_load_yr7_poe10_mva | summer_load_yr8_poe10_mva | summer_load_yr9_poe10_mva | summer_load_yr10_poe10_mva | winter_nameplate_cap_mva | winter_secure_cap_mva | winter_acc_cap_yr_minus2_mva | winter_acc_cap_yr_minus1_mva | winter_acc_cap_yr0_mva | winter_acc_cap_yr1_mva | winter_acc_cap_yr2_mva | winter_acc_cap_yr3_mva | winter_acc_cap_yr4_mva | winter_acc_cap_yr5_mva | winter_acc_cap_yr6_mva | winter_acc_cap_yr7_mva | winter_acc_cap_yr8_mva | winter_acc_cap_yr9_mva | winter_acc_cap_yr10_mva | winter_load_yr1_poe50_mva | winter_load_yr2_poe50_mva | winter_load_yr3_poe50_mva | winter_load_yr4_poe50_mva | winter_load_yr5_poe50_mva | winter_load_yr6_poe50_mva | winter_load_yr7_poe50_mva | winter_load_yr8_poe50_mva | winter_load_yr9_poe50_mva | winter_load_yr10_poe50_mva | winter_load_yr1_poe10_mva | winter_load_yr2_poe10_mva | winter_load_yr3_poe10_mva | winter_load_yr4_poe10_mva | winter_load_yr5_poe10_mva | winter_load_yr6_poe10_mva | winter_load_yr7_poe10_mva | winter_load_yr8_poe10_mva | winter_load_yr9_poe10_mva | winter_load_yr10_poe10_mva | mapped_poe | load_at_risk_yr1_mw | load_at_risk_yr2_mw | load_at_risk_yr3_mw | load_at_risk_yr4_mw | load_at_risk_yr5_mw | EUSE_MWh_yr1 | EUSE_MWh_yr2 | EUSE_MWh_yr3 | EUSE_MWh_yr4 | EUSE_MWh_yr5 | EUSE_MWh_yr6 | EUSE_MWh_yr7 | EUSE_MWh_yr8 | EUSE_MWh_yr9 | EUSE_MWh_yr10 | hrs_exceedance_yr1 | hrs_exceedance_yr2 | hrs_exceedance_yr3 | hrs_exceedance_yr4 | hrs_exceedance_yr5 | hrs_exceedance_yr6 | hrs_exceedance_yr7 | hrs_exceedance_yr8 | hrs_exceedance_yr9 | hrs_exceedance_yr10 | EUSE_value_yr1 | EUSE_value_yr2 | EUSE_value_yr3 | EUSE_value_yr4 | EUSE_value_yr5 | EUSE_value_yr6 | EUSE_value_yr7 | EUSE_value_yr8 | EUSE_value_yr9 | EUSE_value_yr10 | summer_support_constraintyr_mw | summer_support_constraintyr_mva | summer_support_yr1_mva | summer_support_yr2_mva | summer_support_yr3_mva | summer_support_yr4_mva | summer_support_yr5_mva | summer_support_yr6_mva | summer_support_yr7_mva | summer_support_yr8_mva | summer_support_yr9_mva | summer_support_yr10_mva | winter_support_constraintyr_mw | winter_support_constraintyr_mva | winter_support_yr1_mva | winter_support_yr2_mva | winter_support_yr3_mva | winter_support_yr4_mva | winter_support_yr5_mva | winter_support_yr6_mva | winter_support_yr7_mva | winter_support_yr8_mva | winter_support_yr9_mva | winter_support_yr10_mva | power_factor | reactive_support_details | load_transfer_capability_mva | emergency_generation_mva | emergency_generation_mw | historic_emergency_generation_flag | connected_region1 | connected_region1_EF | connected_region2 | connected_region2_EF | connected_region3 | connected_region3_EF | connected_region4 | connected_region4_EF | connected_region5 | connected_region5_EF | connected_region6 | connected_region6_EF | connected_region7 | connected_region7_EF | connected_region8 | connected_region8_EF | connected_region9 | connected_region9_EF | connected_region10 | connected_region10_EF | connected_region11 | connected_region11_EF | connected_region12 | connected_region12_EF | connected_region13 | connected_region13_EF | connected_region14 | connected_region14_EF | connected_region15 | connected_region15_EF | connected_region16 | connected_region16_EF | connected_region17 | connected_region17_EF | connected_region18 | connected_region18_EF | connected_region19 | connected_region19_EF | connected_region20 | connected_region20_EF | connected_region21 | connected_region21_EF | connected_region22 | connected_region22_EF | connected_region23 | connected_region23_EF | connected_region24 | connected_region24_EF | connected_region25 | connected_region25_EF | connected_region26 | connected_region26_EF | connected_region27 | connected_region27_EF | connected_region28 | connected_region28_EF | connected_region29 | connected_region29_EF | connected_region30 | connected_region30_EF | template_version_v3.1
| ATA3B1 Attunga |  |  | DF |  | 11 |  | Tamworth, Garthowen Rd, 18-971752, HV conductor EOL |  | -30.9325 | 150.8491 | -30.8789 | 150.8846 | 490 | 0.155 | Asset Condition |  | 389921 |  |  | 389921 | 0.1 | 0.1 | 31826 |  | 7798 | 06/2027 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [26 empty] | 0.3 | [11 empty] | 0.3 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| AVE3B2 Alstonville 2 |  |  | DF |  | 11 |  | Replace padsub 41-2765 and replace HV cable on existing route-340m |  | -28.8466 | 153.4415 | -28.8462 | 153.4384 | 626 | 0.12 | Asset Condition |  | 330649 |  |  | 330649 | 0.1 | 0.1 | 26988 |  | 6613 | 06/2027 | [7 empty] | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | [15 empty] | 1.22 | 1.24 | 1.26 | 1.28 | 1.31 | [7 empty] | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | [15 empty] | 1.22 | 1.24 | 1.26 | 1.28 | 1.31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| BBI1101 M11 Ghoolendaadi |  |  | DF |  | 11 |  | Boggabri Cotton Gin 75-110051 TX EOL |  | -30.7397 | 149.9821 | -30.7397 | 149.9821 | 55 | 0.018 | Asset Condition |  | 273649 |  |  | 273649 | 0.1 | 0.1 | 22336 |  | 5473 | 06/2025 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 3.04 | 3.08 | 3.14 | 3.19 | 3.24 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 3.04 | 3.08 | 3.14 | 3.19 | 3.24 | [6 empty] | 3.04 | 3.08 | 3.14 | 3.19 | 3.24 | 3.04 | 3.08 | 3.14 | 3.19 | 3.24 | [26 empty] | 3 | [11 empty] | 3 | [10 empty] | 0.943 |  | 0 | 0 |  | No
| BGA2K13 Horton Valley |  |  | DF |  | 22 |  | Installation of a 30MWh Stand Alone Power System replacing 22kV HV network in the vicinity of Narrabri Rd Valley Heights Bingara |  | -29.9603 | 150.4308 | -29.9911 | 150.4136 | 149 | 0.01 | Reliability | 285759 |  |  |  | 285759 | 0.1 | 0.1 | 23324 |  | 5715 | 06/2027 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 0.39 | 0.39 | 0.4 | 0.4 | 0.4 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 0.39 | 0.39 | 0.4 | 0.4 | 0.4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.94 |  | 0 | 0 |  | No
| BHL42 Railwaytown |  |  | DF |  | 22 |  | Broken Hill, Refurbishment sub 6-16271 Sturt Park Sulphide St |  | -31.9571 | 141.4625 | -31.9571 | 141.4625 | 4472 | 0.04 | Asset Condition |  | 296983 |  |  | 296983 | 0.1 | 0.1 | 23994 |  | 5940 | 06/2027 | [7 empty] | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | [15 empty] | 11.57 | 11.57 | 11.53 | 11.53 | 11.56 | [7 empty] | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | 6.71 | [15 empty] | 11.57 | 11.57 | 11.53 | 11.53 | 11.56 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0.5 | [11 empty] | 0.5 | [10 empty] | 1 |  | 0 | 0 |  | No
| BKE4B2 M82 Wanaaring |  |  | DF |  | 33 |  | Bourke Wanaaring BKE4B2 M82 Multiple Sites PPF |  | -30.093 | 145.9572 | -29.9502 | 146.4233 | 330 | 1 | Reliability |  | 285021 |  |  | 285021 | 0.1 | 0.1 | 23264 |  | 5700 | 06/2027 | [7 empty] | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | [15 empty] | 1.68 | 1.69 | 1.71 | 1.7 | 1.65 | [7 empty] | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | 4.31 | [15 empty] | 1.68 | 1.69 | 1.71 | 1.7 | 1.65 | [6 empty] | 0.91 | 0.91 | 0.92 | 0.92 | 0.89 | 0.91 | 0.91 | 0.92 | 0.92 | 0.89 | [26 empty] | 1.68 | [11 empty] | 1.68 | [10 empty] | 0.54 |  | 0 | 0 |  | No
| BLH3B3 Bulahdelah Nth/Markwell/Newells Ck |  |  | DF |  | 11 |  | Replacement of ground mounted substation |  | -32.2922 | 152.175 | -32.2922 | 152.175 | 391 | 0.003 | Safety | 385917 |  |  |  | 385917 | 0.1 | 0.1 | 31499 |  | 7894 | 06/2027 | [7 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [15 empty] | 1.33 | 1.34 | 1.36 | 1.37 | 1.37 | [7 empty] | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | [15 empty] | 1.33 | 1.34 | 1.36 | 1.37 | 1.37 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| BNK24787 Old Bar No.2 |  |  | DF |  | 11 |  | Replacement of undersized 11kV cable |  | -31.9678 | 152.5804 | -31.9734 | 152.5793 | 1199 | 0.47 | Capacity |  | 368642 |  |  | 368642 | 0.25 | 0.1 | 30089 |  | 7352 | 06/2027 | [7 empty] | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | [15 empty] | 2.26 | 2.31 | 2.35 | 2.4 | 2.46 | [7 empty] | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | 2.99 | [15 empty] | 2.26 | 2.31 | 2.35 | 2.4 | 2.46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.998 |  | 0 | 0 |  | No
| BNY3B4 Millthorpe |  |  | DF |  | 11 |  | Upgrade 3.3kms of 7/4.50AAC conductor that is thermally constrained |  | -33.177 | 149.252 | -33.517 | 149.224 | 1150 | 1 | Capacity | 264857 |  |  |  | 264857 | 0.1 | 0.1 | 21618 |  | 5297 | 06/2027 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 3.23 | 3.25 | 3.27 | 3.29 | 3.29 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 3.23 | 3.25 | 3.27 | 3.29 | 3.29 | [6 empty] | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | 2.74 | [26 empty] | 0.38 | [11 empty] | 0.38 | [10 empty] | 0.98 |  | 1 | 0 |  | No
| BNY3B4 Millthorpe |  |  | DF |  | 11 |  | Blayney HV conductor constraints Browns Creek Tallwood |  | -33.532 | 149.1493 | -33.501 | 149.1296 | 1150 | 1 | Capacity | 328800 |  |  |  | 328800 | 0.1 | 0.1 | 26837 |  | 6576 | 06/2027 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 3.23 | 3.25 | 3.27 | 3.29 | 3.29 | [7 empty] | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | 1.14 | [15 empty] | 3.23 | 3.25 | 3.27 | 3.29 | 3.29 | [6 empty] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | [26 empty] | 0.38 | [11 empty] | 0.38 | [10 empty] | 0.98 |  | 1.9 | 0 |  | No
| BOM8B2 Nimmitabel |  |  | DF |  | 22 |  | Replace steel conductor |  | -36.755 | 149.2501 | -36.699 | 149.2408 | 207 | 0.05 | Asset Condition |  | 509010 |  |  | 509010 | 0.1 | 0.1 | 41547 |  | 10180 | 02/2026 | [7 empty] | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | [15 empty] | 0.29 | 0.29 | 0.29 | 0.3 | 0.3 | [7 empty] | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | 1.73 | [15 empty] | 0.29 | 0.29 | 0.29 | 0.3 | 0.3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.887 |  | 0 | 0 |  | No
| BTH72 City Central |  |  | DF |  | 11 |  | Bathurst replace 350 metres underground faulty cable city centre |  | -33.4175 | 149.5805 | -33.4186 | 149.5781 | 631 | 1 | Asset Condition |  | 305454 |  |  | 305454 | 0.1 | 0.1 | 24932 |  | 6109 | 06/2026 | [7 empty] | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | [15 empty] | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | [7 empty] | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | 5.33 | [15 empty] | 1.88 | 1.88 | 1.88 | 1.88 | 1.88 | [6 empty] | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | 1.86 | [26 empty] | 1.88 | [11 empty] | 1.88 | [10 empty] | 0.989 |  | 3 | 0 |  | No
| BTH82 Lloyds Rd |  |  | DF |  | 11 |  | Bathurst supply constraints BTH3B7 Lloyds Rd Feeder |  | -33.4419 | 149.5689 | -33.4612 | 149.5716 | 1317 | 1 | Capacity | 343987 |  |  |  | 343987 | 0.1 | 0.1 | 28077 |  | 6880 | 06/2026 | [7 empty] | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | [15 empty] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | [7 empty] | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | 1.21 | [15 empty] | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | [6 empty] | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | 2.38 | [26 empty] | 2.4 | [11 empty] | 2.4 | [10 empty] | 0.99 |  | 3 | 0 |  | No
| BTH92 Lagoon/Trunkey |  |  | DF |  | 11 |  | Install a 50 amp closed delta regulator at Browns Paddock on the BTH3B8 Lagoon Trunkey Feeder to address voltage constraints |  | -33.7884 | 149.368 | -33.7909 | 149.3677 | 138 | 0.2 | Capacity | 261261 |  |  |  | 261261 | 0.1 | 0.1 | 21325 |  | 5225 | 06/2027 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.1 | [11 empty] | 0.1 | [10 empty] | 1 |  | 0.1 | 0 |  | No
| BTH92 Lagoon/Trunkey |  |  | DF |  | 11 |  | Perthville Backup supply constraints |  | -33.4984 | 149.6226 | -33.5417 | 149.5535 | 469 | 0.68 | Reliability | 623170 |  |  |  | 623170 | 0.1 | 0.1 | 50865 |  | 12463 | 06/2027 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | [7 empty] | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | 1.06 | [15 empty] | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | [6 empty] | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | 1.23 | [26 empty] | 1.23 | [11 empty] | 1.23 | [10 empty] | 1 |  | 0.1 | 0 |  | No
| BTS8B11 Inverell West |  |  | DF |  | 22 |  | Installation of a high voltage underground interconnector between pad sub 82015809 and pad sub 82-983188 |  | -29.7801 | 151.0906 | -29.7804 | 151.0928 | 1648 | 0.039 | Reliability | 383460 |  |  |  | 383460 | 0.1 | 0.1 | 31299 |  | 7669 | 06/2027 | [7 empty] | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | [15 empty] | 5.57 | 5.58 | 5.61 | 5.65 | 5.71 | [7 empty] | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | 4.36 | [15 empty] | 5.57 | 5.58 | 5.61 | 5.65 | 5.71 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| CBB8B1 Tambar Springs |  |  | DF |  | 22 |  | Purlewaugh Coonabarabran Rd HV Conductor End of Life |  | -31.3793 | 149.6429 | -31.3849 | 149.6831 | 780 | 0.26 | Asset Condition |  | 278391 |  |  | 278391 | 0.1 | 0.1 | 22723 |  | 5568 | 06/2027 | [7 empty] | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | [15 empty] | 1.07 | 1.08 | 1.09 | 1.1 | 1.11 | [7 empty] | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | 1.94 | [15 empty] | 1.07 | 1.08 | 1.09 | 1.1 | 1.11 | [6 empty] | 0.57 | 0.6 | 0.6 | 0.6 | 0.6 | 0.57 | 0.6 | 0.6 | 0.6 | 0.6 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| CRA32 Corowa Town No.2 |  |  | DF |  | 22 |  | Corowa, Honour Ave, veranda main & direct buried underground upgrade between sub 63-50260 & CE243198. |  | -35.9931 | 146.3911 | -35.9939 | 146.3911 | 1779 | 0.02 | Asset Condition | 282813 |  |  |  | 282813 | 0.1 | 0.1 | 0 |  | 5656 | 06/2028 | [7 empty] | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | [15 empty] | 6 | 6 | 6.03 | 6.04 | 6.05 | [7 empty] | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | 5.19 | [15 empty] | 6 | 6 | 6.03 | 6.04 | 6.05 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| CRA42 Corurgan |  |  | DF |  | 22 |  | Replace substation |  | -36.0189 | 146.3019 | -36.0189 | 146.3019 | 159 | 0.01 | Asset Condition |  | 440450 |  |  | 440450 | 0.1 | 0.1 | 0 |  | 8809 | 06/2027 | [7 empty] | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | [15 empty] | 3.34 | 3.34 | 3.36 | 3.37 | 3.37 | [7 empty] | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | 2.12 | [15 empty] | 3.34 | 3.34 | 3.36 | 3.37 | 3.37 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| CSO3B3 Leeville |  |  | DF |  | 11 |  | Casino Summerland Way 7.2km HV reconductor due to Voltage Constraint |  | -28.9433 | 150.0063 | -29.0024 | 153.0119 | 460 | 0.38 | Voltage |  |  |  |  | 452738 | 0.1 | 0.1 | 36953 |  | 9055 | 06/2027 | [7 empty] | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | [15 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [7 empty] | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | 1.34 | [15 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| CWD13 Cargo |  |  | DF |  | 11 |  | Canowindra Eulimore Rd/Waterhole Creek Rd HV Reconductor due to voltage constraints |  | -33.399 | 148.6091 | -33.3653 | 148.5516 | 713 | 0.11 | Voltage | 692974 |  |  |  | 692974 | 0.1 | 0.1 | 56562 |  | 13859 | 06/2027 | [7 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | [15 empty] | 1.92 | 1.92 | 1.92 | 1.94 | 1.96 | [7 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | [15 empty] | 1.92 | 1.92 | 1.92 | 1.94 | 1.96 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0.5 | [11 empty] | 0.5 | [10 empty] | 1 |  | 0.15 | 0 |  | No
| DBS3B8 Margaret Cres |  |  | DF |  | 11 |  | Replace existing 1000kVA Pad Sub 30-4559 with a 1500 kVA Pad Sub. |  | -32.26 | 148.6233 | -32.26 | 148.6233 | 2299 | 0 | Capacity | 265581 |  |  |  | 265581 | 0.1 | 0.1 | 21677 |  | 5312 | 06/2026 | [7 empty] | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | [15 empty] | 5.4 | 5.46 | 5.52 | 5.59 | 5.69 | [7 empty] | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | 3.52 | [15 empty] | 5.4 | 5.46 | 5.52 | 5.59 | 5.69 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.998 |  | 0 | 0 |  | No
| DNO132 Dunedoo No.1 |  |  | DF |  | 22 |  | Dunedoo Tucklan St HV Conductor EOL |  | -32.0198 | 149.3882 | -32.0216 | 149.3982 | 380 | 1 | Asset Condition |  | 269490 |  |  | 269490 | 0.1 | 0.1 | 21996 |  | 5390 | 06/2026 | [7 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [15 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [7 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | [15 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [6 empty] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | [26 empty] | 0.8 | [11 empty] | 0.8 | [10 empty] | 0.997 |  | 4 | 0 |  | No
| ESH3B5 Boydtown |  |  | DF |  | 11 |  | Boydtown Nullica St Address encroachment defects |  | -37.0998 | 149.8717 | -37.0979 | 149.8728 | 59 | 1 | Safety | 452840 |  |  |  | 452840 | 0.1 | 0.1 | 36962 |  | 9057 | 06/2026 | [7 empty] | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | [15 empty] | 0.51 | 0.52 | 0.53 | 0.54 | 0.54 | [7 empty] | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | 2.54 | [15 empty] | 0.51 | 0.52 | 0.53 | 0.54 | 0.54 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| ETH3B11 Coles/White |  |  | DF |  | 11 |  | Tamworth White Street transformer 18-141 replacement due to defect |  | -31.093 | 150.9337 | -31.093 | 150.9337 | 52 | 0.135 | Asset Condition |  | 336544 |  |  | 336544 | 0.1 | 0.1 | 27469 |  | 6731 | 06/2027 | [7 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [15 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [7 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [15 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [26 empty] | 0.32 | [11 empty] | 0.32 | [10 empty] | 0.99 |  | 0 | 0.1 |  | No
| ETH3B14 King George Ave |  |  | DF |  | 11 |  | Nemingha Cross Park Rd 1445290 HV Conductor End of Life |  | -31.1279 | 150.9758 | -31.144 | 150.9809 | 407 | 0.128 | Asset Condition |  | 269675 |  |  | 269675 | 0.1 | 0.1 | 22011 |  | 5394 | 06/2027 | [7 empty] | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | [15 empty] | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | [7 empty] | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | 2.36 | [15 empty] | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | [6 empty] | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | [26 empty] | 2.3 | [11 empty] | 2.3 | [10 empty] | 0.99 |  | 2.3 | 0 |  | No
| ETH3B7 TCC/Calala |  |  | DF |  | 11 |  | Address capacity and reliability risks identified within the Calala network |  | -31.1324 | 150.9641 | -31.1363 | 150.9624 | 1906 | 0.972 | Capacity |  |  |  | 496722 | 496722 | 0.1 | 0.1 | 40544 |  | 9934 | 06/2026 | [7 empty] | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | [15 empty] | 5.5 | 6.06 | 6.5 | 6.91 | 7.3 | [7 empty] | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | 3.54 | [15 empty] | 5.5 | 6.06 | 6.5 | 6.91 | 7.3 | [6 empty] | 5.5 | 6.06 | 6.5 | 6.91 | 7.3 | 5.5 | 6.06 | 6.5 | 6.91 | 7.3 | [26 empty] | 4 | [11 empty] | 4 | [10 empty] | 0.99 |  | 1.7 | 0 |  | No
| EWE3B1 Brunswick No.1 |  |  | DF |  | 11 |  | Brunswick Heads LV conductor 3.0km EOL |  | -28.5437 | 153.5451 | -28.5402 | 153.5549 | 1191 | 0.8 | Asset Condition |  | 447683 |  |  | 447683 | 0.1 | 0.1 | 36541 |  | 8954 | 06/2027 | [7 empty] | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | [15 empty] | 2.18 | 2.22 | 2.25 | 2.29 | 2.35 | [7 empty] | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | 3.49 | [15 empty] | 2.18 | 2.22 | 2.25 | 2.29 | 2.35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| FIN52 Tocumwal |  |  | DF |  | 22 |  | Two new 300A 22kV closed delta regulators |  | -35.7022 | 145.5786 | -35.7675 | 145.5669 | 1979 | 1 | Capacity | 630398 |  |  |  | 630398 | 0.1 | 0.1 | 0 |  | 12608 | 06/2027 | [7 empty] | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | [15 empty] | 6.11 | 6.11 | 6.13 | 6.14 | 6.14 | [7 empty] | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | 2.35 | [15 empty] | 6.11 | 6.11 | 6.13 | 6.14 | 6.14 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| GDI8B6 Goondiwindi Town Sth |  |  | DF |  | 22 |  | Replacement of existing Chamber Sub with new padmount sub in the vicinity of Sub 82-7631, Goondiwindi Hospital, Bowen Street, Goondiwindi. |  | -28.5477 | 150.3029 | -28.5477 | 150.3029 | 753 | 0.032 | Asset Condition | 329395 |  |  |  | 329395 | 0.1 | 0.1 | 26886 |  | 6588 | 06/2026 | [7 empty] | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | [15 empty] | 3.8 | 3.81 | 3.81 | 3.8 | 3.78 | [7 empty] | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | 5.02 | [15 empty] | 3.8 | 3.81 | 3.81 | 3.8 | 3.78 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.879 |  | 0 | 0 |  | No
| GFH3B6 Illilliwa |  |  | DF |  | 11 |  | Griffith Illilliwa Curtin Cedar McNabb St 96-2537 replace 1000m of backyard LV |  | -34.2809 | 146.055 | -34.2813 | 146.058 | 1548 | 0.05 | Asset Condition | 348120 |  |  |  | 348120 | 0.1 | 0.1 | 28414 |  | 6962 | 06/2027 | [7 empty] | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | [15 empty] | 4.5 | 4.5 | 4.5 | 4.52 | 4.56 | [7 empty] | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | 3.66 | [15 empty] | 4.5 | 4.5 | 4.5 | 4.52 | 4.56 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| GGB112 Gulargambone |  |  | DF |  | 22 |  | Reconductor 7/064 HDBC between GGB112 CB through to 30-G2930 with 7/450 AAAC in vicinity of Gulargambone |  | -31.325 | 148.4846 | -31.4239 | 148.5251 | 478 | 0.96 | Asset Condition |  | 886190 |  |  | 886190 | 0.1 | 0.1 | 72333 |  | 17724 | 06/2027 | [7 empty] | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | [15 empty] | 1.37 | 1.37 | 1.38 | 1.38 | 1.39 | [7 empty] | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | 1.32 | [15 empty] | 1.37 | 1.37 | 1.38 | 1.38 | 1.39 | [6 empty] | 1.3 | 1.3 | 1.31 | 1.31 | 1.32 | 1.3 | 1.3 | 1.31 | 1.31 | 1.32 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| GID12 Gilgandra Town No.1 |  |  | DF |  | 0.415 |  | Relocate the existing Low Voltage network that supplies the CBD of the Township of Gilgandra. |  | -31.7122 | 148.6682 | -31.7106 | 148.6698 | 707 | 0.11 | Safety | 779509 |  |  |  | 779509 | 0.1 | 0.1 | 63625 |  | 14043 | 06/2027 | [7 empty] | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | [15 empty] | 2 | 2.01 | 2.02 | 2.03 | 2.01 | [7 empty] | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | [15 empty] | 2 | 2.01 | 2.02 | 2.03 | 2.01 | [6 empty] | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.994 |  | 0 | 0 |  | No
| GID22 Rural Nth/Sth/West |  |  | DF |  | 11 |  | Replace 2.9 km of 7/104 HDBC 11 kV conductor with 7/450 AAAC in the vicinity of South Gilgandra. |  | -31.7206 | 148.6554 | -31.7418 | 148.6446 | 614 | 1 | Asset Condition |  | 333364 |  |  | 333364 | 0.1 | 0.1 | 27210 |  | 6121 | 06/2027 | [7 empty] | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | [15 empty] | 2.3 | 2.31 | 2.33 | 2.33 | 2.31 | [7 empty] | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | [15 empty] | 2.3 | 2.31 | 2.33 | 2.33 | 2.31 | [6 empty] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.995 |  | 0 | 0 |  | No
| GLS3B1 Gara |  |  | DF |  | 11 |  | Reconductor 10.8km of copper HV. PPF |  | -30.5312 | 151.6783 | -30.5312 | 151.6783 | 272 | 0.5 | Asset Condition | 655138 |  |  |  | 655138 | 0.1 | 0.1 | 53474 |  | 13103 | 06/2027 | [7 empty] | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | [15 empty] | 0.58 | 0.58 | 0.59 | 0.6 | 0.61 | [7 empty] | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | 1.17 | [15 empty] | 0.58 | 0.58 | 0.59 | 0.6 | 0.61 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| GLS3B2 Rockvale |  |  | DF |  | 11 |  | Replace Padmount sub and HV/LV UG cables. |  | -30.5312 | 151.6783 | -30.5312 | 151.6783 | 938 | 1 | Asset Condition |  | 338295 |  |  | 338295 | 0.1 | 0.1 | 27612 |  | 6766 | 06/2027 | [7 empty] | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | [15 empty] | 1.96 | 1.99 | 2 | 2.03 | 2.06 | [7 empty] | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | 1.07 | [15 empty] | 1.96 | 1.99 | 2 | 2.03 | 2.06 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| GLS3B7 City Central |  |  | DF |  | 11 |  | Replace defective substation and associated HV/LV UG cables. |  | -30.5312 | 151.6783 | -30.5312 | 151.6783 | 774 | 0.07 | Asset Condition |  | 574537 |  |  | 574537 | 0.1 | 0.1 | 46895 |  | 11491 | 06/2026 | [7 empty] | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | [15 empty] | 2.25 | 2.28 | 2.3 | 2.32 | 2.36 | [7 empty] | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | [15 empty] | 2.25 | 2.28 | 2.3 | 2.32 | 2.36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.996 |  | 0 | 0 |  | No
| HAT42 Hay 132 - Carrathool |  |  | DF |  | 33 |  | Upgrade undersized HV voltage regulator 98-V10253 in the vicinity of Nullabor Murrumbidgee River Rd Hay |  | -34.4543 | 145.0943 | -34.4543 | 145.0943 | 129 | 0.68 | Capacity | 419649 |  |  |  | 419649 | 0.1 | 0.1 | 34253 |  | 8393 | 06/2028 | [7 empty] | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | [15 empty] | 7.84 | 7.85 | 7.86 | 7.86 | 7.87 | [7 empty] | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | [15 empty] | 7.84 | 7.85 | 7.86 | 7.86 | 7.87 | [6 empty] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | [26 empty] | 2.5 | [11 empty] | 2.5 | [10 empty] | 0.96 |  | 0 | 0 |  | No
| HGE3B1 Grafton Rd |  |  | DF |  | 11 |  | Reconductor 9.2km of HV with ACSR. |  | -30.5725 | 151.8998 | -30.5725 | 151.8998 | 210 | 0.07 | Reliability |  | 381914 |  |  | 381914 | 0.1 | 0.1 | 31173 |  | 7638 | 06/2027 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.29 | 0.29 | 0.3 | 0.31 | 0.32 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.29 | 0.29 | 0.3 | 0.31 | 0.32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| HGE3B1 Grafton Rd |  |  | DF |  | 11 |  | Reconductor 10.2km of Wagtail HV conductor. |  | -30.5725 | 151.8998 | -30.5725 | 151.8998 | 210 | 0.2 | Reliability | 529086 |  |  |  | 529086 | 0.1 | 0.1 | 43185 |  | 10582 | 06/2028 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.29 | 0.29 | 0.3 | 0.31 | 0.32 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.29 | 0.29 | 0.3 | 0.31 | 0.32 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| HGN3B1 Crowdy Head |  |  | DF |  | 11 |  | Replacement of consac cable |  | -31.8725 | 152.6816 | -31.8712 | 152.6803 | 1036 | 0.5 | Asset Condition |  | 359694 |  |  | 359694 | 0.2 | 0.2 | 29359 |  | 7154 | 06/2027 | [7 empty] | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | [15 empty] | 1.54 | 1.59 | 1.63 | 1.67 | 1.71 | [7 empty] | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | 3.08 | [15 empty] | 1.54 | 1.59 | 1.63 | 1.67 | 1.71 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| HIL1401 Upper Lachlan |  |  | DF |  | 33 |  | Hillston Mt Boothagandra line relocation |  | -33.5249 | 145.8439 | -33.5287 | 145.881 | 201 | 0.02 | Safety | 427957 |  |  |  | 427957 | 0.1 | 0.1 | 34931 |  | 8559 | 06/2026 | [7 empty] | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | [15 empty] | 4.3 | 4.33 | 4.37 | 4.41 | 4.44 | [7 empty] | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | 3.78 | [15 empty] | 4.3 | 4.33 | 4.37 | 4.41 | 4.44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| HOL1890 Wantagong/Woomargama |  |  | DF |  | 22 |  | Install 2 x SAPS |  | -35.8367 | 147.6761 | -35.8528 | 147.6247 | 2 | 1 | Asset Condition |  | 493252 |  |  | 493252 | 0.1 | 0.1 | 0 |  | 9865 | 06/2026 | [7 empty] | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | [15 empty] | 0.76 | 0.76 | 0.76 | 0.76 | 0.77 | [7 empty] | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | 1.79 | [15 empty] | 0.76 | 0.76 | 0.76 | 0.76 | 0.77 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| KOO3B1 Plumpton Rd |  |  | DF |  | 11 |  | Replace eastern LV circuit with 240mm AL XLPE and replace distribution transformer |  | -35.1723 | 147.3521 | -35.1737 | 147.3499 | 1173 | 0.023 | Power Quality | 370686.85 | 87223.41 |  |  | 457910.26 | 0.1 | 0.1 | 0 |  | 9158 | 06/2026 | [7 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.32 | 0.32 | 0.32 | 0.32 | [15 empty] | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | [7 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.32 | 0.32 | 0.32 | 0.32 | [15 empty] | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | [6 empty] | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | 0.08 | 0.09 | 0.1 | 0.11 | 0.12 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.993 |  | 0 | 0 |  | No
| KOO3B6 Lake Albert |  |  | DF |  | 11 |  | Replace steel columns and approx. 350m of LV CONSAC cable with 240mm AL XLPE supplied via sub 71-3645 |  | -35.163 | 147.3777 | -35.1612 | 147.3767 | 1444 | 0.027 | Asset Condition | 444719 |  |  |  | 444719 | 0.1 | 0.1 | 0 |  | 8894 | 06/2027 | [7 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [15 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [7 empty] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | [15 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.993 |  | 0 | 0 |  | No
| LKC7781 Cathie Sth |  |  | DF |  | 11 |  | Wallum Drv Seascape Lake Cathie thermal overload & reliability |  | -31.566 | 152.827 | -31.566 | 152.827 | 1150 | 1 | Reliability | 220000 |  |  |  | 220000 | 0.1 | 0.1 | 17957 |  | 3956 | 06/2029 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 2.15 | 2.23 | 2.32 | 2.4 | 2.47 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 2.15 | 2.23 | 2.32 | 2.4 | 2.47 | [6 empty] | 0.9 | 1.1 | 1.1 | 1.2 | 1.3 | 0.9 | 1.1 | 1.1 | 1.2 | 1.3 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.997 |  | 3 | 0 |  | No
| MGA3B1 Turners Flat |  |  | DF |  | 11 |  | PPF Deep Ck Turners Ck Rd from near 2-R10113 to near sub 2-50477 conductor EOL |  | -31.0216 | 152.7074 | -30.9977 | 152.6996 | 386 | 0.15 | Reliability |  | 257000 |  |  | 257000 | 0.1 | 0.1 | 20977 |  | 5151 | 06/2028 | [7 empty] | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | [15 empty] | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | [7 empty] | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | [15 empty] | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | [6 empty] | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.986 |  | 0 | 0 |  | No
| MLN3B4 Townsend |  |  | DF |  | 11 |  | New 315kVA padmount substation at Maclean Depot |  | -29.4642 | 153.2252 | -29.4642 | 153.2252 | 1592 | 0.01 | Capacity | 283218 |  |  |  | 283218 | 0.1 | 0.1 | 23117 |  | 5664 | 06/2027 | [7 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [15 empty] | 2.77 | 2.78 | 2.76 | 2.77 | 2.79 | [7 empty] | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | 2.27 | [15 empty] | 2.77 | 2.78 | 2.76 | 2.77 | 2.79 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0.5 | [11 empty] | 0.5 | [10 empty] | 0.98 |  | 0.1 | 0 |  | No
| MLN3B5 Woodford Dale-Leigh |  |  | DF |  | 11 |  | Replace pole 74700 with new standard construction. |  | -29.4916 | 153.1173 | -29.4916 | 153.1173 | 868 | 1 | Safety |  | 291304 |  |  | 291304 | 0.1 | 0.1 | 23777 |  | 5673 | 06/2027 | [7 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [15 empty] | 1.6 | 1.6 | 1.59 | 1.6 | 1.61 | [7 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [15 empty] | 1.6 | 1.6 | 1.59 | 1.6 | 1.61 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| MOA8B2 Moama West |  |  | DF |  | 22 |  | Replace underground LV due to extreme apidic acid build up in the vicinity of Lawson Dr Moama |  | -36.1033 | 144.7553 | -36.1068 | 144.7548 | 1662 | 0.03 | Asset Condition |  | 689611 |  |  | 689611 | 0.1 | 0.1 | 56288 |  | 13792 | 06/2028 | [7 empty] | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | [15 empty] | 5.82 | 5.9 | 5.98 | 6.04 | 6.1 | [7 empty] | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | 6.15 | [15 empty] | 5.82 | 5.9 | 5.98 | 6.04 | 6.1 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0.1 | [11 empty] | 0.1 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| MRE8B4 Western Rural |  |  | DF |  | 22 |  | Replace two failed 22kV 1.5MVA Pad-mounted Substations in the vicinity of Brighann Gin Moree NSW. |  | -29.4376 | 149.589 | -29.4376 | 149.589 | 365 | 0 | Asset Condition |  | 330463 |  |  | 330463 | 0.1 | 0.1 | 26973 |  | 6609 | 06/2027 | [7 empty] | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | [15 empty] | 4.03 | 4.39 | 5.19 | 5.94 | 6.57 | [7 empty] | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | 2.43 | [15 empty] | 4.03 | 4.39 | 5.19 | 5.94 | 6.57 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| MRN8B3 Marulan Town |  |  | DF |  | 22 |  | Upgrade conductor removing failing copper |  | -34.7178 | 150.0561 | -34.7078 | 150.1425 | 387 | 0.33 | Asset Condition | 452992 |  |  |  | 452992 | 0.1 | 0.1 | 36974 |  | 9059 | 09/2027 | [7 empty] | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | [15 empty] | 2.93 | 3 | 3.07 | 3.14 | 3.2 | [7 empty] | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | 8.39 | [15 empty] | 2.93 | 3 | 3.07 | 3.14 | 3.2 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 5 | 0 |  | No
| MTG4B1 Tibooburra Backbone Line |  |  | DF |  | 33 |  | Broken Hill - Packsaddle Roadhouse Resilience and EV Charger Connection |  | -30.6102 | 141.9673 | -30.6102 | 141.9673 | 358 | 0.01 | Resilience |  |  | 310611 |  | 310611 | 0.1 | 0.1 | 25353 |  | 6212 | 06/2026 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.4 | 1.43 | 1.44 | 1.46 | 1.5 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.4 | 1.43 | 1.44 | 1.46 | 1.5 | [6 empty] | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | 0.05 | 0.3 | 0.3 | 0.3 | 0.3 | [26 empty] | 0.3 | [11 empty] | 0.3 | [10 empty] | 0.967 |  | 0 | 0 |  | No
| MTG4B1 Tibooburra Backbone Line |  |  | DF |  | 33 |  | Install SAPS to allow the removal of 37km of overhead SWER |  | -29.2259 | 141.001 | -29.2781 | 141.2397 | 358 | 0.003 | Reliability |  | 334991 |  |  | 334991 | 0.1 | 0.1 | 27343 |  | 6700 | 06/2027 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.4 | 1.43 | 1.44 | 1.46 | 1.5 | [7 empty] | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | [15 empty] | 1.4 | 1.43 | 1.44 | 1.46 | 1.5 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.967 |  | 0 | 0 |  | No
| MUA5006 West |  |  | DF |  | 11 |  | Replace 2.26kms of 7/0.064HDBC and 690 metres of 6/1/0.093ACSR high voltage conductor through Carcoar Village |  | -33.6106 | 149.1495 | -33.6163 | 149.1413 | 343 | 0.5 | Asset Condition |  | 315182 |  |  | 315182 | 0.1 | 0.1 | 25726 |  | 6304 | 06/2027 | [7 empty] | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | [15 empty] | 0.99 | 0.99 | 1 | 1 | 1.01 | [7 empty] | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | [15 empty] | 0.99 | 0.99 | 1 | 1 | 1.01 | [6 empty] | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | 0.89 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.996 |  | 0 | 0 |  | No
| MUL3B3 Mullumbimby West |  |  | DF |  | 11 |  | Mullumbimby East LV conductor 2.1km EOL |  | -28.5495 | 153.5044 | -28.5562 | 153.5104 | 1454 | 0.3 | Asset Condition |  | 311824 |  |  | 311824 | 0.1 | 0.1 | 25452 |  | 6236 | 06/2028 | [7 empty] | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | [15 empty] | 3.34 | 3.39 | 3.45 | 3.5 | 3.56 | [7 empty] | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | [15 empty] | 3.34 | 3.39 | 3.45 | 3.5 | 3.56 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| MUL3B3 Mullumbimby West |  |  | DF |  | 11 |  | Mullumbimby West LV conductor 3.4km EOL |  | -28.5583 | 153.4912 | -28.5478 | 153.5005 | 1454 | 0.5 | Asset Condition |  | 461384 |  |  | 461384 | 0.1 | 0.1 | 37659 |  | 9228 | 06/2028 | [7 empty] | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | [15 empty] | 3.34 | 3.39 | 3.45 | 3.5 | 3.56 | [7 empty] | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | 2.81 | [15 empty] | 3.34 | 3.39 | 3.45 | 3.5 | 3.56 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| MWA8B4 North St and Rural |  |  | DF |  | 22 |  | Replace LV underground cables |  | -35.9794 | 146.0197 | -35.9806 | 146.0169 | 877 | 0.01 | Asset Condition |  | 279708 |  |  | 279708 | 0.1 | 0.1 | 0 |  | 5594 | 06/2027 | [7 empty] | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | [15 empty] | 2.32 | 2.32 | 2.32 | 2.33 | 2.33 | [7 empty] | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | 2.08 | [15 empty] | 2.32 | 2.32 | 2.32 | 2.33 | 2.33 | [6 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| MWN3B2 Norco |  |  | DF |  | 11 |  | Create 11kV tie to provide ring for Industrial precinct. |  | -28.3371 | 153.408 | -28.3386 | 153.4191 | 1107 | 0.1 | Capacity | 423152 |  |  |  | 423152 | 0.1 | 0.1 | 34539 |  | 8022 | 06/2026 | [7 empty] | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | [15 empty] | 2.54 | 2.56 | 2.57 | 2.59 | 2.59 | [7 empty] | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | 2.06 | [15 empty] | 2.54 | 2.56 | 2.57 | 2.59 | 2.59 | [6 empty] | 2.44 | 2.45 | 2.47 | 2.48 | 2.49 | 2.44 | 2.45 | 2.47 | 2.48 | 2.49 | [26 empty] | 2.54 | [11 empty] | 2.54 | [10 empty] | 0.96 |  | 2 | 0 |  | No
| MYT3B2 Kiora |  |  | DF |  | 11 |  | Moruya replace chamber substation 31-577 |  | -35.9161 | 150.0598 | -37.0979 | 149.8728 | 1139 | 1 | Asset Condition | 406752 |  |  |  | 406752 | 0.1 | 0.1 | 33200 |  | #VALUE! | 06/2026 | [7 empty] | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | [15 empty] | 2.22 | 2.25 | 2.28 | 2.31 | 2.34 | [7 empty] | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | 1.67 | [15 empty] | 2.22 | 2.25 | 2.28 | 2.31 | 2.34 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 0 | 0 |  | No
| NDL3B2 Woolomin |  |  | DF |  | 11 |  | Woolomin Nundle Rd 232776 HV Conductor EOL |  | -31.3475 | 151.1431 | -31.311 | 151.1464 | 538 | 1 | Asset Condition |  | 470308 |  |  | 470308 | 0.1 | 0.1 | 38388 |  | 9406 | 06/2027 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 1.15 | 1.14 | 1.14 | 1.14 | 1.14 | [7 empty] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | [15 empty] | 1.15 | 1.14 | 1.14 | 1.14 | 1.14 | [6 empty] | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| NGN3B2 Coramba |  |  | DF |  | 11 |  | Establish 11k tie - Coramba East Bank Rd |  | -30.1963 | -30.1963 | -30.1935 | 153.0294 | 444 | 0.79 | Reliability | 306542 |  |  |  | 306542 | 0.1 | 0.1 | 25021 |  | 6131 | 06/2027 | [7 empty] | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | [15 empty] | 0.8 | 0.8 | 0.82 | 0.84 | 0.86 | [7 empty] | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | 1.71 | [15 empty] | 0.8 | 0.8 | 0.82 | 0.84 | 0.86 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| NME8B3 Trangie Rural |  |  | DF |  | 22 |  | Replace approx. 6.6km of 3/2.00 SC/GZ 3PH 22kV conductor in the vicinity of Trangie Dandaloo Rd, Trangie NSW. |  | -32.238 | 147.682 | -32.2606 | 147.6244 | 325 | 0.086 | Reliability |  | 419574 |  |  | 419574 | 0.1 | 0.1 | 34247 |  | 8391 | 06/2028 | [7 empty] | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | [15 empty] | 3.13 | 3.17 | 3.21 | 3.21 | 3.18 | [7 empty] | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | 1.46 | [15 empty] | 3.13 | 3.17 | 3.21 | 3.21 | 3.18 | [6 empty] | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.993 |  | 0 | 0 |  | No
| OPM3B1 Granite St |  |  | DF |  | 11 |  | Replace HV cable 400m McLaren Drv near sub 2-41451 Port Macquarie |  | -31.449 | 152.913 | -31.489 | 152.908 | 1377 | 0.05 | Asset Condition |  | 275470 |  |  | 275470 | 0.1 | 0.1 | 22484 |  | 5509 | 06/2026 | [7 empty] | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | [15 empty] | 2.38 | 2.37 | 2.38 | 2.37 | 2.37 | [7 empty] | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | 4.02 | [15 empty] | 2.38 | 2.37 | 2.38 | 2.37 | 2.37 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.98 |  | 0 | 0 |  | No
| ORS3B3 Email (Electrolux) |  |  | DF |  | 11 |  | Install 4 way switching station to allow the ORS3B3 feeder to be able to support load transfer from either 3B5 or 3B8 feeders |  | -33.2969 | 149.1025 | -33.2969 | 149.1025 | 1 | 1 | Reliability | 294727 |  |  |  | 294727 | 0.1 | 0.1 | 24056 |  | 5895 | 06/2027 | [7 empty] | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | [15 empty] | 0.3 | 0.3 | 0.31 | 0.31 | 0.31 | [7 empty] | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | 6.38 | [15 empty] | 0.3 | 0.3 | 0.31 | 0.31 | 0.31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 1 |  | 5 | 0 |  | No
| ORS3B5 Lords Place |  |  | DF |  | 11 |  | Replace substation 10-9I324 Orange Field Service Centre Lords Place |  | -33.2982 | 149.0978 | -33.2982 | 149.0978 | 1288 | 0.01 | Safety |  | 272888 |  |  | 272888 | 0.1 | 0.1 | 22274 |  | 5458 | 06/2026 | [7 empty] | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | [15 empty] | 3.26 | 3.3 | 3.33 | 3.37 | 3.42 | [7 empty] | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | 3.59 | [15 empty] | 3.26 | 3.3 | 3.33 | 3.37 | 3.42 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [26 empty] | 0.3 | [11 empty] | 0.3 | [10 empty] | 0.999 |  | 0.25 | 0 |  | No
| ORS3B7 Anson St Sth |  |  | DF |  | 11 |  | Orange cable replacements Orange South Zone Feeders |  | -33.2982 | 149.096 | -33.2984 | 149.0918 | 2454 | 1 | Asset Condition |  | 925157 |  |  | 925157 | 0.1 | 0.1 | 75059 |  | 18503 | 06/2026 | [7 empty] | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | [15 empty] | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | [7 empty] | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | 2.23 | [15 empty] | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | [6 empty] | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | [26 empty] | 8.5 | [11 empty] | 8.5 | [10 empty] | 1 |  | 5 | 0 |  | No
| PKH32 Peak Hill |  |  | DF |  | 11 |  | Peak Hill Install 11kV Gas Switches on the PKH32 Fdr |  | -32.7353 | 148.1911 | -32.7237 | 148.1893 | 582 | 1 | Reliability | 254540 |  |  |  | 254540 | 0.1 | 0.1 | 20776 |  | 5091 | 06/2027 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | [7 empty] | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | 2.78 | [15 empty] | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.999 |  | 0 | 0 |  | No
| PSK3B4 Industrial |  |  | DF |  | 11 |  | Kempsey South St sub 2-51085 padsub HV switchgear and cable end of life |  | -31.099 | 152.8255 | -31.099 | 152.8255 | 211 | 0.005 | Asset Condition | 112000 |  |  |  | 112000 | 0.1 | 0.1 | 9142 |  | 2240 | 06/2026 | [7 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [15 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [7 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [15 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [6 empty] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.953 |  | 0 | 0 |  | No
| RAG3B5 OConnell |  |  | DF |  | 11 |  | Upgrade 5.1kms of single phase steel conductor to 3 phase 7/4.50AAAC to address supply and voltage constraints |  | -33.5814 | 149.706 | -33.62 | 149.7184 | 656 | 0.16 | Reliability | 317583 |  |  |  | 317583 | 0.1 | 0.1 | 25922 |  | 7621 | 06/2027 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.6 | 1.61 | 1.62 | 1.62 | 1.63 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.6 | 1.61 | 1.62 | 1.62 | 1.63 | [6 empty] | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | [26 empty] | 0.4 | [11 empty] | 0.4 | [10 empty] | 0.999 |  | 0 | 0 |  | No
| RAG3B5 OConnell |  |  | DF |  | 11 |  | Bathurst SAPS substation 95-926 Brewongle |  | -33.4575 | 149.6751 | -33.4575 | 149.6751 | 655 | 0.001 | Reliability | 405624 |  |  |  | 405624 | 0.1 | 0.1 | 33027 |  | 8112 | 06/2027 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.6 | 1.61 | 1.62 | 1.62 | 1.63 | [7 empty] | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | 1.31 | [15 empty] | 1.6 | 1.61 | 1.62 | 1.62 | 1.63 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.999 |  | 0 | 0 |  | No
| RAG3B6 Limekilns |  |  | DF |  | 11 |  | Upgrade 7kms HV conductor on the RAG3B6 Limekilns Feeder to allow the backfeed supply to Hill End Village |  | -33.297 | 149.6568 | -33.2348 | 149.6512 | 1307 | 0.28 | Reliability |  | 516975 |  |  | 516975 | 0.1 | 0.1 | 42197 |  | 10340 | 06/2027 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 2.9 | 2.91 | 2.93 | 2.94 | 2.96 | [7 empty] | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | 1.19 | [15 empty] | 2.9 | 2.91 | 2.93 | 2.94 | 2.96 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.997 |  | 0 | 0 |  | No
| SGN3B1 Armidale Rd |  |  | DF |  | 11 |  | 11kV Feeder backup Pacific Highway, Halfway Creek |  | -29.9812 | 153.144 | -29.9523 | 153.1204 | 1258 | 0.12 | Reliability | 622225 | 100000 |  |  | 722225 | 0.1 | 0.1 | 58950 |  | 14445 | 06/2027 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.37 | 2.36 | 2.36 | 2.36 | 2.35 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.37 | 2.36 | 2.36 | 2.36 | 2.35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| SGN3B1 Armidale Rd |  |  | DF |  | 11 |  | Create 11kV tie to allow ring supply to Halfway Creek |  | -29.9082 | 153.0231 | -29.9075 | 153.0647 | 1258 | 1 | Reliability | 479057 |  |  |  | 479057 | 0.1 | 0.1 | 39102 |  | 9581 | 06/2026 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.37 | 2.36 | 2.36 | 2.36 | 2.35 | [7 empty] | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | [15 empty] | 2.37 | 2.36 | 2.36 | 2.36 | 2.35 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0.65 | 0 |  | No
| STH3B9 Winton |  |  | DF |  | 11 |  | Tamworth, between new and old Winton Rds, 18-4746, HV Conductor EOL |  | -31.0813 | 150.777 | -31.0407 | 150.7704 | 356 | 0.219 | Asset Condition |  | 290803 |  |  | 290803 | 0.1 | 0.1 | 23736 |  | 5816 | 06/2027 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [7 empty] | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | [15 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [6 empty] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | [26 empty] | 0.3 | [11 empty] | 0.3 | [10 empty] | 0.97 |  | 0.1 | 0 |  | No
| SWT12 Stewarts Mt |  |  | DF |  | 11 |  | Upgrade 5.6kms of 6/1/0.118ACSR to 7/4.50AAAC along Turondale Road to address voltage constraints |  | -33.3043 | 149.5532 | -33.2649 | 149.5728 | 1053 | 0.42 | Voltage | 385869 |  |  |  | 385869 | 0.1 | 0.1 | 31495 |  | 7717 | 06/2027 | [7 empty] | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | [15 empty] | 2.27 | 2.3 | 2.33 | 2.36 | 2.39 | [7 empty] | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | [15 empty] | 2.27 | 2.3 | 2.33 | 2.36 | 2.39 | [6 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [26 empty] | 0.3 | [11 empty] | 0.3 | [10 empty] | 0.99 |  | 0.1 | 0 |  | No
| SWT42 Simplot |  |  | DF |  | 11 |  | Stewart load constraints Corporation Ave Bathurst |  | -33.4133 | 149.5432 | -33.4148 | 149.5467 | 848 | 1 | Capacity | 508683 |  |  |  | 508683 | 0.1 | 0.1 | 41520 |  | 10174 | 06/2026 | [7 empty] | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | [15 empty] | 5.86 | 5.93 | 6 | 6.08 | 6.17 | [7 empty] | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | 3.22 | [15 empty] | 5.86 | 5.93 | 6 | 6.08 | 6.17 | [6 empty] | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | [26 empty] | 2 | [11 empty] | 2 | [10 empty] | 0.99 |  | 8 | 0 |  | No
| TDL8B2 Tullamore/Tottenham |  |  | DF |  | 22 |  | Trundle ZS TDL8B2 Tullamore/Tottenham Voltage Regulation |  | -32.756 | 147.6366 | -32.756 | 147.6366 | 857 | 1 | Voltage | 386305 |  |  |  | 386305 | 0.1 | 0.1 | 31531 |  | 7726 | 06/2026 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 1.87 | 1.84 | 1.88 | 1.85 | 1.75 | [7 empty] | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | 2.97 | [15 empty] | 1.87 | 1.84 | 1.88 | 1.85 | 1.75 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0.5 | 0 |  | No
| TEA3B3 Mineral Deposits |  |  | DF |  | 11 |  | Underbore of river to install conduits for future cable replacement |  | -32.6697 | 152.1666 | -32.6689 | 152.1705 | 1262 | 0 | Reliability | 1150000 |  |  |  | 1150000 | 0.2 | 0.2 | 93866 |  | 23000 | 06/2027 | [7 empty] | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | [15 empty] | 2.24 | 2.25 | 2.25 | 2.25 | 2.24 | [7 empty] | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | 2.82 | [15 empty] | 2.24 | 2.25 | 2.25 | 2.25 | 2.24 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.994 |  | 0 | 0 |  | No
| TEA3B4 Tea Gardens |  |  | DF |  | 11 |  | 11kV underground tie |  | -32.6546 | 152.1488 | -32.6608 | 152.1375 | 1320 | 1 | Reliability | 885660 |  |  |  | 885660 | 0.1 | 0.1 | 72290 |  | 17204 | 06/2027 | [7 empty] | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | [15 empty] | 2.82 | 2.83 | 2.84 | 2.83 | 2.82 | [7 empty] | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | 3.94 | [15 empty] | 2.82 | 2.83 | 2.84 | 2.83 | 2.82 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.997 |  | 3 | 0 |  | No
| THA2223 West End |  |  | DF |  | 11 |  | Griffith Griffin Ave Altin 96-4876 encroachment |  | -34.2853 | 146.0223 | -34.2853 | 146.0223 | 1419 | 0.75 | Safety |  | 306549 |  |  | 306549 | 0.1 | 0.1 | 25021 |  | 6131 | 06/2027 | [7 empty] | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | [15 empty] | 3.48 | 3.49 | 3.49 | 3.52 | 3.57 | [7 empty] | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | 3.98 | [15 empty] | 3.48 | 3.49 | 3.49 | 3.52 | 3.57 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| TXS3X06 Yelarbon |  |  | DF |  | 33 |  | Texas 82-R4753 4.8km HV Reconductor |  | -28.6702 | 150.8167 | -28.6575 | 150.7709 | 347 | 0.29 | Asset Condition |  |  |  |  | 319542 | 0.1 | 0.1 | 26082 |  | 6391 | 06/2027 | [7 empty] | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | [15 empty] | 2.31 | 2.3 | 2.31 | 2.31 | 2.3 | [7 empty] | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | [15 empty] | 2.31 | 2.3 | 2.31 | 2.31 | 2.3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| TXS3X06 Yelarbon |  |  | DF |  | 33 |  | Texas Holdflat Rd defect rectification of 9.8km HV Conductor |  | -28.6697 | 150.6858 | -28.7519 | 150.7042 | 346 | 0.07 | Asset Condition |  |  |  |  | 628083 | 0.1 | 0.1 | 49633 |  | 12192 | 06/2026 | [7 empty] | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | [15 empty] | 2.31 | 2.3 | 2.31 | 2.31 | 2.3 | [7 empty] | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | 5.08 | [15 empty] | 2.31 | 2.3 | 2.31 | 2.31 | 2.3 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| UNI3B2 Tilbuster/Puddledock |  |  | DF |  | 11 |  | Reconductor 5.3km of HV conductor |  | -30.4922 | 151.6495 | -30.4922 | 151.6495 | 369 | 0.7 | Asset Condition | 367385 |  |  |  | 367385 | 0.1 | 0.1 | 29987 |  | 7348 | 06/2027 | [7 empty] | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | [15 empty] | 0.76 | 0.78 | 0.79 | 0.81 | 0.83 | [7 empty] | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | [15 empty] | 0.76 | 0.78 | 0.79 | 0.81 | 0.83 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| WBN3B3 Coraki |  |  | DF |  | 11 |  | East Coraki Oakland Rd Conductor 5.7km EOL |  | -28.9976 | 153.2933 | -29.0297 | 153.2831 | 916 | 0.04 | Asset Condition |  | 329744 |  |  | 329744 | 0.1 | 0.1 | 26914 |  | 6595 | 06/2027 | [7 empty] | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | [15 empty] | 1.92 | 1.93 | 1.94 | 1.96 | 1.99 | [7 empty] | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | 1.87 | [15 empty] | 1.92 | 1.93 | 1.94 | 1.96 | 1.99 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| WBN3B4 Broadwater |  |  | DF |  | 11 |  | Augmet to dual river crossing and reconduct 9.8km |  | -28.874 | 153.432 | -28.9942 | 153.4589 | 385 | 1 | Voltage | 200000 | 1687199 |  |  | 1887199 | 0.1 | 0.1 | 154037 |  | 37744 | 06/2026 | [7 empty] | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | [15 empty] | 0.68 | 0.68 | 0.68 | 0.69 | 0.7 | [7 empty] | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | 2.37 | [15 empty] | 0.68 | 0.68 | 0.68 | 0.69 | 0.7 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.97 |  | 0 | 0 |  | No
| WCK516 Dewhurst/Gordon |  |  | DF |  | 11 |  | Werris Creek Dewhurst Street 213917 HV Conductor EOL |  | -31.3592 | 150.6486 | -31.3444 | 150.651 | 706 | 1 | Asset Condition |  | 304361 |  |  | 304361 | 0.1 | 0.1 | 24843 |  | 6087 | 06/2026 | [7 empty] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | [15 empty] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | [7 empty] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | [15 empty] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | [6 empty] | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | [26 empty] | 1.7 | [11 empty] | 1.7 | [10 empty] | 0.95 |  | 2.5 | 0 |  | No
| WGA3B6 Corindi |  |  | DF |  | 11 |  | Remove pole from sand dunes, and re-route as UG cable |  | -30.103 | 153.1988 | -30.103 | 153.1988 | 2118 | 1 | Reliability | 289060 |  |  |  | 289060 | 0.1 | 0.1 | 23594 |  | 5781 | 06/2026 | [7 empty] | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | [15 empty] | 4.02 | 4.1 | 4.19 | 4.28 | 4.36 | [7 empty] | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | 2.98 | [15 empty] | 4.02 | 4.1 | 4.19 | 4.28 | 4.36 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.99 |  | 0 | 0 |  | No
| WGM3B5 Hillside |  |  | DF |  | 11 |  | HV extension to new substation for Community precinct |  | -31.8523 | 152.3767 | -31.8529 | 152.3795 | 1395 | 0 | Capacity | 347555 |  |  |  | 347555 | 0.2 | 0.2 | 28368 |  | 6951 | 06/2026 | [7 empty] | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | [15 empty] | 3.1 | 3.12 | 3.15 | 3.18 | 3.19 | [7 empty] | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | 1.03 | [15 empty] | 3.1 | 3.12 | 3.15 | 3.18 | 3.19 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.998 |  | 0 | 0 |  | No
| WGN72 Yeoval |  |  | DF |  | 11 |  | Wellington, Rural Conductor Upgrade beyond 30-R12412 |  | -32.7265 | 148.7982 | -32.7663 | 148.8076 | 375 | 0.09 | Voltage | 402793 |  |  |  | 402793 | 0.1 | 0.1 | 32877 |  | 8056 | 06/2027 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.74 | 0.75 | 0.75 | 0.76 | 0.78 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.74 | 0.75 | 0.75 | 0.76 | 0.78 | [6 empty] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | [26 empty] | 0.03 | [11 empty] | 0.03 | [10 empty] | 0.95 |  | 0 | 0 |  | No
| WGN72 Yeoval |  |  | DF |  | 11 |  | Wellington, Upgrade conductor beyond 30-R12394, Protection constraints |  | -32.7362 | 148.7431 | -32.8098 | 148.7905 | 373 | 0.12 | Capacity | 618067 |  |  |  | 618067 | 0.1 | 0.1 | 48770 |  | 12361 | 06/2027 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.74 | 0.75 | 0.75 | 0.76 | 0.78 | [7 empty] | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | [15 empty] | 0.74 | 0.75 | 0.75 | 0.76 | 0.78 | [6 empty] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | [26 empty] | 0.02 | [11 empty] | 0.02 | [10 empty] | 0.95 |  | 0.01 | 0 |  | No
| WLS3B1 Walcha East |  |  | DF |  | 11 |  | Reconductor 2.6km of Copper HV conductor. |  | -30.9968 | 151.5859 | -30.9968 | 151.5859 | 718 | 1 | Asset Condition |  | 275566 |  |  | 275566 | 0.1 | 0.1 | 22492 |  | 5511 | 06/2026 | [7 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | [15 empty] | 1.41 | 1.42 | 1.43 | 1.44 | 1.44 | [7 empty] | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | [15 empty] | 1.41 | 1.42 | 1.43 | 1.44 | 1.44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.996 |  | 2 | 0 |  | No
| WLS8B5 Uralla/Walcha Rd/Wollun |  |  | DF |  | 22 |  | Reconductor 10km of 7/0.64Cu HV conductor. |  | -30.9968 | 151.5859 | -30.9968 | 151.5859 | 367 | 0.5 | Asset Condition | 763139 |  |  |  | 763139 | 0.1 | 0.1 | 62289 |  | 15263 | 06/2027 | [7 empty] | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | [15 empty] | 0.67 | 0.67 | 0.68 | 0.68 | 0.68 | [7 empty] | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | 4.84 | [15 empty] | 0.67 | 0.67 | 0.68 | 0.68 | 0.68 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.83 |  | 0 | 0 |  | No
| WOO3B2 Rural Fdr 2 |  |  | DF |  | 11 |  | Reconductor single phase line to 3 phase to supply Tarago town via 10km shorter route than existing supply |  | -35.0626 | 149.5914 | -35.0793 | 149.6354 | 363 | 1 | Reliability | 534675 |  |  |  | 534675 | 0.1 | 0.1 | 43641 |  | 10693 | 09/2027 | [7 empty] | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | [15 empty] | 0.76 | 0.76 | 0.76 | 0.76 | 0.75 | [7 empty] | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | [15 empty] | 0.76 | 0.76 | 0.76 | 0.76 | 0.75 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 1 | [11 empty] | 1 | [10 empty] | 1 |  | 5 | 0 |  | No
| WTR8B2 Poison Gate |  |  | DF |  | 22 |  | Replacement of 8km of high impedance steel conductor to reduce fault levels from pole 27020834 to pole 270200962 |  | -29.7111 | 149.1589 | -29.7109 | 149.0854 | 92 | 0.13 | Asset Condition | 404771 |  |  |  | 404771 | 0.1 | 0.1 | 33038 |  | 8095 | 06/2027 | [7 empty] | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | [15 empty] | 3.52 | 3.52 | 3.52 | 3.5 | 3.46 | [7 empty] | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | [15 empty] | 3.52 | 3.52 | 3.52 | 3.5 | 3.46 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.961 |  | 0 | 0 |  | No
| YAM3B4 Yamba West |  |  | DF |  | 11 |  | Replace substation 51-796 |  | -29.4265 | 153033047 | -29.4265 | 153033047 | 2132 | 0.05 | Asset Condition | 178061 | 120000 |  |  | 298061 | 0.1 | 0.1 | 24328 |  | 5961 | 06/2026 | [7 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [15 empty] | 3.32 | 3.35 | 3.37 | 3.4 | 3.44 | [7 empty] | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | [15 empty] | 3.32 | 3.35 | 3.37 | 3.4 | 3.44 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0.32 | [11 empty] | 0.32 | [10 empty] | 0.99 |  | 0.1 | 0 |  | No
| YAN2319 Euroley Rd |  |  | DF |  | 11 |  | Yanco Euroley 3.8km conductor upgrade |  | -34.6257 | 146.3922 | -34.6257 | 146.3922 | 46 | 0.01 | Asset Condition |  | 290624 |  |  | 290624 | 0.1 | 0.1 | 23721 |  | 5812 | 06/2028 | [7 empty] | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | [15 empty] | 0.67 | 0.67 | 0.67 | 0.68 | 0.68 | [7 empty] | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | 1.75 | [15 empty] | 0.67 | 0.67 | 0.67 | 0.68 | 0.68 | [6 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [26 empty] | 0.53 | [11 empty] | 0.53 | [10 empty] | 0.951 |  | 0 | 0 |  | No
| YAS6242 Yass Town Sth |  |  | DF |  | 22 |  | Yass, Barber St, replace substation 25-714 due to asset condition |  | -34.8476 | 148.922 | -34.8476 | 148.922 | 1635 | 0.018 | Asset Condition | 312596 |  |  |  | 312596 | 0.1 | 0.1 | 25515 |  | 6252 | 06/2027 | [7 empty] | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | [15 empty] | 4.83 | 4.85 | 4.89 | 4.92 | 4.96 | [7 empty] | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | 5.44 | [15 empty] | 4.83 | 4.85 | 4.89 | 4.92 | 4.96 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | [11 empty] | 0 | [10 empty] | 0.996 |  | 0.06 | 0 |  | No
Note on A1: Full asset name (or, for TNSPs, 'Project Name' if more relevant). Should include any spatially represented asset type for which you wish to present data. For Zone Sustation asset this will generally match the asset_name in NOM polygon files. Units/format: Free text field
Note on B1: AER Ref: DT004 'shorthand' code or asset ID of Network Asset. Should be consistent with RIN Sustained Interruptions sheet from Category Analysis template. Generally this will match NOM polygon file asset_codes however the entry of the relevant asset_code of mapped region now occurs in connected_region1. (Col FN) Units/format: Free text field but ideally short notation no spaces and be unique.
Note on C1: There may be multiple investments (data lines) that relate to a given mapping region/polygon (such as a transformer replacement, a feeder augmentation and a switchboard rebuild at the same Zone Substation), but only 1 data line can be associated with each polygon's available capacity information. Therefore this cell specifies - where multiple investments are occurring - which lines the NOM should map on "Proposed Investment" and "Annual Deferral Value" maps, but ignore for "Available Capacity" and "Peak Day Available Capacity". Zone Substation data is generally preferred to display, or data for the sub-investment with the greatest opportunity for non-network solutions. Format: enter 'TRUE' to exclude. Otherwise leave blank.
Note on D1: Name of NSP or planning manager (for Vic transmission). Units/format: Text, but must conform exactly (case sensitive) to following list: United Energy, Tasnetworks, Transgrid, Essential Energy, Endeavour, Ausgrid, Evoenergy, Ergon Energy, Energex, SA Power Networks, Electranet, Jemena, Ausnet, Citipower-Powercor, AEMO
Note on E1: AER Ref: DT005 TL: Transmission Line TS: Transmission terminal station TCP: Transmission Connection Point STL: Sub transmission line ZS: Zone Substation ZS (proposed): New Zone Substation proposed to be built DF: (Distribution) feeder Units/format: Defined code above. Must match exactly (case sensitive)
Note on F1: Some assets may not have a 10-yr forecast, and only have a 5-yr forecast available (e.g. feeders). However, the maps produced will be for 10 years. Marking this field TRUE will keep yr5 loads and support requirements static out to yr10, and automatically include a standard caveat explaining this in the investment_description field. Format: enter 'TRUE' to use 5yr forecast only. Otherwise leave blank.
Note on G1: AER Ref: DT009 Highest operational voltage level of the assets involved in the constraints Units/format: kV (integer)
Note on H1: AER Ref: DT009 Operational voltage level of the assets involved in the constraints on the low side of the transformer Units/format: kV (integer)
Note on I1: AER Ref: DT012 Description of the problem or general asset situation and proposed network solution. Units/format: Free text field. Include special data caveats here if relevant.
Note on J1: Indicate the reliability criteria applied to the network asset. For example n, n-1, n-2, n-1 + risk. Unit/Format: Free text.
Note on K1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on L1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on M1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on N1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on O1: AER Ref: DT006 Total number of customers affected
Note on P1: AER Ref: DT006_a Percent of customers affected Format: Percent, entered as a positive decimal between 0 and 1 (e.g. 15% would be entered as 0.15)
Note on Q1: AER Ref: DT001 Constraint primary investment driver Format: Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage; market benefit. Must match list (but no longer case sensitive)
Note on R1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Demand growth related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on S1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Age/condition related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on T1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Connections related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on U1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Related to investments not falling into one of the other categories. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on V1: AER Ref: DT013 Total value of proposed network solution - should be the sum of Cols P to S (all investment types). If zero leave blank. Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on W1: AER Ref: DT014_a Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on X1: AER Ref: DT014_b Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on Y1: AER Ref: DT017 Saving in cost of capital from defering the project. Note that this does not use Value of Customer Reliability as an Input, as originally specified in AER guidance. Units: $/a (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload. NB: This is not the same calculation as represented in the Annual Deferral Value (ADV) map on the Network Opportunity Maps.
Note on Z1: Provide the component of the total proposed investment (Col T) that is considered deferrable with the non-network alternative/ Includes: • Defering augmentation (reducing project demand growth) • Defering new infrastructure riven by revised reliability criteria • Retiring assets (by reducing demand) • Downsizing assets (by reducing demand) • Extending the life of assets (by reducing the load conditions) Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AA1: AER Ref: DT013_a Annual operating costs (including overheads, risk allowance and contingency allowance if included) Units/Formats: $ AUD (real) Note: It may be useful to view your $ figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AB1: AER Ref: DT015 Provide the expected month and year when investment is planned for commissioning. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AC1: Provide the expected month and year when investment decision is locked in and non-network solutions are no longer an option. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AD1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AE1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AF1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AG1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AH1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on AI1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on AJ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AK1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AL1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AM1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AN1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AO1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AP1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AQ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AR1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AW1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AX1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AY1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AZ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BA1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BB1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BC1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BD1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BE1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BF1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BG1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BH1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BI1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BJ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BK1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BL1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BM1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BN1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BO1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BP1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BQ1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on BR1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on BS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BW1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BX1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BY1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BZ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CA1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CB1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CC1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CD1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CE1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CF1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CG1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CH1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CI1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CJ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CK1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CL1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CM1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CN1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CO1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CP1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CQ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CR1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CS1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CT1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CU1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CV1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CW1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CX1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CY1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CZ1: Provide Probability of Exceedance (POE) to be used in the NOM calculations. Should be the forecast upon which investment decision is based. Unit/Format: integer (10 or 50 ONLY)
Note on DA1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DB1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DC1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DD1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DE1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DF1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DG1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DH1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DI1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DJ1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DK1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DL1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DM1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DN1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DO1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DP1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DQ1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DR1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DS1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DT1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DU1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DV1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DW1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DX1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DY1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DZ1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EA1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EB1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EC1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on ED1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EE1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EF1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EG1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EH1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EI1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EJ1: AER Ref: DT016_a Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EK1: AER Ref: DT016_b Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EL1: AER Ref: DT016 Support Required in Summer. Unit/Format: MVA
Note on EM1: Support Required in Summer. Unit/Format: MVA
Note on EN1: Support Required in Summer. Unit/Format: MVA
Note on EO1: Support Required in Summer. Unit/Format: MVA
Note on EP1: Support Required in Summer. Unit/Format: MVA
Note on EQ1: Support Required in Summer. Unit/Format: MVA
Note on ER1: Support Required in Summer. Unit/Format: MVA
Note on ES1: Support Required in Summer. Unit/Format: MVA
Note on ET1: Support Required in Summer. Unit/Format: MVA
Note on EU1: Support Required in Summer. Unit/Format: MVA
Note on EV1: AER Ref: DT016_a Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EW1: AER Ref: DT016_b Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the following 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EX1: AER Ref: DT016 Support Required in Winter. Unit/Format: MVA
Note on EY1: Support Required in winter. Unit/Format: MVA
Note on EZ1: Support Required in winter. Unit/Format: MVA
Note on FA1: Support Required in winter. Unit/Format: MVA
Note on FB1: Support Required in winter. Unit/Format: MVA
Note on FC1: Support Required in winter. Unit/Format: MVA
Note on FD1: Support Required in winter. Unit/Format: MVA
Note on FE1: Support Required in winter. Unit/Format: MVA
Note on FF1: Support Required in winter. Unit/Format: MVA
Note on FG1: Support Required in winter. Unit/Format: MVA
Note on FH1: Supports solution for AER Refs: DT007_a, DT008_a, DT017_a, DT021_a Asset specific power factor Not used in NOM Format: Decimal between 0 and 1
Note on FI1: Optional: Description of reactive power requirements in an area. Unit/Format: Free text Note: Using this field will specify MVAr support required on ADV maps and thus not display other capacity related calculations (even if only a space is included " ")
Note on FJ1: AER Ref: DT017/ DT017_a NB: Leave BLANK if not applicable
Note on FK1: AER Ref: DT018 Emergency generation capacity available within constrained area Format: MVA NB: Leave BLANK if not applicable
Note on FL1: AER Ref: DT018_a Emergency generation capacity available within constrained area Format: MW
Note on FM1: AER Ref: DT019/ DT019_a Format: 'Yes' or 'No' Assets marked Yes will have 3yr half hourly data supplied in AER_NOM_emergencyresponse_data.xlsx and those with No will not.
Note on FN1: Mandatory (ALL data lines must have at least one connection specified): Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)

## Notes & Colour Key
This data template has been produced by the University of Technology Sydney on behalf of Energy Networks Austraila
Notes
This spreadsheet series combines the requirements of the Network Opportunity Maps and the AER DAPR digital data requirements in a single, consistent format that is machine readable for very large datasets.
The three spreadsheets in the series are as follows: | AER_NOM_annual_data_v3.1.xlsx | Main annual planning spreadsheet data input for all constrained assets under AER requirements for DNSPs, and all unconstrained Zone Substation data provided for NOM (only capacity and load forecast data dump required for latter assets)
| AER_NOM_loadtrace_data_mva_v3.1.xlsx | Detailed MVA load trace spreadsheet data for all constrained assets under AER requirement, and all unconstrained Zone Substation data provided for NOM. Machine linked to other spreadsheet using asset_code / ID. Responds to AER Ref: DT020
| AER_NOM_emergencyresponse_data_v3.xlsx | Only required to be filled out according to AER requirements for assets where emergency generation has been used in the past 3 years. Full 3yrs of half hourly data should be provided for any asset for which data is supplied. Responds to AER Ref: DT019 and DT019_a. This is only relevant for DNSPs.
The AER Reference number is shown in cell comments along with other relevant definitional information.
When this spreadsheet is saved as a .CSV (using the first worksheet only) it will be the machine readable input for online upload to the Network Opportunity Maps platform.
Cell Colour Key
Required by AER (and may be used in NOM)
NOM only (mandatory)
NOM only (optional)
Versions | Changes | Change (detail) | Data supplier Implication
Final, issued 15 December 2017
v1, issued 30 April 2018 | Corrects minor field name errors affecting data processing
v2, issued 30 November 2018 | Adjusts for 'support required' incompatibilies with AER requirements, and builds support for plotting multiple sub-projects at the one location with exclude_from_ADV column. Removes all drop down list to prevent errors in automated upload process. | Removed all drop-down boxes to eliminate automated upload issues | network, network_element & primary_driver must match prescribed case-sensitive list exactly (in cell comment and guideline) otherwise error will be drawn upon dataset upload.
|  | Cell formating changes and validations | If viewing $ value data entries in accounting format with , separators and/or $ sign need to "Edit>clear formats" for these cells before saving as CSV. No zero values allowed (if zero leave blank).
|  | New "exclude_from_capacity_ADV" field | Allows AER compliant dataset with multiple investments within one polygon to be mapped without errors. See Examples worksheet for application
|  | Added "summer_support_constraintyr_mw" and "summer_support_constraintyr_mva" | These are the AER requirements to disclose for the year the constraint bites. Previously this was the first year in the support required dataset (summer_support_yr1_mva) but this is often not the same as yr1 in the series. It should correspond with one of the years in the support required dataset, but this will differ depending on project_timing
|  | "connected_ZSX" changed to "connected_regionX": Terminology shift to be compatible with businesses using polygon that represent feeders rather than zone substation regions (or a mix thereof) | None
v2.1, issued 13 June 2019 | Adds cell comment guidance on year notations for Annual Data spreadsheet (only). Thus annual data template is v2.1 while others are still v2. | Yr1 now refers to Winter (Jun-Aug 2020) and Summer (Dec 2019-Feb 2020) | For any winter forecasts this may not align with TAPRs, as Jun-Aug 2019 will generally be the first year of 10-yr forecast series. Please check carefully, and we will change to naming specific years in the data templates for 2020 to avoid confusion, and request 11 years of data from TNSPs to manage the time mismatch between the 6-month DNSPs/TNSPs release timing (the final year can be extrapolated)
v3.0, issued 28 Nov 2020 | Minor changes to annual data template improve flexibility and streamline data entry | 1) Changed "exclude_from_capacity_ADV" (Col C) to "exclude_from_capacity_layers" as all investments are now able to be passed through to a specified polygon in ADV layers, and the exclude function now only applies to Available Capacity and Peak Day Available Capacity layers. 2) Includes new Col F "Use_5yr_forecast" for assets where 10yrs of data is not available. Marking TRUE in this field will keep yr5 loads static out to year 10, and automatically include a standard caveat explaining this in problem_context. Please use 10yr data wherever available. 3) Made connected_regionX field (Col FN onwards) mandatory for ALL data lines. This means that the asset_name and asset_code of the investments doesn't necessary need to match the polygon file, as the link to the polygon file occurs through the connected_regionX fields. | 1) Data entry basically the same as previous template. 2) If only 5 years of capacity, load forecast or support_required data is supplied, an error will be triggered unless the "Use_5yr_forecast" entry is marked as TRUE. 3) Every data line requires a linkage specified in Col FN.
v3.1, not yet issued | Added primary_driver category "market benefit" | Included in cell guidance in Col Q. Also no longer case sensitive. | Additional primary_driver category can now be used.
Note on A19: For assets for which this data is able to be produced (for example, a 10 yr forecast may be possibble for zone substations but not feeders)

## Examples
asset_name | asset_code | exclude_from_capacity_layers | network | network_element | use_5yr_forecast | voltage_highside | voltage_lowside | investment_description | reliability_criteria | latitude | longitude | latitude_end | longitude_end | res_cust_affected_no | res_cust_affected_percent | primary_driver | augmentation_invest | replacement_invest | connections_invest | other_invest | total_invest | cost_accuracy_plus | cost_accuracy_minus | annual_deferral | deferrable_invest | opex | project_timing | commitment_timing | summer_critical | winter_critical | spring_critical | autumn_critical | summer_nameplate_cap_mva | summer_secure_cap_mva | summer_acc_cap_yr_minus2_mva | summer_acc_cap_yr_minus1_mva | summer_acc_cap_yr0_mva | summer_acc_cap_yr1_mva | summer_acc_cap_yr2_mva | summer_acc_cap_yr3_mva | summer_acc_cap_yr4_mva | summer_acc_cap_yr5_mva | summer_acc_cap_yr6_mva | summer_acc_cap_yr7_mva | summer_acc_cap_yr8_mva | summer_acc_cap_yr9_mva | summer_acc_cap_yr10_mva | summer_load_yr1_poe50_mva | summer_load_yr2_poe50_mva | summer_load_yr3_poe50_mva | summer_load_yr4_poe50_mva | summer_load_yr5_poe50_mva | summer_load_yr6_poe50_mva | summer_load_yr7_poe50_mva | summer_load_yr8_poe50_mva | summer_load_yr9_poe50_mva | summer_load_yr10_poe50_mva | summer_load_yr1_poe10_mva | summer_load_yr2_poe10_mva | summer_load_yr3_poe10_mva | summer_load_yr4_poe10_mva | summer_load_yr5_poe10_mva | summer_load_yr6_poe10_mva | summer_load_yr7_poe10_mva | summer_load_yr8_poe10_mva | summer_load_yr9_poe10_mva | summer_load_yr10_poe10_mva | winter_nameplate_cap_mva | winter_secure_cap_mva | winter_acc_cap_yr_minus2_mva | winter_acc_cap_yr_minus1_mva | winter_acc_cap_yr0_mva | winter_acc_cap_yr1_mva | winter_acc_cap_yr2_mva | winter_acc_cap_yr3_mva | winter_acc_cap_yr4_mva | winter_acc_cap_yr5_mva | winter_acc_cap_yr6_mva | winter_acc_cap_yr7_mva | winter_acc_cap_yr8_mva | winter_acc_cap_yr9_mva | winter_acc_cap_yr10_mva | winter_load_yr1_poe50_mva | winter_load_yr2_poe50_mva | winter_load_yr3_poe50_mva | winter_load_yr4_poe50_mva | winter_load_yr5_poe50_mva | winter_load_yr6_poe50_mva | winter_load_yr7_poe50_mva | winter_load_yr8_poe50_mva | winter_load_yr9_poe50_mva | winter_load_yr10_poe50_mva | winter_load_yr1_poe10_mva | winter_load_yr2_poe10_mva | winter_load_yr3_poe10_mva | winter_load_yr4_poe10_mva | winter_load_yr5_poe10_mva | winter_load_yr6_poe10_mva | winter_load_yr7_poe10_mva | winter_load_yr8_poe10_mva | winter_load_yr9_poe10_mva | winter_load_yr10_poe10_mva | mapped_poe | load_at_risk_yr1_mw | load_at_risk_yr2_mw | load_at_risk_yr3_mw | load_at_risk_yr4_mw | load_at_risk_yr5_mw | EUSE_MWh_yr1 | EUSE_MWh_yr2 | EUSE_MWh_yr3 | EUSE_MWh_yr4 | EUSE_MWh_yr5 | EUSE_MWh_yr6 | EUSE_MWh_yr7 | EUSE_MWh_yr8 | EUSE_MWh_yr9 | EUSE_MWh_yr10 | hrs_exceedance_yr1 | hrs_exceedance_yr2 | hrs_exceedance_yr3 | hrs_exceedance_yr4 | hrs_exceedance_yr5 | hrs_exceedance_yr6 | hrs_exceedance_yr7 | hrs_exceedance_yr8 | hrs_exceedance_yr9 | hrs_exceedance_yr10 | EUSE_value_yr1 | EUSE_value_yr2 | EUSE_value_yr3 | EUSE_value_yr4 | EUSE_value_yr5 | EUSE_value_yr6 | EUSE_value_yr7 | EUSE_value_yr8 | EUSE_value_yr9 | EUSE_value_yr10 | summer_support_constraintyr_mw | summer_support_constraintyr_mva | summer_support_yr1_mva | summer_support_yr2_mva | summer_support_yr3_mva | summer_support_yr4_mva | summer_support_yr5_mva | summer_support_yr6_mva | summer_support_yr7_mva | summer_support_yr8_mva | summer_support_yr9_mva | summer_support_yr10_mva | winter_support_constraintyr_mw | winter_support_constraintyr_mva | winter_support_yr1_mva | winter_support_yr2_mva | winter_support_yr3_mva | winter_support_yr4_mva | winter_support_yr5_mva | winter_support_yr6_mva | winter_support_yr7_mva | winter_support_yr8_mva | winter_support_yr9_mva | winter_support_yr10_mva | power_factor | reactive_support_details | load_transfer_capability_mva | emergency_generation_mva | emergency_generation_mw | historic_emergency_generation_flag | connected_region1 | connected_region1_EF | connected_region2 | connected_region2_EF | connected_region3 | connected_region3_EF | connected_region4 | connected_region4_EF | connected_region5 | connected_region5_EF | connected_region6 | connected_region6_EF | connected_region7 | connected_region7_EF | connected_region8 | connected_region8_EF | connected_region9 | connected_region9_EF | connected_region10 | connected_region10_EF | connected_region11 | connected_region11_EF | connected_region12 | connected_region12_EF | connected_region13 | connected_region13_EF | connected_region14 | connected_region14_EF | connected_region15 | connected_region15_EF | connected_region16 | connected_region16_EF | connected_region17 | connected_region17_EF | connected_region18 | connected_region18_EF | connected_region19 | connected_region19_EF | connected_region20 | connected_region20_EF | connected_region21 | connected_region21_EF | connected_region22 | connected_region22_EF | connected_region23 | connected_region23_EF | connected_region24 | connected_region24_EF | connected_region25 | connected_region25_EF | connected_region26 | connected_region26_EF | connected_region27 | connected_region27_EF | connected_region28 | connected_region28_EF | connected_region29 | connected_region29_EF | connected_region30 | connected_region30_EF
Coburg North Zone Substation | CN |  | Jemena | ZS |  | 66 | 66 | Replace 66 kV 1-2 bus-tie circuit breaker at CN | economic/probabilistic | -37.7212 | 144.9778 | -37.7426 | 144.9626 | 21454 | 0.91649 | asset condition |  | 360000 |  |  | 360000 | 0.3 | 0.3 | 20000 | 360000 | 5400 | 2021-11-01 | 2019-06-01 | TRUE |  |  |  | 93 | 90 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 59.6001 | 60.1924 | 61.23 | 60.0791 | 59.8037 | 60.2273 | 59.8301 | 60.4631 | 60.1028 | 60.1366 | 65.6614 | 66.3525 | 67.4268 | 66.2315 | 66.1556 | 66.3655 | 66.0953 | 67.0858 | 66.4047 | 66.4442 | 93 | 90 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 57.2105 | 57.8859 | 58.9291 | 57.7878 | 57.6272 | 58.1072 | 57.9609 | 58.8006 | 59.1338 | 59.4636 | 58.5656 | 59.2324 | 60.2132 | 59.1372 | 59.0053 | 59.4382 | 59.2862 | 60.168 | 60.5061 | 60.8372 | 10 | 65.6264 | 66.3094 | 67.3695 | 66.1899 | 66.1149 | 1250 | 1250 | 1250 | 1250 | 1250 | [25 empty] | 65.6264 | 69.8575 | [22 empty] | 0.93943 |  | 18.6591 |  |  | No | JE_CN | 1
AW-03 Feeder | AW-03 |  | Jemena | DF | TRUE | 22 | 22 | Reconfigure AW-03 feeder loads. Deferral and capacity values shown are for an investment at AW-03 feeder and thus relate to a smaller area than shown in the map. Investments are also occuring to reconfigure AW-06, AW-07 and AW-08 feeder loads | economic/probabilistic | -37.7153 | 144.8859 | -37.7132 | 144.8607 | 1 | 0.011765 | capacity | 900000 |  |  |  | 900000 | 0.3 | 0.3 | 60000 | 900000 | 13500 | 2019-11-01 | 2018-06-01 | TRUE |  |  |  | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 5.9 | 5.8 | 5.8 | 5.9 | 6.1 | [5 empty] | 6.1 | 6.1 | 6.1 | 6.1 | 6.4 | [5 empty] | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 5.8 | 5.8 | 5.8 | 5.8 | 6 | [5 empty] | 5.9 | 5.9 | 5.9 | 6 | 6.2 | [5 empty] | 10 | 5.6 | 5.6 | 5.6 | 5.7 | 5.9 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 5.6 | 6.2222 | [22 empty] | 0.9 |  | 26.1 |  |  | No | JE_AW | 1
AW-06 Feeder | AW-06 | TRUE | Jemena | DF | TRUE | 22 | 22 | Reconfigure AW-06, AW-07 and AW-08 feeder loads | economic/probabilistic | -37.7153 | 144.8859 | -37.7572 | 144.8657 | 4952 | 0.97022 | capacity | 740000 |  |  |  | 740000 | 0.3 | 0.3 | 50000 | 740000 | 11100 | 2022-11-01 | 2020-06-01 | TRUE |  |  |  | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 12.1 | 12 | 11.9 | 11.7 | 11.7 | [5 empty] | 13.4 | 13.4 | 13.3 | 13 | 13.1 | [5 empty] | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 8.3 | 8.3 | 8.3 | 8.1 | 8.1 | [5 empty] | 8.5 | 8.5 | 8.4 | 8.3 | 8.3 | [5 empty] | 10 | 12.3 | 12.3 | 12.2 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 12.3 | 13.6667 | [22 empty] | 0.9 |  | 16.3 |  |  | No | JE_AW | 1
AW-07 Feeder | AW-07 | TRUE | Jemena | DF | TRUE | 22 | 22 | Reconfigure AW-06, AW-07 and AW-08 feeder loads | economic/probabilistic | -37.7153 | 144.8859 | -37.7497 | 144.8534 | 4702 | 0.96077 | capacity | 740000 |  |  |  | 740000 | 0.3 | 0.3 | 50000 | 740000 | 11100 | 2022-11-01 | 2020-06-01 | TRUE |  |  |  | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 11.7 | 11.7 | 11.6 | 11.4 | 11.5 | [5 empty] | 12.9 | 12.9 | 12.8 | 12.6 | 12.7 | [5 empty] | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 7.4 | 7.4 | 7.4 | 7.3 | 7.3 | [5 empty] | 7.6 | 7.6 | 7.6 | 7.5 | 7.5 | [5 empty] | 10 | 11.8 | 11.8 | 11.8 | 11.6 | 11.7 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 11.8 | 13.1111 | [22 empty] | 0.9 |  | 16.7 |  |  | No | JE_AW | 1
Airport West Zone Substation | AW | TRUE | Jemena | ZS |  | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7155 | 144.8858 | -37.7155 | 144.8858 | 19949 | 0.88044 | [13 empty] | TRUE |  |  |  | 130 | 130 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 85.792 | 87.2799 | 86.4517 | 85.0735 | 85.4697 | 87.3576 | 88.0234 | 90.2939 | 91.0433 | 92.427 | 93.4014 | 95.0684 | 94.0486 | 92.6714 | 93.4399 | 95.115 | 96.0987 | 99.0093 | 99.4039 | 100.9174 | 130 | 130 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 66.1945 | 67.7915 | 67.178 | 66.1743 | 66.6425 | 68.1595 | 68.9543 | 70.9642 | 72.3914 | 73.8423 | 67.7787 | 69.3859 | 68.6548 | 67.7339 | 68.2524 | 69.7383 | 70.5504 | 72.6358 | 74.0988 | 75.586 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [49 empty] | 0.91931 |  | 39.0753 |  |  | No | JE_AW | 1
KTS-BY-ES Sub-transmission Loop | KTS-BY-ES |  | Jemena | STL |  | 66 | 66 | Augment KTS-BY-ES 66 kV loop | economic/probabilistic | -37.7382 | 144.8747 | -37.7824 | 144.8747 | 36197 | 0.92154 | capacity | 2210000 |  |  |  | 2210000 | 0.3 | 0.3 | 150000 | 2210000 | 33150 | 2019-11-01 | 2018-06-01 | TRUE |  |  |  | 72.6 | 72.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.8999 | 81.0432 | 80.6774 | 78.9208 | 78.6048 | 79.9165 | 79.9521 | 81.4524 | 81.2159 | 81.5245 | 90.1368 | 90.2494 | 89.9716 | 88.0382 | 88.2057 | 89.2101 | 89.5089 | 91.4399 | 91.0864 | 91.0864 | 83.5 | 83.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.0109 | 63.2293 | 63.2786 | 61.9679 | 61.9679 | 62.988 | 63.3035 | 64.6413 | 65.4151 | 65.4151 | 64.6622 | 64.759 | 64.6372 | 63.4477 | 63.5693 | 64.4686 | 64.6622 | 66.2193 | 67.0439 | 67.0183 | 10 | 13.5412 | 14.0801 | 14.0729 | 12.6209 | 12.8906 | 1.3033 | 2.4165 | 2.5456 | 1.1263 | 1.3072 | 2.2063 | 1.1922 | 2.7583 | 3.4081 | 2.5182 | 38 | 43.5 | 43.5 | 35.5 | 37 | 43.5 | 47.5 | 45 | 50.5 | 43.5 | 52440.606 | 97231.176 | 102426.8758 | 45319.0291 | 52599.6885 | 88776.7755 | 47969.4996 | 110987.6172 | 137133.3043 | 101323.112 | 13.5412 | 15.0458 | [22 empty] | 0.9 |  | 43.5 |  |  | No | JE_BY | 1 | JE_ES | 1
x | x | x | x | x |  | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Note on A1: Full asset name (or, for TNSPs, 'Project Name' if more relevant). Should include any spatially represented asset type for which you wish to present data. Must match NOM polygon files. Units/format: Free text field
Note on B1: AER Ref: DT004 'shorthand' code or asset ID of Network Asset. Should be consistent with RIN Sustained Interruptions sheet from Category Analysis template. Must match NOM polygon files. Units/format: Free text field but ideally short notation no spaces and be unique.
Note on C1: There may be multiple investments (data lines) that relate to a given mapping region/polygon (such as a transformer replacement, a feeder augmentation and a switchboard rebuild at the same Zone Substation), but only 1 data line can be associated with each polygon. Therefore this cell specifies - where multiple investments are occurring - which ones the NOM should map on "Proposed Investment" but ignore for all other capacity and deferral value maps. The sub-investment with the greatest opportunity for non-network solutions should be kept in the dataset Format: enter 'TRUE' to exclude. Otherwise leave blank or FALSE
Note on D1: Name of NSP or planning manager (for Vic transmission). Units/format: Text, but must conform exactly (case sensitive) to following list: United Energy, Tasnetworks, Transgrid, Essential Energy, Endeavour, Ausgrid, Evoenergy, Ergon Energy, Energex, SA Power Networks, Electranet, Jemena, Ausnet, Citipower-Powercor, AEMO
Note on E1: AER Ref: DT005 TL: Transmission Line TS: Transmission terminal station TCP: Transmission Connection Point ZS: Zone Substation DF: (Distribution) feeder Units/format: Defined code above. Must match exactly (case sensitive)
Note on F1: Some assets may not have a 10-yr forecast, and only have a 5-yr forecast available (e.g. feeders). However, the maps produced will be for 10 years. Marking this field TRUE will keep yr5 loads and support requirements static out to yr10, and automatically include a standard caveat explaining this in the investment_description field. Format: enter 'TRUE' to use 5yr forecast only. Otherwise leave blank.
Note on G1: AER Ref: DT009 Highest operational voltage level of the assets involved in the constraints Units/format: kV (integer)
Note on H1: AER Ref: DT009 Operational voltage level of the assets involved in the constraints on the low side of the transformer Units/format: kV (integer)
Note on I1: AER Ref: DT012 Description of the problem or general asset situation and proposed network solution. Units/format: Free text field. Include special data caveats here if relevant.
Note on J1: Indicate the reliability criteria applied to the network asset. For example n, n-1, n-2, n-1 + risk. Unit/Format: Free text.
Note on K1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on L1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. Units/format: Decimal degrees
Note on M1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on N1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. Units/format: Decimal degrees
Note on O1: AER Ref: DT006 Total number of customers affected
Note on P1: AER Ref: DT006_a Percent of customers affected Format: Percent, entered as a positive decimal between 0 and 1 (e.g. 15% would be entered as 0.15)
Note on Q1: AER Ref: DT001 Constraint primary investment driver Format: Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage. Must match list exactly (case sensitive)
Note on R1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Demand growth related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on S1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Age/condition related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on T1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Connections related. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on U1: Provide estimated value of proposed network investment for each network asset in this category. If zero leave blank (entered value must be > 0). Related to investments not falling into one of the other categories. Units/Formats: $ AUD (real) . Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on V1: AER Ref: DT013 Total value of proposed network solution - should be the sum of Cols P to S (all investment types). If zero leave blank. Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on W1: AER Ref: DT014_a Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on X1: AER Ref: DT014_b Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as 0.15 in minus field 0.15 in plus field)
Note on Y1: AER Ref: DT017 Saving in cost of capital from defering the project. Note that this does not use Value of Customer Reliability as an Input, as originally specified in AER guidance. Units: $/a (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload. NB: This is not the same calculation as represented in the Annual Deferral Value (ADV) map on the Network Opportunity Maps.
Note on Z1: Provide the component of the total proposed investment (Col T) that is considered deferrable with the non-network alternative/ Includes: • Defering augmentation (reducing project demand growth) • Defering new infrastructure riven by revised reliability criteria • Retiring assets (by reducing demand) • Downsizing assets (by reducing demand) • Extending the life of assets (by reducing the load conditions) Units/Formats: $ AUD (real) Note: It may be useful to view your investment figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AA1: AER Ref: DT013_a Annual operating costs (including overheads, risk allowance and contingency allowance if included) Units/Formats: $ AUD (real) Note: It may be useful to view your $ figures in acccounting format with "," separators to ensure they are correct. Please select "Edit>Clear formats" on these cells before ssavings as a CSV otherwise CSV export will include non-numeric characters (- , $) causing errors on data upload.
Note on AB1: AER Ref: DT015 Provide the expected month and year when investment is planned for commissioning. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AC1: Provide the expected month and year when investment decision is locked in and non-network solutions are no longer an option. Units/Format: MMM-YY (convert to this format if pasting overwrites MMM-YY, and will cause data upload error)
Note on AD1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AE1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AF1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AG1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'TRUE' if yes. 'FALSE or leave blank otherwise'
Note on AH1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on AI1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on AJ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AK1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AL1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AM1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AN1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AO1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AP1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AQ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AR1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS) AND PROJECTED (10yrs): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AW1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AX1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AY1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AZ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BA1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BB1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BC1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BD1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BE1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BF1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BG1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BH1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BI1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BJ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BK1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BL1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BM1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BN1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BO1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BP1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BQ1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on BR1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on BS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BW1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BX1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BY1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BZ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CA1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CB1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CC1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CD1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CE1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CF1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CG1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CH1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CI1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CJ1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CK1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CL1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CM1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CN1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CO1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CP1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CQ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CR1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CS1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CT1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CU1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CV1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CW1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CX1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CY1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CZ1: Provide Probability of Exceedance (POE) to be used in the NOM calculations. Should be the forecast upon which investment decision is based. Unit/Format: integer (10 or 50 ONLY)
Note on DA1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DB1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DC1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DD1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DE1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DF1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DG1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DH1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DI1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DJ1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DK1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DL1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DM1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DN1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DO1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DP1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DQ1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DR1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DS1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DT1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DU1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DV1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DW1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DX1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DY1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DZ1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EA1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EB1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EC1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on ED1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EE1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EF1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EG1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EH1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EI1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EJ1: AER Ref: DT016_a Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EK1: AER Ref: DT016_b Network support required in Summer in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EL1: AER Ref: DT016 Support Required in Summer. Unit/Format: MVA
Note on EM1: Support Required in Summer. Unit/Format: MVA
Note on EN1: Support Required in Summer. Unit/Format: MVA
Note on EO1: Support Required in Summer. Unit/Format: MVA
Note on EP1: Support Required in Summer. Unit/Format: MVA
Note on EQ1: Support Required in Summer. Unit/Format: MVA
Note on ER1: Support Required in Summer. Unit/Format: MVA
Note on ES1: Support Required in Summer. Unit/Format: MVA
Note on ET1: Support Required in Summer. Unit/Format: MVA
Note on EU1: Support Required in Summer. Unit/Format: MVA
Note on EV1: AER Ref: DT016_a Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MW
Note on EW1: AER Ref: DT016_b Network support required in Winter in the year constraint bites (i.e. to achieve 1 year deferral). Note: This value will appear somewhere in the follwoing 10yr support required data series for Network Opportunity Maps (NOM) if support required is being used for NOM. Unit/Format: MVA
Note on EX1: AER Ref: DT016 Support Required in Winter. Unit/Format: MVA
Note on EY1: Support Required in winter. Unit/Format: MVA
Note on EZ1: Support Required in winter. Unit/Format: MVA
Note on FA1: Support Required in winter. Unit/Format: MVA
Note on FB1: Support Required in winter. Unit/Format: MVA
Note on FC1: Support Required in winter. Unit/Format: MVA
Note on FD1: Support Required in winter. Unit/Format: MVA
Note on FE1: Support Required in winter. Unit/Format: MVA
Note on FF1: Support Required in winter. Unit/Format: MVA
Note on FG1: Support Required in winter. Unit/Format: MVA
Note on FH1: Supports solution for AER Refs: DT007_a, DT008_a, DT017_a, DT021_a Asset specific power factor Format: Decimal between 0 and 1
Note on FI1: Optional: Description of reactive power requirements in an area. Unit/Format: Free text Note: Using this field will specify MVAr support required on ADV maps and thus not display other capacity related calculations (even if only a space is included " ")
Note on FJ1: AER Ref: DT017/ DT017_a NB: Leave BLANK if not applicable
Note on FK1: AER Ref: DT018 Emergency generation capacity available within constrained area Format: MVA NB: Leave BLANK if not applicable
Note on FL1: AER Ref: DT018_a Emergency generation capacity available within constrained area Format: MW
Note on FM1: AER Ref: DT019/ DT019_a Format: 'Yes' or 'No' Assets marked Yes will have 3yr half hourly data supplied in AER_NOM_emergencyresponse_data.xlsx and those with No will not.
Note on FN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on FY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on FZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GV1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GW1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GX1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on GY1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on GZ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HA1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HB1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HC1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HD1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HE1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HF1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HG1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HH1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HI1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HJ1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HK1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HL1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HM1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HN1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HO1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HP1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HQ1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HR1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HS1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on HT1: Mandatory: Provide the codenames of the region polygon that this asset will be mapped to. This is usually Distribution Zone Substations (ZS) but may also be Distrigbution Feeder or other type depending on the preferred geometry. Note: ZS connections are only required to be entered for STL, TS and TL assets (those above the level represented in the GIS polygons). Unit/Format: NSP_Prefix (from table below) followed by underscore then the asset_code. E.g. The data line for Evoenergy’s Belconnen Zone Sub (BZS) would note EV_BZS in its connected_region1 field. Evoenergy's A20 transmission line that is connected to Belconnen Zone Sub (BZS) would also note in connected_region1 field EV_BZS, along with any connected polygon regions. These codes MUST exactly match the .geojson GIS polygon file. NSP_Prefixes: Endeavour Energy: EE Essential Energy: ES Transgrid: TG Ausgrid: AG Energex: EX Ergon Energy: ER Electranet: EN SA Power Networks: SA TasNetworks: TN AusNet Services: AS Citipower: CP Powercor: PC Jemena: JE United Energy: UE Powerlink: PL Evoenergy: EV AEMO: AE
Note on HU1: Mandatory: For transmission or subtransmission constraints, demand management may be more effective in one network location than another. Enter the “effectiveness factor”, which represents whether demand management within the given connection zone or region is fully or partially effective. Format: decimal between 0 (not effective) and 1 (fully effective)
Note on C2: Only 1 data line associated with CN asset_code so no need to specify exclusions
Note on C3: The capacity situation for feeder (DF) asset was selected as data line to map to available/peak day capacity maps as highest deferrable value. The Zone Sub data line may alternatively be selected based on DNSP preference
Note on F3: Only 5yr forecast available for feeder assets so marked as TRUE
Note on I3: Note comment inserted when mapping DF situation to ZS: "Deferral and capacity values shown are for an investment at AW-03 feeder and thus relate to a smaller area than shown in the map." This is useful IF you choose to map a feeder constraint to zone polygon. An alternative is to create some smaller feeder polygons where such constraints exist.
Note on C6: Zone Substation situation considered less important as no investment taking place, therefore excluded and feeder situation mapped in preference
Note on FN7: ALL data lines now require connections specified to connect data to polygon map regions